## 5 minutes
Time range: | 2026-06-02 00:00:00 - 2026-06-02 23:59:59
Export time: | 2026-06-03 00:38:48
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge energy(kWh) | Total discharge energy(kWh) | Daily auxiliary power consumption(kWh) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge power(kW) | SOC(%) | Equivalent number of cycles | Battery cabin temperature 1(℃) | Battery cabin humidity 1(%) | Battery cabin temperature 2(℃) | Battery cabin humidity 2(%) | CO concentration 1(ppm) | CO concentration 2(ppm) | H2 concentration 1(ppm) | H2 concentration 2(ppm) | Control unit cabin temperature 1(℃) | Control unit cabin humidity 1(%) | Control status of EEV 1(step) | Control status of EEV 2(step) | Running status of outdoor fan 1(%) | Running status of outdoor fan 2(%) | Discharge temperature of compressor 1(℃) | Suction temperature of refrigerant system 1(℃) | Condenser outlet temperature of refrigerant system 1(℃) | Condenser outlet pressure of refrigerant system 1(Mpa) | Suction superheat degree of refrigerant system 1(℃) | Discharge superheat degree of compressor 1(℃) | Running status of outdoor fan 3(%) | Discharge temperature of compressor 2(℃) | Suction temperature of refrigerant system 2(℃) | Condenser outlet temperature of refrigerant system 2(℃) | Condenser outlet pressure of refrigerant system 2(Mpa) | Suction superheat degree of refrigerant system 2(℃) | Discharge superheat degree of compressor 2(℃) | Battery-side supply water temperature(℃) | Battery-side return water temperature(℃) | Air intake temperature(℃) | Discharge pressure of refrigerant system 1(Mpa) | Suction pressure of refrigerant system 1(Mpa) | Discharge pressure of refrigerant system 2(Mpa) | Suction pressure of refrigerant system 2(Mpa) | Running status of EEV 1(step) | Running status of EEV 2(step) | Compressor 1 running status(rpm) | Compressor 2 running status(rpm)
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:00:00 | 0 | 2.68 | 825502.6 | 801636.74 | 0.01 | 3763.884 | 664.212 | -252.447 | 15 | 184 | 25.7 | 60.4 | 25.8 | 60.3 | 0 | 0 | - | - | 29 | 55.2 | 0 | 0 | 0 | 0 | 28.1 | 29.5 | 27.7 | 1.48 | 5.3 | 3.8 | 0 | 27.6 | 29.3 | 27.5 | 1.51 | 5 | 3.5 | 24.3 | 24.2 | 27.3 | 1.51 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:05:00 | 0 | 17.3 | 825502.6 | 801651.16 | 0.07 | 3808.164 | 619.932 | -180.375 | 15 | 184 | 25.6 | 60.4 | 25.9 | 60.2 | 0 | 0 | - | - | 29 | 55.2 | 0 | 0 | 0 | 0 | 28 | 29.4 | 27.7 | 1.48 | 5.2 | 3.8 | 0 | 27.6 | 29.2 | 27.5 | 1.51 | 4.8 | 3.4 | 24.3 | 24.2 | 27.4 | 1.51 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:10:00 | 0 | 34.28 | 825502.6 | 801668.2 | 0.14 | 3808.164 | 619.932 | -125.739 | 15 | 184 | 25.6 | 60.5 | 25.9 | 60.2 | 0 | 0 | - | - | 29 | 55.3 | 0 | 0 | 0 | 0 | 28 | 29.3 | 27.7 | 1.48 | 5.1 | 3.7 | 0 | 27.6 | 29.2 | 27.5 | 1.51 | 4.7 | 3.4 | 24.3 | 24.3 | 27.4 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:15:00 | 0.6 | 38.14 | 825503.2 | 801671.78 | 0.2 | 3808.164 | 619.932 | -20.015 | 15 | 184 | 25.6 | 60.5 | 25.9 | 60.2 | 0 | 0 | - | - | 29 | 55.3 | 0 | 0 | 0 | 0 | 28 | 29.3 | 27.7 | 1.49 | 5.1 | 3.8 | 0 | 27.6 | 29.1 | 27.6 | 1.51 | 4.6 | 3.3 | 24.4 | 24.3 | 27.5 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:20:00 | 6.74 | 38.36 | 825509.48 | 801671.96 | 0.26 | 3808.164 | 619.932 | 101.723 | 15 | 184 | 25.6 | 60.5 | 25.9 | 60.3 | 0 | 0 | - | - | 29 | 55.4 | 0 | 0 | 0 | 0 | 28 | 29.3 | 27.7 | 1.49 | 5.1 | 3.8 | 0 | 27.6 | 29.1 | 27.6 | 1.51 | 4.6 | 3.3 | 24.4 | 24.3 | 27.5 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:25:00 | 23.58 | 38.36 | 825526.5 | 801671.96 | 0.33 | 3808.164 | 619.932 | 213.234 | 15 | 184 | 25.6 | 60.7 | 25.8 | 60.3 | 0 | 0 | - | - | 28.9 | 55.4 | 0 | 0 | 0 | 0 | 28 | 29.3 | 27.7 | 1.49 | 5 | 3.7 | 0 | 27.6 | 29 | 27.6 | 1.51 | 4.5 | 3.3 | 24.4 | 24.3 | 27.6 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:30:00 | 44.66 | 38.36 | 825547.54 | 801671.96 | 0.39 | 3763.884 | 664.212 | 229.881 | 16 | 184 | 25.6 | 60.6 | 25.8 | 60.4 | 0 | 0 | - | - | 28.9 | 55.4 | 0 | 0 | 0 | 0 | 28.1 | 29.3 | 27.7 | 1.49 | 5 | 3.8 | 0 | 27.6 | 29 | 27.6 | 1.51 | 4.5 | 3.3 | 24.4 | 24.3 | 27.6 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:35:00 | 56.8 | 38.36 | 825559.58 | 801671.96 | 0.46 | 3763.884 | 664.212 | 84.9 | 16 | 184 | 25.6 | 60.7 | 25.8 | 60.4 | 0 | 0 | - | - | 28.9 | 55.5 | 0 | 0 | 0 | 0 | 28.1 | 29.3 | 27.8 | 1.49 | 5 | 3.8 | 0 | 27.6 | 29 | 27.7 | 1.52 | 4.5 | 3.3 | 24.4 | 24.3 | 27.6 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:40:00 | 61.56 | 38.44 | 825564.22 | 801672.04 | 0.52 | 3763.884 | 664.212 | 63.731 | 16 | 184 | 25.6 | 60.8 | 25.8 | 60.4 | 0 | 0 | - | - | 28.8 | 55.5 | 0 | 0 | 0 | 0 | 28.2 | 29.2 | 27.8 | 1.49 | 4.9 | 3.8 | 0 | 27.6 | 28.9 | 27.7 | 1.51 | 4.4 | 3.4 | 24.4 | 24.4 | 27.3 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:45:00 | 65.74 | 40.3 | 825568.34 | 801674.06 | 0.58 | 3763.884 | 664.212 | -48.321 | 16 | 184 | 25.6 | 60.8 | 25.8 | 60.4 | 0 | 0 | - | - | 28.8 | 55.6 | 0 | 0 | 0 | 0 | 28.1 | 29.2 | 27.8 | 1.49 | 4.9 | 3.8 | 0 | 27.6 | 28.9 | 27.7 | 1.52 | 4.4 | 3.3 | 24.4 | 24.4 | 27.2 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:50:00 | 67.2 | 42.02 | 825569.8 | 801675.62 | 0.64 | 3763.884 | 664.212 | -27.773 | 16 | 184 | 25.6 | 60.8 | 25.8 | 60.4 | 0 | 0 | - | - | 28.8 | 55.6 | 0 | 0 | 0 | 0 | 27.9 | 29 | 27.7 | 1.49 | 4.7 | 3.6 | 0 | 27.5 | 28.7 | 27.7 | 1.51 | 4.2 | 3.2 | 24.4 | 24.4 | 27.2 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 00:55:00 | 67.2 | 46.6 | 825569.8 | 801680.24 | 0.7 | 3763.884 | 664.212 | -27.366 | 16 | 184 | 25.6 | 60.8 | 25.8 | 60.5 | 0 | 0 | - | - | 28.8 | 55.7 | 0 | 0 | 0 | 0 | 27.9 | 28.9 | 27.7 | 1.48 | 4.7 | 3.6 | 0 | 27.4 | 28.7 | 27.7 | 1.51 | 4.1 | 3.2 | 24.4 | 24.4 | 27.1 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:00:00 | 67.56 | 50.64 | 825570.16 | 801684.24 | 0.76 | 3763.884 | 664.212 | -10.373 | 16 | 184 | 25.6 | 60.9 | 25.8 | 60.5 | 0 | 0 | - | - | 28.7 | 55.7 | 0 | 0 | 0 | 0 | 27.8 | 28.8 | 27.6 | 1.49 | 4.6 | 3.5 | 0 | 27.3 | 28.6 | 27.7 | 1.52 | 4 | 3.1 | 24.4 | 24.4 | 27.1 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:05:00 | 70.6 | 51.28 | 825573.22 | 801684.94 | 0.82 | 3763.884 | 664.212 | -25.654 | 16 | 184 | 25.6 | 60.8 | 25.8 | 60.4 | 0 | 0 | - | - | 28.7 | 55.7 | 0 | 0 | 0 | 0 | 27.7 | 28.7 | 27.5 | 1.49 | 4.5 | 3.4 | 0 | 27.2 | 28.4 | 27.6 | 1.52 | 3.9 | 3 | 24.5 | 24.4 | 27.1 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:10:00 | 71.06 | 55.56 | 825573.66 | 801689.26 | 0.88 | 3763.884 | 664.212 | -15.298 | 16 | 184 | 25.6 | 60.8 | 25.9 | 60.4 | 0 | 0 | - | - | 28.7 | 55.8 | 0 | 0 | 0 | 0 | 27.7 | 28.7 | 27.5 | 1.49 | 4.4 | 3.3 | 0 | 27.2 | 28.4 | 27.6 | 1.52 | 3.8 | 2.9 | 24.5 | 24.4 | 27.1 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:15:00 | 71.3 | 64.44 | 825573.9 | 801698.1 | 0.95 | 3763.884 | 664.212 | -11.858 | 16 | 184 | 25.6 | 60.8 | 25.9 | 60.4 | 0 | 0 | - | - | 28.7 | 55.8 | 0 | 0 | 0 | 0 | 27.7 | 28.7 | 27.5 | 1.49 | 4.3 | 3.3 | 0 | 27.2 | 28.3 | 27.6 | 1.52 | 3.8 | 2.9 | 24.5 | 24.4 | 27.1 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:20:00 | 73.08 | 65.28 | 825575.7 | 801698.88 | 1.01 | 3763.884 | 664.212 | 33.398 | 16 | 184 | 25.6 | 60.8 | 25.9 | 60.4 | 0 | 0 | - | - | 28.7 | 55.8 | 0 | 0 | 0 | 0 | 27.7 | 28.7 | 27.5 | 1.49 | 4.3 | 3.4 | 0 | 27.2 | 28.3 | 27.6 | 1.52 | 3.7 | 2.9 | 24.5 | 24.4 | 26.8 | 1.52 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:25:00 | 74.6 | 68.44 | 825577.2 | 801702.06 | 1.07 | 3763.884 | 664.212 | 7.345 | 16 | 184 | 25.7 | 60.8 | 25.9 | 60.4 | 0 | 0 | - | - | 28.7 | 55.8 | 0 | 0 | 0 | 0 | 27.7 | 28.6 | 27.4 | 1.49 | 4.2 | 3.3 | 0 | 27.2 | 28.2 | 27.6 | 1.52 | 3.6 | 2.8 | 24.5 | 24.5 | 26.8 | 1.52 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:30:00 | 74.78 | 71.66 | 825577.38 | 801705.32 | 1.13 | 3763.884 | 664.212 | -58.283 | 16 | 184 | 25.6 | 60.7 | 25.9 | 60.4 | 0 | 0 | - | - | 28.6 | 55.8 | 0 | 0 | 0 | 0 | 27.7 | 28.5 | 27.5 | 1.49 | 4.2 | 3.3 | 0 | 27.2 | 28.2 | 27.6 | 1.52 | 3.5 | 2.8 | 24.5 | 24.5 | 26.7 | 1.52 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:35:00 | 74.78 | 76.74 | 825577.38 | 801710.42 | 1.19 | 3763.884 | 664.212 | -15.015 | 15 | 184 | 25.7 | 60.7 | 25.9 | 60.4 | 0 | 0 | - | - | 28.6 | 55.8 | 0 | 0 | 0 | 0 | 27.7 | 28.4 | 27.4 | 1.49 | 4 | 3.2 | 0 | 27.2 | 28.1 | 27.6 | 1.52 | 3.5 | 2.8 | 24.5 | 24.5 | 26.7 | 1.52 | 1.51 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:40:00 | 74.78 | 80.34 | 825577.38 | 801713.98 | 1.25 | 3763.884 | 664.212 | -23.096 | 15 | 184 | 25.7 | 60.7 | 26 | 60.4 | 0 | 0 | - | - | 28.6 | 55.9 | 0 | 0 | 0 | 0 | 27.6 | 28.3 | 27.4 | 1.49 | 3.9 | 3.2 | 0 | 27.1 | 28.1 | 27.5 | 1.52 | 3.3 | 2.8 | 24.5 | 24.5 | 26.7 | 1.52 | 1.51 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:45:00 | 75.26 | 83.12 | 825577.86 | 801716.78 | 1.31 | 3786.024 | 642.072 | 1.218 | 15 | 184 | 25.7 | 60.6 | 26 | 60.3 | 0 | 0 | - | - | 28.6 | 55.9 | 0 | 0 | 0 | 0 | 27.6 | 28.2 | 27.4 | 1.49 | 3.8 | 3.1 | 0 | 27.1 | 27.9 | 27.4 | 1.52 | 3.3 | 2.7 | 24.5 | 24.5 | 26.6 | 1.52 | 1.51 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:50:00 | 75.76 | 86.58 | 825578.36 | 801720.22 | 1.37 | 3808.164 | 619.932 | -54.004 | 15 | 184 | 25.7 | 60.6 | 25.9 | 60.4 | 0 | 0 | - | - | 28.6 | 55.9 | 0 | 0 | 0 | 0 | 27.5 | 28.2 | 27.3 | 1.49 | 3.7 | 3.1 | 0 | 27.1 | 27.8 | 27.4 | 1.52 | 3.1 | 2.6 | 24.6 | 24.5 | 26.6 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 01:55:00 | 78.8 | 88.94 | 825581.92 | 801722.54 | 1.43 | 3800.784 | 627.312 | 250.907 | 15 | 184 | 25.7 | 60.6 | 25.8 | 60.7 | 0 | 0 | - | - | 28.6 | 55.9 | 0 | 0 | 0 | 0 | 27.4 | 28.1 | 27.3 | 1.49 | 3.6 | 3 | 0 | 27 | 27.7 | 27.4 | 1.52 | 3 | 2.6 | 24.6 | 24.6 | 26.6 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:00:00 | 86.94 | 92.42 | 825589.54 | 801726.06 | 1.49 | 3763.884 | 664.212 | -94.77 | 15 | 184 | 25.7 | 60.7 | 25.8 | 60.9 | 0 | 0 | - | - | 28.6 | 55.9 | 0 | 0 | 0 | 0 | 27.4 | 28.1 | 27.2 | 1.49 | 3.6 | 2.9 | 0 | 26.9 | 27.7 | 27.4 | 1.52 | 3 | 2.5 | 24.6 | 24.6 | 26.6 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:05:00 | 86.94 | 97.72 | 825589.54 | 801731.32 | 1.56 | 3808.164 | 619.932 | -17.939 | 15 | 184 | 25.8 | 60.6 | 25.9 | 60.5 | 0 | 0 | - | - | 28.6 | 56 | 0 | 0 | 0 | 0 | 27.3 | 28 | 27.2 | 1.49 | 3.5 | 2.8 | 0 | 26.9 | 27.6 | 27.3 | 1.52 | 2.9 | 2.5 | 24.6 | 24.6 | 26.5 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:10:00 | 87.24 | 99.94 | 825589.84 | 801733.6 | 1.62 | 3808.164 | 619.932 | -38.905 | 15 | 184 | 25.8 | 60.6 | 25.9 | 60.5 | 0 | 0 | - | - | 28.6 | 56 | 0 | 0 | 0 | 0 | 27.3 | 27.9 | 27.2 | 1.49 | 3.5 | 2.9 | 0 | 26.9 | 27.6 | 27.3 | 1.52 | 2.9 | 2.5 | 24.6 | 24.6 | 26.4 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:15:00 | 87.8 | 100.36 | 825590.4 | 801733.96 | 1.68 | 3808.164 | 619.932 | 43.333 | 15 | 184 | 25.8 | 60.6 | 25.9 | 60.5 | 0 | 0 | - | - | 28.6 | 56 | 0 | 0 | 0 | 0 | 27.3 | 27.8 | 27.2 | 1.49 | 3.3 | 2.8 | 0 | 26.8 | 27.4 | 27.3 | 1.52 | 2.8 | 2.4 | 24.6 | 24.6 | 26.5 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:20:00 | 89.16 | 101.32 | 825591.76 | 801734.96 | 1.74 | 3808.164 | 619.932 | 5.79 | 15 | 184 | 25.8 | 60.6 | 26 | 60.4 | 0 | 0 | - | - | 28.6 | 56 | 0 | 0 | 0 | 0 | 27.3 | 27.8 | 27.2 | 1.49 | 3.3 | 2.8 | 0 | 26.8 | 27.4 | 27.3 | 1.52 | 2.7 | 2.4 | 24.6 | 24.6 | 26.6 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:25:00 | 90.3 | 101.44 | 825593 | 801735.04 | 1.8 | 3763.884 | 664.212 | 53.063 | 15 | 184 | 25.8 | 60.7 | 26 | 60.4 | 0 | 0 | - | - | 28.6 | 56 | 0 | 0 | 0 | 0 | 27.3 | 27.7 | 27.2 | 1.49 | 3.4 | 2.8 | 0 | 26.8 | 27.4 | 27.3 | 1.52 | 2.7 | 2.4 | 24.7 | 24.6 | 26.6 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:30:00 | 97.04 | 101.56 | 825599.78 | 801735.16 | 1.86 | 3763.884 | 664.212 | 94.309 | 15 | 184 | 25.8 | 60.7 | 26 | 60.4 | 0 | 0 | - | - | 28.6 | 56 | 0 | 0 | 0 | 0 | 27.3 | 27.8 | 27.2 | 1.49 | 3.3 | 2.9 | 0 | 26.8 | 27.4 | 27.3 | 1.52 | 2.7 | 2.4 | 24.6 | 24.6 | 26.6 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:35:00 | 100.5 | 104.42 | 825603.1 | 801738.12 | 1.92 | 3763.884 | 664.212 | -61.846 | 15 | 184 | 25.8 | 60.6 | 26 | 60.4 | 0 | 0 | - | - | 28.5 | 56.1 | 0 | 0 | 0 | 0 | 27.3 | 27.8 | 27.2 | 1.49 | 3.4 | 2.9 | 0 | 26.8 | 27.3 | 27.2 | 1.52 | 2.7 | 2.5 | 24.6 | 24.6 | 26.6 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:40:00 | 101.2 | 106.68 | 825603.8 | 801740.3 | 1.98 | 3763.884 | 664.212 | -29.654 | 15 | 184 | 25.8 | 60.6 | 26 | 60.4 | 0 | 0 | - | - | 28.5 | 56.1 | 0 | 0 | 0 | 0 | 27.3 | 27.7 | 27.2 | 1.49 | 3.3 | 2.8 | 0 | 26.8 | 27.3 | 27.3 | 1.52 | 2.6 | 2.4 | 24.6 | 24.6 | 26.6 | 1.52 | 1.51 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:45:00 | 102.42 | 108.1 | 825605.02 | 801741.7 | 2.04 | 3763.884 | 664.212 | 11.458 | 15 | 184 | 25.8 | 60.6 | 26 | 60.4 | 0 | 0 | - | - | 28.6 | 56.1 | 0 | 0 | 0 | 0 | 27.3 | 27.7 | 27.2 | 1.49 | 3.3 | 2.9 | 0 | 26.8 | 27.3 | 27.2 | 1.52 | 2.6 | 2.4 | 24.7 | 24.6 | 26.5 | 1.52 | 1.51 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:50:00 | 105.58 | 108.12 | 825608.22 | 801741.72 | 2.1 | 3763.884 | 664.212 | -12.154 | 15 | 184 | 25.8 | 60.6 | 26 | 60.4 | 0 | 0 | - | - | 28.5 | 56.1 | 0 | 0 | 0 | 0 | 27.2 | 27.7 | 27.1 | 1.49 | 3.3 | 2.9 | 0 | 26.8 | 27.2 | 27.2 | 1.52 | 2.6 | 2.5 | 24.7 | 24.6 | 26.4 | 1.52 | 1.51 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 02:55:00 | 108.28 | 108.54 | 825610.88 | 801742.16 | 2.16 | 3763.884 | 664.212 | -65.669 | 15 | 184 | 25.9 | 60.6 | 26 | 60.4 | 0 | 0 | - | - | 28.5 | 56.1 | 0 | 0 | 0 | 0 | 27.3 | 27.7 | 27.1 | 1.49 | 3.2 | 2.9 | 0 | 26.8 | 27.2 | 27.2 | 1.52 | 2.6 | 2.4 | 24.7 | 24.6 | 26.5 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:00:00 | 108.48 | 112.36 | 825611.08 | 801746.06 | 2.22 | 3763.884 | 664.212 | -53.551 | 15 | 184 | 25.8 | 60.6 | 26 | 60.3 | 0 | 0 | - | - | 28.5 | 56.1 | 0 | 0 | 0 | 0 | 27.3 | 27.7 | 27.1 | 1.49 | 3.3 | 2.9 | 0 | 26.7 | 27.2 | 27.2 | 1.52 | 2.5 | 2.4 | 24.7 | 24.7 | 26.4 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:05:00 | 108.48 | 116.82 | 825611.08 | 801750.5 | 2.28 | 3793.404 | 634.692 | -18.457 | 15 | 184 | 25.8 | 60.7 | 26 | 60.4 | 0 | 0 | - | - | 28.5 | 56.2 | 0 | 0 | 0 | 0 | 27.3 | 27.6 | 27.1 | 1.49 | 3.2 | 2.9 | 0 | 26.8 | 27.2 | 27.2 | 1.52 | 2.5 | 2.5 | 24.7 | 24.7 | 26.4 | 1.52 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:10:00 | 109.76 | 119.32 | 825612.36 | 801753.1 | 2.33 | 3800.784 | 627.312 | -157.25 | 15 | 184 | 25.9 | 60.7 | 26 | 60.5 | 0 | 0 | - | - | 28.5 | 56.2 | 0 | 0 | 0 | 0 | 27.3 | 27.6 | 27.1 | 1.49 | 3.2 | 2.9 | 0 | 26.8 | 27.1 | 27.2 | 1.52 | 2.5 | 2.5 | 24.7 | 24.7 | 26.4 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:15:00 | 109.76 | 125.7 | 825612.36 | 801759.38 | 2.4 | 3808.164 | 619.932 | -107.821 | 15 | 184 | 25.9 | 60.7 | 25.9 | 60.8 | 0 | 0 | - | - | 28.5 | 56.3 | 0 | 0 | 0 | 0 | 27.2 | 27.5 | 27.1 | 1.49 | 3.2 | 2.9 | 0 | 26.7 | 27.1 | 27.2 | 1.51 | 2.5 | 2.5 | 24.7 | 24.7 | 26.3 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:20:00 | 109.76 | 136.86 | 825612.36 | 801770.62 | 2.46 | 3808.164 | 619.932 | -120.577 | 15 | 184 | 25.9 | 60.6 | 26 | 60.6 | 0 | 0 | - | - | 28.4 | 56.3 | 0 | 0 | 0 | 0 | 27.3 | 27.5 | 27.1 | 1.49 | 3.2 | 2.9 | 0 | 26.7 | 27.1 | 27.2 | 1.52 | 2.5 | 2.5 | 24.7 | 24.7 | 26.4 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:25:00 | 109.76 | 150.78 | 825612.36 | 801784.52 | 2.52 | 3808.164 | 619.932 | -64.757 | 14 | 184 | 25.9 | 60.7 | 26 | 60.5 | 0 | 0 | - | - | 28.4 | 56.4 | 0 | 0 | 0 | 0 | 27.3 | 27.4 | 27.1 | 1.49 | 3.2 | 2.9 | 0 | 26.7 | 27 | 27.2 | 1.51 | 2.5 | 2.5 | 24.7 | 24.7 | 26.3 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:30:00 | 110.4 | 153.78 | 825613 | 801787.42 | 2.58 | 3808.164 | 619.932 | -73.243 | 14 | 184 | 25.9 | 60.7 | 26 | 60.5 | 0 | 0 | - | - | 28.4 | 56.4 | 0 | 0 | 0 | 0 | 27.3 | 27.4 | 27.1 | 1.49 | 3.1 | 2.9 | 0 | 26.7 | 27 | 27.2 | 1.52 | 2.4 | 2.5 | 24.7 | 24.7 | 26.3 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:35:00 | 112.66 | 154.92 | 825615.44 | 801788.52 | 2.64 | 3808.164 | 619.932 | 58.844 | 14 | 184 | 25.8 | 60.7 | 26.1 | 60.5 | 0 | 0 | - | - | 28.4 | 56.4 | 0 | 0 | 0 | 0 | 27.3 | 27.4 | 27.1 | 1.49 | 3 | 2.9 | 0 | 26.7 | 26.9 | 27.2 | 1.52 | 2.3 | 2.5 | 24.7 | 24.7 | 26.4 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:40:00 | 114.76 | 157.6 | 825617.36 | 801791.22 | 2.7 | 3808.164 | 619.932 | -32.114 | 14 | 184 | 25.8 | 60.8 | 26 | 60.5 | 0 | 0 | - | - | 28.4 | 56.5 | 0 | 0 | 0 | 0 | 27.3 | 27.3 | 27.1 | 1.49 | 3 | 3 | 0 | 26.7 | 26.9 | 27.2 | 1.51 | 2.3 | 2.5 | 24.8 | 24.7 | 26.4 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:45:00 | 116.66 | 159.76 | 825619.44 | 801793.36 | 2.76 | 3808.164 | 619.932 | 141.218 | 14 | 184 | 25.8 | 60.9 | 26 | 60.5 | 0 | 0 | - | - | 28.3 | 56.6 | 0 | 0 | 0 | 0 | 27.3 | 27.4 | 27.1 | 1.49 | 3 | 2.9 | 0 | 26.8 | 26.9 | 27.2 | 1.51 | 2.3 | 2.5 | 24.8 | 24.8 | 26.5 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:50:00 | 119.42 | 160.36 | 825622.02 | 801793.96 | 2.82 | 3808.164 | 619.932 | -6.761 | 14 | 184 | 25.8 | 60.9 | 26 | 60.6 | 0 | 0 | - | - | 28.3 | 56.7 | 0 | 0 | 0 | 0 | 27.3 | 27.4 | 27.1 | 1.49 | 3 | 3 | 0 | 26.8 | 26.9 | 27.2 | 1.51 | 2.3 | 2.5 | 24.8 | 24.8 | 26.6 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 03:55:00 | 120.18 | 161.04 | 825622.78 | 801794.74 | 2.88 | 3808.164 | 619.932 | -15.603 | 14 | 184 | 25.8 | 60.9 | 26 | 60.6 | 0 | 0 | - | - | 28.3 | 56.7 | 0 | 0 | 0 | 0 | 27.3 | 27.4 | 27.1 | 1.49 | 3.1 | 3 | 0 | 26.8 | 26.9 | 27.2 | 1.51 | 2.3 | 2.5 | 24.8 | 24.7 | 26.7 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:00:00 | 120.42 | 162.38 | 825623.02 | 801795.98 | 2.94 | 3808.164 | 619.932 | -2.328 | 14 | 184 | 25.8 | 61 | 26 | 60.6 | 0 | 0 | - | - | 28.3 | 56.8 | 0 | 0 | 0 | 0 | 27.4 | 27.5 | 27.2 | 1.49 | 3.1 | 3 | 0 | 26.8 | 26.9 | 27.2 | 1.51 | 2.3 | 2.6 | 24.8 | 24.7 | 26.7 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:05:00 | 121.02 | 162.76 | 825623.62 | 801796.36 | 2.99 | 3808.164 | 619.932 | 7.016 | 14 | 184 | 25.7 | 61 | 26 | 60.7 | 0 | 0 | - | - | 28.3 | 56.8 | 0 | 0 | 0 | 0 | 27.4 | 27.5 | 27.2 | 1.49 | 3.1 | 3.1 | 0 | 26.8 | 26.9 | 27.2 | 1.52 | 2.3 | 2.6 | 24.8 | 24.8 | 26.7 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:10:00 | 123.08 | 162.9 | 825625.68 | 801796.52 | 3.05 | 3808.164 | 619.932 | -10.433 | 15 | 184 | 25.7 | 61.1 | 26 | 60.7 | 0 | 0 | - | - | 28.2 | 56.9 | 0 | 0 | 0 | 0 | 27.4 | 27.5 | 27.2 | 1.49 | 3.2 | 3.1 | 0 | 26.8 | 27 | 27.3 | 1.52 | 2.4 | 2.6 | 24.8 | 24.8 | 26.7 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:15:00 | 123.8 | 164.58 | 825626.42 | 801798.18 | 3.11 | 3808.164 | 619.932 | 28.53 | 15 | 184 | 25.7 | 61.2 | 26 | 60.8 | 0 | 0 | - | - | 28.2 | 56.9 | 0 | 0 | 0 | 0 | 27.4 | 27.5 | 27.2 | 1.49 | 3.2 | 3.1 | 0 | 26.8 | 27 | 27.3 | 1.52 | 2.4 | 2.6 | 24.8 | 24.8 | 26.7 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:20:00 | 125.66 | 166.46 | 825628.26 | 801800.22 | 3.17 | 3808.164 | 619.932 | -90.631 | 14 | 184 | 25.7 | 61.2 | 26 | 60.8 | 0 | 0 | - | - | 28.2 | 57.1 | 0 | 0 | 0 | 0 | 27.4 | 27.5 | 27.2 | 1.49 | 3.1 | 3.1 | 0 | 26.8 | 27 | 27.3 | 1.52 | 2.3 | 2.6 | 24.8 | 24.8 | 26.7 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:25:00 | 125.66 | 176.04 | 825628.26 | 801809.76 | 3.23 | 3830.307 | 597.792 | -91.83 | 14 | 184 | 25.7 | 61.3 | 26 | 60.8 | 0 | 0 | - | - | 28.2 | 57 | 0 | 0 | 0 | 0 | 27.4 | 27.5 | 27.2 | 1.49 | 3.1 | 3.1 | 0 | 26.9 | 26.9 | 27.3 | 1.52 | 2.3 | 2.7 | 24.8 | 24.8 | 26.7 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:30:00 | 125.66 | 182.7 | 825628.26 | 801816.52 | 3.29 | 3852.45 | 575.652 | -107.453 | 14 | 184 | 25.7 | 61.3 | 25.9 | 60.9 | 0 | 0 | - | - | 28.2 | 57.1 | 0 | 0 | 0 | 0 | 27.4 | 27.4 | 27.2 | 1.49 | 3.1 | 3.1 | 0 | 26.9 | 26.9 | 27.3 | 1.51 | 2.3 | 2.6 | 24.9 | 24.8 | 26.7 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:35:00 | 125.66 | 191.06 | 825628.26 | 801824.74 | 3.35 | 3852.45 | 575.652 | -76.204 | 14 | 184 | 25.6 | 61.4 | 26 | 60.9 | 0 | 0 | - | - | 28.2 | 57.2 | 0 | 0 | 0 | 0 | 27.4 | 27.5 | 27.3 | 1.49 | 3.1 | 3.1 | 0 | 26.9 | 26.9 | 27.2 | 1.51 | 2.3 | 2.6 | 24.9 | 24.8 | 26.8 | 1.51 | 1.51 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:40:00 | 127.28 | 194.98 | 825629.88 | 801828.92 | 3.41 | 3852.45 | 575.652 | -91.535 | 14 | 184 | 25.7 | 61.4 | 26 | 60.9 | 0 | 0 | - | - | 28.1 | 57.2 | 0 | 0 | 0 | 0 | 27.5 | 27.6 | 27.3 | 1.49 | 3.1 | 3.1 | 0 | 26.9 | 26.9 | 27.3 | 1.52 | 2.3 | 2.6 | 24.9 | 24.9 | 26.7 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:45:00 | 127.42 | 200.54 | 825630.02 | 801834.16 | 3.47 | 3852.45 | 575.652 | -7.041 | 14 | 184 | 25.6 | 61.4 | 25.9 | 61 | 0 | 0 | - | - | 28.1 | 57.2 | 0 | 0 | 0 | 0 | 27.5 | 27.6 | 27.3 | 1.49 | 3.1 | 3.1 | 0 | 26.9 | 27 | 27.3 | 1.52 | 2.3 | 2.6 | 24.9 | 24.9 | 26.7 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:50:00 | 132.86 | 200.56 | 825635.5 | 801834.16 | 3.53 | 3852.45 | 575.652 | 26.374 | 14 | 184 | 25.6 | 61.5 | 25.9 | 61 | 0 | 0 | - | - | 28.1 | 57.3 | 0 | 0 | 0 | 0 | 27.5 | 27.6 | 27.3 | 1.49 | 3.1 | 3.1 | 0 | 26.9 | 27 | 27.3 | 1.52 | 2.3 | 2.6 | 24.9 | 24.9 | 26.7 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 04:55:00 | 134.2 | 202.7 | 825636.8 | 801836.3 | 3.59 | 3852.45 | 575.652 | 13.779 | 14 | 184 | 25.6 | 61.5 | 25.9 | 61 | 0 | 0 | - | - | 28.1 | 57.3 | 0 | 0 | 0 | 0 | 27.5 | 27.6 | 27.3 | 1.49 | 3.1 | 3.2 | 0 | 26.9 | 27 | 27.3 | 1.52 | 2.3 | 2.6 | 24.9 | 24.9 | 26.6 | 1.51 | 1.51 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:00:00 | 135.14 | 205.74 | 825637.74 | 801839.5 | 3.65 | 3852.45 | 575.652 | -42.171 | 14 | 184 | 25.6 | 61.5 | 25.9 | 61 | 0 | 0 | - | - | 28.1 | 57.3 | 0 | 0 | 0 | 0 | 27.4 | 27.4 | 27.2 | 1.49 | 3 | 3.1 | 0 | 26.9 | 27 | 27.3 | 1.52 | 2.3 | 2.6 | 24.9 | 24.9 | 26.6 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:05:00 | 135.26 | 209.42 | 825637.86 | 801843.18 | 3.71 | 3852.45 | 575.652 | -111.489 | 14 | 184 | 25.6 | 61.5 | 25.9 | 61 | 0 | 0 | - | - | 28.1 | 57.4 | 0 | 0 | 0 | 0 | 27.4 | 27.4 | 27.2 | 1.48 | 3 | 3.1 | 0 | 26.9 | 26.9 | 27.2 | 1.52 | 2.3 | 2.6 | 24.9 | 24.9 | 26.6 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:10:00 | 135.26 | 218.3 | 825637.86 | 801852.14 | 3.77 | 3852.45 | 575.652 | -123.847 | 14 | 184 | 25.6 | 61.6 | 25.9 | 61 | 0 | 0 | - | - | 28.1 | 57.4 | 0 | 0 | 0 | 0 | 27.4 | 27.3 | 27.2 | 1.48 | 2.9 | 3.1 | 0 | 26.9 | 26.9 | 27.2 | 1.52 | 2.2 | 2.6 | 24.9 | 24.9 | 26.5 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:15:00 | 135.28 | 226.18 | 825637.88 | 801859.86 | 3.83 | 3852.45 | 575.652 | -1.114 | 13 | 184 | 25.6 | 61.6 | 25.9 | 61 | 0 | 0 | - | - | 28.1 | 57.4 | 0 | 0 | 0 | 0 | 27.3 | 27.3 | 27.1 | 1.49 | 2.9 | 3 | 0 | 26.8 | 26.9 | 27.2 | 1.51 | 2.2 | 2.6 | 25 | 24.9 | 26.7 | 1.51 | 1.51 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:20:00 | 135.28 | 234.02 | 825637.88 | 801867.78 | 3.89 | 3896.73 | 531.372 | -151.754 | 13 | 184 | 25.6 | 61.6 | 25.9 | 61.1 | 0 | 0 | - | - | 28 | 57.5 | 0 | 0 | 0 | 0 | 27.4 | 27.4 | 27.2 | 1.49 | 3 | 3.1 | 0 | 26.8 | 26.9 | 27.2 | 1.52 | 2.2 | 2.6 | 25 | 25 | 26.8 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:25:00 | 135.28 | 250.56 | 825637.88 | 801884.4 | 3.96 | 3896.73 | 531.372 | -134.031 | 13 | 184 | 25.6 | 61.6 | 25.9 | 61.1 | 0 | 0 | - | - | 28 | 57.5 | 0 | 0 | 0 | 0 | 27.4 | 27.5 | 27.3 | 1.49 | 3 | 3 | 0 | 26.9 | 26.9 | 27.2 | 1.52 | 2.2 | 2.6 | 25 | 25 | 26.9 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:30:00 | 135.28 | 264.32 | 825637.88 | 801898.18 | 4.02 | 3896.73 | 531.372 | -196.307 | 12 | 184 | 25.6 | 61.6 | 25.9 | 61.1 | 0 | 0 | - | - | 28 | 57.6 | 0 | 0 | 0 | 0 | 27.5 | 27.6 | 27.4 | 1.49 | 3.1 | 3.2 | 0 | 26.9 | 27 | 27.3 | 1.52 | 2.3 | 2.6 | 25.1 | 25 | 27.1 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:35:00 | 135.28 | 280.48 | 825637.88 | 801914.44 | 4.08 | 3941.01 | 487.087 | -243.412 | 12 | 184 | 25.6 | 61.6 | 25.9 | 61.1 | 0 | 0 | - | - | 28 | 57.6 | 0 | 0 | 0 | 0 | 27.7 | 27.7 | 27.6 | 1.49 | 3.2 | 3.3 | 0 | 27.1 | 27.1 | 27.4 | 1.52 | 2.3 | 2.7 | 25.1 | 25.1 | 27.1 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:40:00 | 145.88 | 289.82 | 825649.16 | 801923.42 | 4.15 | 3933.63 | 494.468 | 406.895 | 12 | 184 | 25.6 | 61.6 | 25.9 | 61.1 | 0 | 0 | - | - | 28 | 57.6 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.7 | 1.49 | 3.3 | 3.4 | 0 | 27.2 | 27.2 | 27.4 | 1.52 | 2.4 | 2.7 | 25.1 | 25.1 | 27.2 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:45:00 | 180.78 | 289.82 | 825683.38 | 801923.42 | 4.22 | 3911.49 | 516.61 | 389.519 | 13 | 184 | 25.6 | 61.7 | 26 | 61.1 | 0 | 0 | - | - | 28.1 | 57.6 | 0 | 0 | 0 | 0 | 27.9 | 27.8 | 27.7 | 1.49 | 3.3 | 3.5 | 0 | 27.2 | 27.2 | 27.4 | 1.53 | 2.3 | 2.7 | 25.2 | 25.1 | 27.2 | 1.52 | 1.52 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:50:00 | 205 | 289.82 | 825708.14 | 801923.42 | 4.29 | 3881.97 | 546.132 | 345.02 | 14 | 184 | 25.7 | 61.6 | 26 | 61.1 | 0 | 0 | - | - | 28.1 | 57.6 | 0 | 0 | 0 | 0 | 27.9 | 27.9 | 27.7 | 1.49 | 3.3 | 3.4 | 0 | 27.2 | 27.2 | 27.5 | 1.52 | 2.3 | 2.7 | 25.2 | 25.2 | 27.2 | 1.52 | 1.52 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 05:55:00 | 242.98 | 289.82 | 825745.72 | 801923.42 | 4.36 | 3845.068 | 583.032 | 282.424 | 14 | 184 | 25.7 | 61.6 | 26 | 61.1 | 0 | 0 | - | - | 28.1 | 57.6 | 0 | 0 | 0 | 0 | 27.9 | 27.9 | 27.8 | 1.5 | 3.3 | 3.3 | 0 | 27.3 | 27.2 | 27.5 | 1.53 | 2.3 | 2.7 | 25.2 | 25.2 | 27.4 | 1.52 | 1.52 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:00:00 | 255.3 | 292.3 | 825757.9 | 801926.84 | 4.43 | 3837.688 | 590.412 | -265.064 | 15 | 184 | 25.7 | 61.6 | 26.1 | 61 | 0 | 0 | - | - | 28.1 | 57.6 | 0 | 0 | 0 | 0 | 28.1 | 28 | 28 | 1.5 | 3.4 | 3.5 | 0 | 27.4 | 27.3 | 27.6 | 1.53 | 2.4 | 2.8 | 25.2 | 25.2 | 27.5 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:05:00 | 255.3 | 312.38 | 825757.9 | 801946.26 | 4.49 | 3845.068 | 583.032 | -171.185 | 14 | 184 | 25.8 | 61.5 | 26 | 61.2 | 0 | 0 | - | - | 28.1 | 57.6 | 0 | 0 | 0 | 0 | 28.2 | 28.1 | 28.2 | 1.5 | 3.5 | 3.6 | 0 | 27.5 | 27.4 | 27.6 | 1.53 | 2.5 | 2.9 | 25.2 | 25.2 | 27.7 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:10:00 | 255.52 | 320.64 | 825758.22 | 801954.24 | 4.55 | 3867.21 | 560.892 | 49.942 | 14 | 184 | 25.8 | 61.5 | 25.9 | 61.4 | 0 | 0 | - | - | 28.1 | 57.6 | 0 | 0 | 0 | 0 | 28.2 | 28.1 | 28.2 | 1.5 | 3.5 | 3.6 | 0 | 27.5 | 27.5 | 27.7 | 1.53 | 2.5 | 2.9 | 25.2 | 25.2 | 27.7 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:15:00 | 260.04 | 321.14 | 825762.68 | 801954.74 | 4.61 | 3867.21 | 560.892 | 15.414 | 14 | 184 | 25.9 | 61.3 | 26.1 | 61 | 0 | 0 | - | - | 28.2 | 57.6 | 0 | 0 | 0 | 0 | 28.3 | 28.2 | 28.2 | 1.5 | 3.5 | 3.6 | 0 | 27.6 | 27.5 | 27.8 | 1.53 | 2.5 | 2.9 | 25.3 | 25.2 | 28 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:20:00 | 268.1 | 321.14 | 825770.88 | 801954.74 | 4.67 | 3845.068 | 583.032 | 106.665 | 14 | 184 | 26 | 61.3 | 26.3 | 60.8 | 0 | 0 | - | - | 28.2 | 57.6 | 0 | 0 | 0 | 0 | 28.3 | 28.2 | 28.2 | 1.5 | 3.5 | 3.6 | 0 | 27.6 | 27.5 | 27.8 | 1.53 | 2.5 | 2.9 | 25.2 | 25.3 | 28.1 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:25:00 | 283.82 | 321.14 | 825786.76 | 801954.74 | 4.74 | 3837.688 | 590.412 | 233.204 | 15 | 184 | 26 | 61.3 | 26.3 | 60.6 | 0 | 0 | - | - | 28.3 | 57.5 | 0 | 0 | 0 | 0 | 28.4 | 28.3 | 28.3 | 1.51 | 3.5 | 3.6 | 0 | 27.6 | 27.6 | 27.9 | 1.54 | 2.6 | 2.9 | 25.3 | 25.2 | 28.2 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:30:00 | 298.36 | 321.14 | 825801.18 | 801954.74 | 4.8 | 3822.926 | 605.172 | 111.625 | 15 | 184 | 26 | 61.2 | 26.4 | 60.5 | 0 | 0 | - | - | 28.3 | 57.5 | 0 | 0 | 0 | 0 | 28.4 | 28.3 | 28.3 | 1.51 | 3.6 | 3.6 | 0 | 27.7 | 27.7 | 28 | 1.54 | 2.6 | 3 | 25.3 | 25.2 | 28.3 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:35:00 | 311.72 | 321.14 | 825814.56 | 801954.74 | 4.86 | 3800.785 | 627.312 | 169.559 | 15 | 184 | 26.1 | 61 | 26.5 | 60.4 | 0 | 0 | - | - | 28.4 | 57.4 | 0 | 0 | 0 | 0 | 28.4 | 28.3 | 28.3 | 1.51 | 3.5 | 3.6 | 0 | 27.7 | 27.7 | 28.1 | 1.54 | 2.7 | 3 | 25.3 | 25.3 | 28.4 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:40:00 | 332.26 | 321.14 | 825835.26 | 801954.74 | 4.93 | 3793.404 | 634.692 | 268.824 | 16 | 184 | 26.2 | 60.9 | 26.5 | 60.3 | 0 | 0 | - | - | 28.4 | 57.4 | 0 | 0 | 0 | 0 | 28.5 | 28.4 | 28.4 | 1.51 | 3.6 | 3.6 | 0 | 27.8 | 27.8 | 28.2 | 1.54 | 2.7 | 3.1 | 25.3 | 25.3 | 28.7 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:45:00 | 364.9 | 321.14 | 825868.9 | 801954.74 | 5 | 3749.124 | 678.972 | 419.461 | 17 | 184 | 26.3 | 60.8 | 26.6 | 60.3 | 0 | 0 | - | - | 28.5 | 57.3 | 0 | 0 | 0 | 0 | 28.6 | 28.5 | 28.5 | 1.51 | 3.6 | 3.6 | 0 | 27.8 | 27.8 | 28.2 | 1.54 | 2.7 | 3.1 | 25.3 | 25.2 | 29.2 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:50:00 | 401.7 | 321.14 | 825905.22 | 801954.74 | 5.08 | 3712.224 | 715.872 | 359.25 | 17 | 184 | 26.4 | 60.6 | 26.7 | 60.1 | 0 | 0 | - | - | 28.6 | 57.2 | 0 | 0 | 0 | 0 | 28.7 | 28.7 | 28.8 | 1.51 | 3.7 | 3.8 | 0 | 28 | 27.9 | 28.4 | 1.54 | 2.8 | 3.2 | 25.3 | 25.3 | 29.8 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 06:55:00 | 431.56 | 321.14 | 825934.6 | 801954.74 | 5.15 | 3690.084 | 738.012 | 303.131 | 18 | 184 | 26.6 | 60.3 | 26.9 | 59.8 | 0 | 0 | - | - | 28.8 | 56.9 | 0 | 0 | 0 | 0 | 28.9 | 28.8 | 28.9 | 1.52 | 3.8 | 3.9 | 0 | 28.2 | 28.1 | 28.6 | 1.54 | 2.9 | 3.3 | 25.3 | 25.3 | 30.9 | 1.54 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:00:00 | 441.06 | 321.34 | 825943.66 | 801955.06 | 5.21 | 3682.704 | 745.392 | -77.908 | 18 | 184 | 26.9 | 59.8 | 27.1 | 59.4 | 0 | 0 | - | - | 29.1 | 56.7 | 0 | 0 | 0 | 0 | 29 | 28.9 | 29.1 | 1.52 | 3.9 | 3.9 | 0 | 28.3 | 28.2 | 28.8 | 1.54 | 3.1 | 3.4 | 25.4 | 25.3 | 32.8 | 1.55 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:05:00 | 441.06 | 344.7 | 825943.66 | 801979.14 | 5.28 | 3704.844 | 723.252 | -468.45 | 18 | 184 | 27.1 | 59.3 | 27.2 | 59.1 | 0 | 0 | - | - | 29.3 | 56.4 | 0 | 0 | 0 | 0 | 29.1 | 28.9 | 29.2 | 1.52 | 3.8 | 4 | 0 | 28.3 | 28.3 | 29 | 1.54 | 3.1 | 3.4 | 25.4 | 25.3 | 33.3 | 1.55 | 1.55 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:10:00 | 441.06 | 402.58 | 825943.66 | 802037.66 | 5.36 | 3763.884 | 664.212 | -970.141 | 16 | 184 | 27.3 | 59 | 27.4 | 59.8 | 0 | 0 | - | - | 29.6 | 56.1 | 0 | 0 | 0 | 0 | 29.2 | 29.1 | 29.4 | 1.52 | 4 | 4 | 0 | 28.5 | 28.4 | 29.2 | 1.54 | 3.2 | 3.6 | 25.4 | 25.4 | 32.6 | 1.55 | 1.55 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:15:00 | 441.06 | 469.22 | 825943.66 | 802103.78 | 5.44 | 3763.884 | 664.212 | -654.236 | 16 | 184 | 27.5 | 59.7 | 27.6 | 59.6 | 0 | 0 | - | - | 29.8 | 55.7 | 0 | 0 | 0 | 0 | 29.4 | 29.2 | 29.6 | 1.53 | 4 | 4.2 | 0 | 28.7 | 28.6 | 29.4 | 1.54 | 3.3 | 3.7 | 25.5 | 25.5 | 31.7 | 1.56 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:20:00 | 442.56 | 494.18 | 825945.24 | 802127.78 | 5.51 | 3778.644 | 649.452 | 80.156 | 15 | 184 | 27.6 | 59.5 | 27.7 | 59.4 | 0 | 0 | - | - | 29.9 | 55.5 | 0 | 0 | 0 | 0 | 29.6 | 29.3 | 29.7 | 1.53 | 4.1 | 4.2 | 0 | 28.8 | 28.7 | 29.6 | 1.55 | 3.4 | 3.8 | 25.7 | 25.7 | 33.3 | 1.56 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:25:00 | 443.02 | 505.7 | 825945.62 | 802140.14 | 5.57 | 3808.164 | 619.932 | -592.09 | 15 | 184 | 27.8 | 59.2 | 27.7 | 59.4 | 0 | 0 | - | - | 30.1 | 55.3 | 0 | 0 | 0 | 0 | 29.7 | 29.4 | 29.9 | 1.53 | 4.1 | 4.3 | 0 | 28.9 | 28.8 | 29.8 | 1.55 | 3.3 | 3.8 | 25.8 | 25.7 | 32.6 | 1.56 | 1.56 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:30:00 | 443.02 | 542.84 | 825945.62 | 802176.44 | 5.65 | 3837.688 | 590.412 | -207.622 | 14 | 184 | 27.9 | 59.1 | 27.8 | 59.3 | 0 | 0 | - | - | 30.2 | 55.2 | 0 | 0 | 0 | 0 | 29.8 | 29.4 | 29.9 | 1.54 | 4.1 | 4.4 | 0 | 29.1 | 28.9 | 30 | 1.56 | 3.4 | 4 | 25.8 | 25.8 | 32.7 | 1.56 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:35:00 | 452.6 | 545.26 | 825955.68 | 802178.86 | 5.71 | 3837.688 | 590.412 | 237.692 | 15 | 184 | 28 | 58.9 | 28 | 59.1 | 0 | 0 | - | - | 30.4 | 55 | 0 | 0 | 0 | 0 | 29.9 | 29.5 | 30 | 1.54 | 4 | 4.4 | 0 | 29.2 | 28.9 | 30.1 | 1.56 | 3.3 | 3.9 | 25.9 | 25.9 | 34 | 1.57 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:40:00 | 468.62 | 545.26 | 825971.36 | 802178.86 | 5.78 | 3815.545 | 612.552 | 81.671 | 15 | 184 | 28.1 | 58.8 | 28.1 | 58.9 | 0 | 0 | - | - | 30.5 | 54.9 | 0 | 0 | 0 | 0 | 30 | 29.7 | 30.2 | 1.54 | 4.2 | 4.4 | 0 | 29.3 | 29.1 | 30.4 | 1.56 | 3.4 | 3.9 | 26 | 25.9 | 35.8 | 1.57 | 1.57 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:45:00 | 473.3 | 545.26 | 825976.28 | 802178.86 | 5.84 | 3815.545 | 612.552 | 185.39 | 15 | 184 | 28.3 | 58.5 | 28.2 | 58.9 | 0 | 0 | - | - | 30.6 | 54.8 | 0 | 0 | 0 | 0 | 30.1 | 29.8 | 30.4 | 1.54 | 4.3 | 4.5 | 0 | 29.4 | 29.2 | 30.7 | 1.56 | 3.5 | 4 | 26 | 25.9 | 36.8 | 1.57 | 1.57 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:50:00 | 500.16 | 545.26 | 826002.94 | 802178.86 | 5.91 | 3778.644 | 649.452 | 191.823 | 16 | 184 | 28.5 | 58.3 | 28.3 | 58.6 | 0 | 0 | - | - | 30.8 | 54.6 | 0 | 0 | 0 | 0 | 30.3 | 30 | 30.6 | 1.55 | 4.3 | 4.6 | 0 | 29.6 | 29.3 | 31.1 | 1.57 | 3.5 | 4.1 | 26 | 25.9 | 37.7 | 1.57 | 1.57 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 07:55:00 | 537.94 | 545.26 | 826041.04 | 802178.86 | 5.98 | 3749.124 | 678.972 | 301.08 | 17 | 184 | 28.7 | 58 | 28.5 | 58.3 | 0 | 0 | - | - | 31 | 54.4 | 0 | 0 | 0 | 0 | 30.5 | 30.3 | 30.9 | 1.55 | 4.7 | 4.8 | 0 | 29.8 | 29.5 | 31.6 | 1.57 | 3.8 | 4.3 | 26 | 25.9 | 38.4 | 1.58 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:00:00 | 551.38 | 549.16 | 826053.98 | 802183.36 | 6.05 | 3734.364 | 693.732 | -307.723 | 17 | 184 | 28.9 | 57.7 | 28.7 | 58.1 | 0 | 0 | - | - | 31.3 | 54.1 | 0 | 0 | 0 | 0 | 30.8 | 30.6 | 31.3 | 1.55 | 4.8 | 5 | 0 | 30 | 29.8 | 32.1 | 1.57 | 3.9 | 4.4 | 26 | 25.9 | 39.5 | 1.58 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:05:00 | 551.38 | 575.56 | 826053.98 | 802209.5 | 6.11 | 3756.504 | 671.592 | -235.426 | 16 | 184 | 29.1 | 57.4 | 28.9 | 57.8 | 0 | 0 | - | - | 31.6 | 53.6 | 0 | 0 | 0 | 0 | 31.2 | 31 | 31.9 | 1.55 | 5.2 | 5.4 | 0 | 30.4 | 30.1 | 32.7 | 1.57 | 4.3 | 4.8 | 26 | 26 | 40.1 | 1.58 | 1.58 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:10:00 | 551.38 | 594.06 | 826053.98 | 802227.8 | 6.17 | 3778.644 | 649.452 | -4.392 | 16 | 184 | 29.4 | 57 | 29.1 | 57.6 | 0 | 0 | - | - | 32.1 | 53 | 0 | 0 | 0 | 0 | 31.5 | 31.3 | 32.3 | 1.55 | 5.5 | 5.7 | 0 | 30.6 | 30.4 | 33.2 | 1.58 | 4.5 | 5 | 26.1 | 26.1 | 39.4 | 1.58 | 1.58 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:15:00 | 551.38 | 595.64 | 826053.98 | 802229.24 | 6.22 | 3786.024 | 642.072 | -5.211 | 16 | 184 | 29.6 | 56.6 | 29.3 | 57.3 | 0 | 0 | - | - | 32.6 | 52.3 | 0 | 0 | 0 | 0 | 31.8 | 31.4 | 32.5 | 1.55 | 5.6 | 5.9 | 0 | 30.9 | 30.6 | 33.6 | 1.58 | 4.6 | 5.2 | 26.2 | 26.1 | 39 | 1.58 | 1.58 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:20:00 | 551.38 | 603.82 | 826053.98 | 802237.8 | 6.28 | 3793.404 | 634.692 | -257.55 | 16 | 184 | 29.9 | 56.3 | 29.5 | 57.1 | 0 | 0 | - | - | 33.1 | 51.7 | 0 | 0 | 0 | 0 | 32 | 31.5 | 32.7 | 1.55 | 5.7 | 6.1 | 0 | 31.1 | 30.8 | 33.9 | 1.58 | 4.8 | 5.5 | 26.2 | 26.1 | 39.1 | 1.58 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:25:00 | 551.38 | 624.54 | 826053.98 | 802258.26 | 6.34 | 3815.545 | 612.552 | -113.103 | 15 | 184 | 30.1 | 55.9 | 29.6 | 56.8 | 0 | 0 | - | - | 33.5 | 51.1 | 0 | 0 | 0 | 0 | 32.1 | 31.6 | 32.9 | 1.56 | 5.7 | 6.2 | 0 | 31.3 | 30.9 | 34.1 | 1.58 | 4.9 | 5.6 | 26.2 | 26.1 | 37.9 | 1.58 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:30:00 | 553.16 | 630.38 | 826055.76 | 802264.3 | 6.39 | 3815.545 | 612.552 | -230.977 | 15 | 184 | 30.3 | 55.6 | 29.8 | 56.6 | 0 | 0 | - | - | 33.8 | 50.6 | 0 | 0 | 0 | 0 | 32.2 | 31.6 | 33 | 1.55 | 5.8 | 6.3 | 0 | 31.4 | 30.9 | 34.2 | 1.58 | 4.9 | 5.8 | 26.2 | 26.2 | 37.4 | 1.58 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:35:00 | 553.16 | 661.6 | 826055.76 | 802295.52 | 6.46 | 3867.209 | 560.892 | -232.232 | 14 | 184 | 30.5 | 55.3 | 30 | 56.3 | 0 | 0 | - | - | 34.1 | 50.3 | 0 | 0 | 0 | 0 | 32.3 | 31.6 | 33.1 | 1.55 | 5.7 | 6.4 | 0 | 31.6 | 31 | 34.2 | 1.58 | 5 | 5.8 | 26.3 | 26.2 | 36.2 | 1.58 | 1.58 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:40:00 | 553.16 | 672.5 | 826055.76 | 802306.12 | 6.51 | 3874.59 | 553.512 | -15.739 | 13 | 184 | 30.6 | 55.1 | 30.1 | 56.2 | 0 | 0 | - | - | 34.2 | 50 | 0 | 0 | 0 | 0 | 32.4 | 31.6 | 33.1 | 1.55 | 5.7 | 6.4 | 0 | 31.7 | 31 | 34.2 | 1.58 | 4.9 | 5.9 | 26.3 | 26.3 | 36.1 | 1.58 | 1.58 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:45:00 | 559.76 | 672.98 | 826062.88 | 802306.58 | 6.56 | 3874.59 | 553.512 | 254.161 | 14 | 184 | 30.8 | 55 | 30.3 | 56.1 | 0 | 0 | - | - | 34.4 | 49.9 | 0 | 0 | 0 | 0 | 32.4 | 31.6 | 33.1 | 1.55 | 5.7 | 6.5 | 0 | 31.8 | 31 | 34.1 | 1.58 | 4.9 | 6 | 26.4 | 26.3 | 36.6 | 1.58 | 1.58 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:50:00 | 585.32 | 672.98 | 826089.26 | 802306.58 | 6.62 | 3845.069 | 583.032 | 469.535 | 14 | 184 | 31 | 54.8 | 30.4 | 55.9 | 0 | 0 | - | - | 34.5 | 49.8 | 0 | 0 | 0 | 0 | 32.4 | 31.5 | 33.1 | 1.56 | 5.6 | 6.5 | 0 | 31.8 | 31 | 34.1 | 1.58 | 4.9 | 6.1 | 26.4 | 26.4 | 37.2 | 1.58 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 08:55:00 | 628.68 | 672.98 | 826131.58 | 802306.58 | 6.69 | 3800.784 | 627.312 | 598.111 | 15 | 184 | 31.1 | 54.6 | 30.5 | 55.7 | 0 | 0 | - | - | 34.7 | 49.6 | 0 | 0 | 0 | 0 | 32.6 | 31.5 | 33.2 | 1.56 | 5.6 | 6.6 | 0 | 31.9 | 31 | 34.1 | 1.58 | 4.9 | 6.1 | 26.4 | 26.3 | 38.1 | 1.58 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:00:00 | 677.34 | 672.98 | 826180.62 | 802306.58 | 6.76 | 3756.504 | 671.592 | 338.05 | 16 | 184 | 31.3 | 54.3 | 30.7 | 55.5 | 0 | 0 | - | - | 35 | 49.2 | 0 | 0 | 0 | 0 | 32.7 | 31.6 | 33.4 | 1.56 | 5.6 | 6.7 | 0 | 32.1 | 31.1 | 34.1 | 1.58 | 5 | 6.4 | 26.4 | 26.3 | 38.8 | 1.59 | 1.58 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:05:00 | 693.78 | 672.98 | 826196.4 | 802306.58 | 6.81 | 3741.744 | 686.352 | 111.185 | 17 | 184 | 31.5 | 54 | 30.9 | 55.4 | 0 | 0 | - | - | 35.3 | 48.9 | 0 | 0 | 0 | 0 | 32.9 | 31.7 | 33.6 | 1.56 | 5.8 | 6.9 | 0 | 32.3 | 31.3 | 34.2 | 1.58 | 5.1 | 6.5 | 26.4 | 26.4 | 38.4 | 1.59 | 1.58 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:10:00 | 695.48 | 677.74 | 826198.4 | 802311.34 | 6.87 | 3749.124 | 678.972 | 142.462 | 17 | 184 | 31.7 | 53.8 | 31 | 55.2 | 0 | 0 | - | - | 35.6 | 48.5 | 0 | 0 | 0 | 0 | 32.9 | 31.7 | 33.6 | 1.56 | 5.8 | 6.9 | 0 | 32.3 | 31.2 | 34.5 | 1.58 | 5.1 | 6.6 | 26.5 | 26.4 | 37.7 | 1.59 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:15:00 | 726.02 | 677.74 | 826229.62 | 802311.34 | 6.93 | 3712.224 | 715.872 | 648.947 | 17 | 184 | 31.9 | 53.4 | 31.2 | 54.9 | 0 | 0 | - | - | 35.8 | 48.3 | 0 | 0 | 0 | 0 | 32.9 | 31.7 | 33.6 | 1.56 | 5.7 | 6.9 | 0 | 32.3 | 31.2 | 34.6 | 1.58 | 5.1 | 6.5 | 26.5 | 26.4 | 39.1 | 1.59 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:20:00 | 782.7 | 677.74 | 826286.66 | 802311.34 | 7 | 3660.564 | 767.534 | 662.86 | 19 | 184 | 32.1 | 53.2 | 31.5 | 54.6 | 0 | 0 | - | - | 36.1 | 48 | 0 | 0 | 0 | 0 | 33 | 31.7 | 33.7 | 1.56 | 5.8 | 7 | 0 | 32.5 | 31.3 | 34.6 | 1.58 | 5.1 | 6.7 | 26.6 | 26.4 | 37.6 | 1.59 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:25:00 | 838.36 | 677.74 | 826342.26 | 802311.34 | 7.07 | 3601.52 | 826.578 | 504.125 | 20 | 184 | 32.3 | 52.9 | 31.7 | 54.3 | 0 | 0 | - | - | 36.3 | 47.7 | 0 | 0 | 0 | 0 | 33.1 | 31.8 | 33.9 | 1.56 | 5.8 | 7 | 0 | 32.6 | 31.4 | 34.7 | 1.59 | 5.2 | 6.7 | 26.6 | 26.5 | 37.3 | 1.59 | 1.58 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:30:00 | 872.36 | 677.74 | 826375.06 | 802311.34 | 7.14 | 3579.378 | 848.718 | 227.457 | 21 | 184 | 32.4 | 52.7 | 31.8 | 54.2 | 0 | 0 | - | - | 36.4 | 47.6 | 0 | 0 | 0 | 0 | 33.1 | 31.8 | 33.9 | 1.56 | 5.8 | 7.1 | 0 | 32.6 | 31.3 | 34.7 | 1.58 | 5.2 | 6.8 | 26.6 | 26.5 | 37.6 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:35:00 | 884.82 | 678 | 826387.44 | 802311.6 | 7.2 | 3564.618 | 863.478 | 12.709 | 21 | 184 | 32.6 | 52.5 | 31.9 | 54.1 | 0 | 0 | - | - | 36.6 | 47.4 | 0 | 0 | 0 | 0 | 33.2 | 31.8 | 33.9 | 1.56 | 5.7 | 7.1 | 0 | 32.7 | 31.3 | 34.7 | 1.58 | 5.1 | 6.8 | 26.7 | 26.6 | 37.9 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:40:00 | 884.94 | 691.9 | 826387.54 | 802325.62 | 7.26 | 3579.378 | 848.718 | -82.473 | 21 | 184 | 32.8 | 52.3 | 32 | 53.9 | 0 | 0 | - | - | 36.7 | 47.2 | 0 | 0 | 0 | 0 | 33.3 | 31.9 | 34 | 1.56 | 5.8 | 7.2 | 0 | 32.8 | 31.4 | 34.8 | 1.58 | 5.2 | 7 | 26.7 | 26.6 | 37.6 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:45:00 | 885.3 | 699.84 | 826387.9 | 802333.68 | 7.32 | 3579.378 | 848.718 | -73.95 | 21 | 184 | 33 | 52.1 | 32.1 | 53.8 | 0 | 0 | - | - | 36.8 | 47.1 | 0 | 0 | 0 | 0 | 33.4 | 31.9 | 34.1 | 1.56 | 5.8 | 7.2 | 0 | 32.9 | 31.4 | 34.9 | 1.59 | 5.1 | 7 | 26.7 | 26.6 | 36.6 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:50:00 | 885.3 | 716.86 | 826387.9 | 802351.06 | 7.38 | 3579.378 | 848.718 | -218.853 | 20 | 184 | 33.1 | 51.9 | 32.2 | 53.6 | 0 | 0 | - | - | 36.9 | 47 | 0 | 0 | 0 | 0 | 33.4 | 31.9 | 34.1 | 1.56 | 5.8 | 7.3 | 0 | 32.9 | 31.4 | 34.9 | 1.59 | 5.1 | 7 | 26.7 | 26.7 | 36.3 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 09:55:00 | 901.64 | 719.62 | 826404.68 | 802353.22 | 7.44 | 3579.378 | 848.718 | 557.515 | 20 | 184 | 33.2 | 51.8 | 32.3 | 53.5 | 0 | 0 | - | - | 36.8 | 47 | 0 | 0 | 0 | 0 | 33.5 | 31.9 | 34.2 | 1.56 | 5.8 | 7.4 | 0 | 33 | 31.5 | 34.9 | 1.58 | 5.2 | 7.1 | 26.8 | 26.7 | 35.7 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:00:00 | 930.9 | 719.62 | 826433.66 | 802353.22 | 7.51 | 3557.238 | 870.858 | 6.605 | 21 | 184 | 33.3 | 51.8 | 32.4 | 53.5 | 0 | 0 | - | - | 36.8 | 47.1 | 0 | 0 | 0 | 0 | 33.5 | 31.8 | 34.1 | 1.56 | 5.8 | 7.5 | 0 | 33 | 31.5 | 34.8 | 1.59 | 5.2 | 7.2 | 26.8 | 26.7 | 35.4 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:05:00 | 940.12 | 719.62 | 826443.28 | 802353.22 | 7.56 | 3535.099 | 892.998 | 375.372 | 21 | 184 | 33.3 | 51.7 | 32.4 | 53.5 | 0 | 0 | - | - | 36.7 | 47.1 | 0 | 0 | 0 | 0 | 33.6 | 31.8 | 34.1 | 1.56 | 5.7 | 7.5 | 0 | 33.1 | 31.6 | 34.7 | 1.59 | 5.2 | 7.2 | 26.8 | 26.7 | 35.4 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:10:00 | 971.06 | 719.62 | 826473.98 | 802353.22 | 7.63 | 3520.338 | 907.758 | 306.603 | 22 | 184 | 33.3 | 51.7 | 32.5 | 53.5 | 0 | 0 | - | - | 36.6 | 47.3 | 0 | 0 | 0 | 0 | 33.6 | 31.8 | 34.1 | 1.56 | 5.7 | 7.5 | 0 | 33.1 | 31.6 | 34.6 | 1.59 | 5.2 | 7.2 | 26.8 | 26.7 | 35 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:15:00 | 1003.78 | 719.62 | 826507.06 | 802353.22 | 7.7 | 3483.438 | 944.658 | 450.49 | 23 | 184 | 33.3 | 51.9 | 32.7 | 53.2 | 0 | 0 | - | - | 36.6 | 47.4 | 0 | 0 | 0 | 0 | 33.4 | 31.8 | 33.9 | 1.56 | 5.6 | 7.4 | 0 | 32.9 | 31.5 | 34.6 | 1.58 | 5.1 | 7.1 | 26.8 | 26.8 | 35.6 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:20:00 | 1051.42 | 719.62 | 826554.7 | 802353.22 | 7.78 | 3439.158 | 988.938 | 526.06 | 24 | 184 | 33.3 | 52 | 32.9 | 52.9 | 0 | 0 | - | - | 36.5 | 47.4 | 0 | 0 | 0 | 0 | 33.4 | 31.8 | 33.9 | 1.56 | 5.7 | 7.4 | 0 | 33 | 31.5 | 34.5 | 1.58 | 5.1 | 7.1 | 26.9 | 26.8 | 35.9 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:25:00 | 1087.38 | 719.62 | 826590.74 | 802353.22 | 7.86 | 3402.258 | 1025.839 | 369.048 | 25 | 184 | 33.4 | 51.9 | 32.8 | 53.2 | 0 | 0 | - | - | 36.6 | 47.4 | 0 | 0 | 0 | 0 | 33.6 | 31.8 | 34.1 | 1.56 | 5.7 | 7.5 | 0 | 33.1 | 31.6 | 34.4 | 1.58 | 5.2 | 7.2 | 27 | 26.8 | 36.1 | 1.58 | 1.59 | 1.57 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:30:00 | 1104.94 | 719.62 | 826607.58 | 802353.22 | 7.92 | 3387.498 | 1040.601 | 23.37 | 25 | 184 | 33.9 | 51.4 | 32.8 | 53.2 | 0 | 0 | - | - | 36.6 | 47.4 | 0 | 0 | 0 | 0 | 33.6 | 31.8 | 34.1 | 1.56 | 5.7 | 7.5 | 0 | 33.1 | 31.7 | 34.5 | 1.59 | 5.1 | 7.2 | 27 | 26.9 | 35.8 | 1.59 | 1.59 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:35:00 | 1115.12 | 719.62 | 826617.84 | 802353.22 | 7.98 | 3372.737 | 1055.362 | 80.89 | 25 | 184 | 34.4 | 50.7 | 33.1 | 52.9 | 0 | 0 | - | - | 36.7 | 47.4 | 0 | 0 | 0 | 0 | 33.6 | 31.9 | 34.1 | 1.56 | 5.7 | 7.5 | 0 | 33.1 | 31.7 | 34.6 | 1.59 | 5.2 | 7.2 | 27 | 26.9 | 36.4 | 1.59 | 1.59 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:40:00 | 1128.72 | 719.62 | 826631.56 | 802353.22 | 8.05 | 3357.977 | 1070.124 | 111.555 | 26 | 184 | 34.3 | 50.6 | 33 | 53 | 0 | 0 | - | - | 36.8 | 47.2 | 0 | 0 | 0 | 0 | 33.6 | 31.9 | 34.1 | 1.56 | 5.8 | 7.6 | 0 | 33.1 | 31.7 | 34.6 | 1.59 | 5.2 | 7.3 | 27 | 26.9 | 35.9 | 1.59 | 1.59 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:45:00 | 1131.38 | 726.4 | 826633.98 | 802360.08 | 8.11 | 3357.977 | 1070.124 | -183.909 | 26 | 184 | 34.1 | 50.9 | 32.9 | 53.2 | 0 | 0 | - | - | 36.9 | 47.1 | 0 | 0 | 0 | 0 | 33.7 | 32 | 34.2 | 1.56 | 5.8 | 7.6 | 0 | 33.2 | 31.8 | 34.6 | 1.59 | 5.2 | 7.3 | 27.1 | 26.9 | 35.6 | 1.59 | 1.59 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:50:00 | 1142.46 | 729.26 | 826645.06 | 802362.86 | 8.18 | 3357.977 | 1070.124 | 415.408 | 26 | 184 | 34.1 | 51 | 33.1 | 52.9 | 0 | 0 | - | - | 36.9 | 47 | 0 | 0 | 0 | 0 | 33.8 | 32.1 | 34.3 | 1.56 | 5.8 | 7.7 | 0 | 33.4 | 31.9 | 34.7 | 1.59 | 5.3 | 7.4 | 27.1 | 27 | 35.4 | 1.59 | 1.59 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 10:55:00 | 1178.12 | 729.26 | 826681.3 | 802362.86 | 8.25 | 3298.932 | 1129.164 | 269.664 | 27 | 184 | 34.2 | 51 | 33.1 | 52.9 | 0 | 0 | - | - | 36.9 | 47.1 | 0 | 0 | 0 | 0 | 33.8 | 32.1 | 34.3 | 1.56 | 5.9 | 7.7 | 0 | 33.4 | 31.9 | 34.7 | 1.59 | 5.4 | 7.4 | 27.1 | 27 | 35.6 | 1.59 | 1.59 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:00:00 | 1202.42 | 729.26 | 826705.82 | 802362.86 | 8.33 | 3276.792 | 1151.304 | 443.158 | 27 | 184 | 34.2 | 51 | 33.1 | 53 | 0 | 0 | - | - | 36.9 | 47 | 0 | 0 | 0 | 0 | 34 | 32.2 | 34.4 | 1.56 | 6 | 7.8 | 0 | 33.6 | 32 | 34.7 | 1.59 | 5.4 | 7.6 | 27.1 | 27 | 35.5 | 1.59 | 1.59 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:05:00 | 1267.36 | 729.26 | 826770.8 | 802362.86 | 8.4 | 3210.372 | 1217.724 | 855.795 | 29 | 184 | 34.2 | 51 | 33.1 | 53 | 0 | 0 | - | - | 36.9 | 47 | 0 | 0 | 0 | 0 | 34.1 | 32.2 | 34.6 | 1.56 | 6 | 7.9 | 0 | 33.7 | 32.1 | 34.8 | 1.59 | 5.4 | 7.6 | 27.2 | 27.1 | 35.1 | 1.59 | 1.59 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:10:00 | 1330.44 | 729.26 | 826833.18 | 802362.88 | 8.48 | 3143.952 | 1284.15 | -14.053 | 30 | 184 | 34.2 | 51.1 | 33.2 | 53 | 0 | 0 | - | - | 36.9 | 47 | 0 | 0 | 0 | 0 | 34.1 | 32.3 | 34.6 | 1.56 | 6 | 8 | 0 | 33.7 | 32.1 | 34.8 | 1.59 | 5.4 | 7.7 | 27.2 | 27.1 | 35.7 | 1.59 | 1.6 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:15:00 | 1341 | 729.66 | 826843.98 | 802363.26 | 8.55 | 3136.572 | 1291.53 | 226.841 | 30 | 184 | 34.2 | 51 | 33.1 | 53.1 | 0 | 0 | - | - | 37 | 47 | 0 | 0 | 0 | 0 | 34.1 | 32.3 | 34.6 | 1.56 | 6.1 | 8 | 0 | 33.8 | 32.1 | 34.8 | 1.59 | 5.5 | 7.6 | 27.2 | 27.2 | 35.6 | 1.59 | 1.6 | 1.59 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:20:00 | 1361.32 | 729.66 | 826864.02 | 802363.26 | 8.63 | 3121.812 | 1306.29 | 66.22 | 31 | 184 | 34.2 | 51.1 | 33.2 | 53.2 | 0 | 0 | - | - | 37.1 | 47 | 0 | 0 | 0 | 0 | 34.3 | 32.3 | 34.7 | 1.56 | 6.1 | 8.1 | 0 | 33.9 | 32.2 | 34.9 | 1.6 | 5.5 | 7.9 | 27.3 | 27.2 | 35.6 | 1.59 | 1.6 | 1.59 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:25:00 | 1365.58 | 731.34 | 826868.5 | 802364.94 | 8.7 | 3107.052 | 1321.05 | 135.67 | 31 | 184 | 34.4 | 51 | 33.4 | 52.9 | 0 | 0 | - | - | 37.1 | 46.9 | 0 | 0 | 0 | 0 | 34.3 | 32.4 | 34.7 | 1.56 | 6.2 | 8.2 | 0 | 33.9 | 32.2 | 34.9 | 1.6 | 5.5 | 7.9 | 27.4 | 27.3 | 36.1 | 1.59 | 1.6 | 1.59 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:30:00 | 1402.34 | 731.34 | 826906.64 | 802364.94 | 8.78 | 3077.529 | 1350.57 | 889.135 | 32 | 184 | 34.5 | 50.8 | 33.4 | 52.9 | 0 | 0 | - | - | 37.3 | 46.7 | 0 | 0 | 0 | 0 | 34.4 | 32.5 | 34.9 | 1.57 | 6.2 | 8.2 | 0 | 34 | 32.3 | 35.1 | 1.6 | 5.5 | 7.8 | 27.4 | 27.3 | 36 | 1.59 | 1.6 | 1.59 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:35:00 | 1483.2 | 731.34 | 826987.8 | 802364.94 | 9.3 | 3003.726 | 1424.37 | 948.386 | 34 | 184 | 34.7 | 50.6 | 33.4 | 52.9 | 0 | 0 | - | - | 37.4 | 46.5 | 120 | 120 | 0 | 0 | 34.4 | 32.6 | 34.9 | 1.56 | 6.5 | 8.3 | 0 | 34.1 | 32.4 | 35.2 | 1.6 | 5.8 | 7.9 | 23.4 | 26.2 | 35.4 | 2.71 | 1.15 | 2.92 | 1.12 | 270 | 211 | 3120 | 3180
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:40:00 | 1575.64 | 731.34 | 827078.94 | 802364.94 | 10.36 | 2907.786 | 1520.312 | 1389.492 | 36 | 184 | 34.9 | 50.1 | 33.5 | 52.6 | 0 | 0 | - | - | 37.5 | 46.4 | 270 | 211 | 69.2 | 69.3 | 65.8 | 25.2 | 45.5 | 2.69 | 9.1 | 17.9 | 69.4 | 73.8 | 25.2 | 48.7 | 2.97 | 9.5 | 22.8 | 21.3 | 23.3 | 35.5 | 2.7 | 1.14 | 2.96 | 1.14 | 269 | 198 | 2871 | 2871
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:45:00 | 1692.64 | 731.34 | 827198.24 | 802364.94 | 11.19 | 2782.32 | 1645.776 | 1434.056 | 39 | 184 | 35.1 | 49.5 | 33.8 | 51.9 | 0 | 0 | - | - | 37.6 | 46.2 | 266 | 197 | 67.1 | 67.2 | 64.9 | 22.9 | 45.4 | 2.62 | 8.4 | 18.3 | 66.9 | 75.3 | 23.1 | 48.6 | 2.89 | 8.7 | 25.5 | 21.5 | 23.1 | 35.8 | 2.55 | 1.11 | 2.8 | 1.12 | 254 | 197 | 2271 | 2271
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:50:00 | 1821.86 | 731.34 | 827326.74 | 802364.94 | 11.91 | 2656.86 | 1771.236 | 1465.01 | 42 | 184 | 35.4 | 49.1 | 33.9 | 51.6 | 0 | 0 | - | - | 37.8 | 46.1 | 254 | 197 | 61.6 | 61.1 | 65.7 | 23.1 | 43 | 2.41 | 9.1 | 22.6 | 61.6 | 74 | 23.2 | 46.7 | 2.75 | 8.9 | 26.3 | 21.9 | 23.5 | 37 | 2.62 | 1.12 | 2.83 | 1.12 | 254 | 197 | 2275 | 2275
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 11:55:00 | 1943.34 | 731.34 | 827447.1 | 802364.94 | 12.63 | 2538.776 | 1889.322 | 1054.716 | 44 | 184 | 35.6 | 48.8 | 34.1 | 51.4 | 0 | 0 | - | - | 37.9 | 45.9 | 254 | 197 | 63 | 62.6 | 67.5 | 23.5 | 43.9 | 2.48 | 9.3 | 23.2 | 63 | 74.5 | 23.6 | 47.1 | 2.79 | 9.3 | 26.3 | 22.2 | 23.7 | 37.6 | 2.56 | 1.12 | 2.81 | 1.13 | 254 | 197 | 2275 | 2275
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:00:00 | 1998.9 | 731.34 | 827502.18 | 802364.94 | 13.35 | 2487.114 | 1940.982 | 441.297 | 46 | 185 | 35.8 | 48.6 | 34.2 | 51.2 | 0 | 0 | - | - | 38 | 45.7 | 254 | 197 | 62.9 | 63.1 | 67.8 | 23.8 | 43.8 | 2.51 | 9.6 | 23 | 62.9 | 74.6 | 23.9 | 47.2 | 2.81 | 9.4 | 26.1 | 22.3 | 23.9 | 36.5 | 2.54 | 1.12 | 2.79 | 1.13 | 254 | 197 | 2275 | 2275
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:05:00 | 2025.06 | 731.34 | 827528.18 | 802364.94 | 14.08 | 2464.974 | 1963.122 | 185.188 | 46 | 185 | 36 | 48.3 | 34.2 | 51.2 | 0 | 0 | - | - | 38.1 | 45.6 | 254 | 197 | 62.8 | 62.8 | 67.3 | 23.8 | 43.5 | 2.52 | 9.9 | 22.5 | 62.5 | 74.2 | 23.9 | 47 | 2.8 | 9.5 | 25.8 | 22.3 | 23.9 | 37.4 | 2.56 | 1.12 | 2.82 | 1.13 | 254 | 197 | 2313 | 2313
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:10:00 | 2031.3 | 732.44 | 827533.9 | 802366.28 | 14.79 | 2457.594 | 1970.502 | -168.253 | 46 | 185 | 36.1 | 48 | 34.2 | 51.1 | 0 | 0 | - | - | 38.1 | 45.5 | 254 | 197 | 62.2 | 62.2 | 67.5 | 23.9 | 43.1 | 2.48 | 9.7 | 23.3 | 62 | 74.5 | 24 | 47 | 2.79 | 9.5 | 26.3 | 22.2 | 23.8 | 34.8 | 2.55 | 1.12 | 2.79 | 1.13 | 254 | 197 | 2310 | 2310
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:15:00 | 2031.3 | 743.78 | 827533.9 | 802377.46 | 15.5 | 2472.354 | 1955.742 | -46.416 | 46 | 185 | 36.2 | 48 | 34.3 | 51 | 0 | 0 | - | - | 38.1 | 45.4 | 254 | 197 | 61.7 | 61.7 | 67.1 | 23.7 | 43.4 | 2.5 | 9.5 | 22.4 | 61.6 | 73.7 | 23.8 | 46.7 | 2.78 | 9.4 | 25.6 | 22.1 | 23.7 | 34.2 | 2.53 | 1.11 | 2.78 | 1.12 | 254 | 197 | 2310 | 2310
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:20:00 | 2038.66 | 745.3 | 827541.54 | 802378.9 | 16.21 | 2464.974 | 1963.122 | 139.918 | 46 | 185 | 36.1 | 48 | 34.2 | 51 | 0 | 0 | - | - | 38.2 | 45.4 | 254 | 197 | 61.7 | 61.7 | 66.8 | 23.6 | 43.1 | 2.48 | 9.8 | 22.5 | 61.7 | 73.7 | 23.7 | 46.7 | 2.78 | 9.4 | 25.6 | 21.9 | 23.6 | 36.1 | 2.55 | 1.11 | 2.8 | 1.12 | 254 | 197 | 2310 | 2310
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:25:00 | 2049.42 | 745.3 | 827552.24 | 802378.9 | 16.92 | 2450.214 | 1977.882 | 87.065 | 46 | 185 | 36 | 48 | 34.2 | 51 | 0 | 0 | - | - | 38.1 | 45.5 | 254 | 197 | 61.7 | 61.7 | 67.3 | 23.4 | 43.2 | 2.46 | 9.5 | 23.4 | 62.1 | 74.1 | 23.6 | 46.7 | 2.77 | 9.3 | 26.2 | 21.8 | 23.3 | 36.5 | 2.58 | 1.1 | 2.8 | 1.11 | 254 | 197 | 2310 | 2310
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:30:00 | 2051.56 | 751.3 | 827554.16 | 802385.32 | 17.63 | 2450.214 | 1977.882 | -339.059 | 46 | 185 | 35.8 | 48.1 | 34.1 | 51 | 0 | 0 | - | - | 38.1 | 45.4 | 254 | 197 | 62.7 | 62.8 | 67.6 | 23.2 | 43.7 | 2.52 | 9.6 | 22.7 | 62.6 | 74.2 | 23.4 | 46.9 | 2.79 | 9.4 | 26 | 21.7 | 23.2 | 36.6 | 2.52 | 1.11 | 2.78 | 1.12 | 254 | 197 | 2251 | 2262
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:35:00 | 2051.56 | 781.1 | 827554.16 | 802415.16 | 18.31 | 2472.354 | 1955.742 | -328.622 | 46 | 185 | 35.7 | 48.3 | 33.9 | 51.2 | 0 | 0 | - | - | 38 | 45.4 | 254 | 197 | 61.1 | 61.3 | 66.8 | 23.2 | 42.7 | 2.44 | 9.5 | 23.3 | 61.1 | 73.6 | 23.2 | 46.4 | 2.75 | 9.1 | 26 | 21.7 | 23.2 | 36.6 | 2.52 | 1.1 | 2.76 | 1.12 | 254 | 197 | 2128 | 2128
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:40:00 | 2051.56 | 820.92 | 827554.16 | 802454.96 | 18.95 | 2509.254 | 1918.842 | -392.351 | 45 | 185 | 35.5 | 48.4 | 33.7 | 51.4 | 0 | 0 | - | - | 38 | 45.4 | 254 | 197 | 61.1 | 60.8 | 66.9 | 23.1 | 43 | 2.47 | 9.5 | 22.8 | 60.6 | 73.3 | 23.2 | 46.3 | 2.75 | 9.1 | 25.7 | 21.8 | 23.2 | 36.6 | 2.48 | 1.11 | 2.73 | 1.14 | 254 | 197 | 2001 | 2001
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:45:00 | 2058 | 831.22 | 827561.08 | 802464.82 | 19.55 | 2524.014 | 1904.082 | 325.337 | 45 | 185 | 35.3 | 48.6 | 33.5 | 51.6 | 0 | 0 | - | - | 37.9 | 45.4 | 254 | 197 | 58.9 | 58.7 | 66 | 23.2 | 41.9 | 2.39 | 9.3 | 23.2 | 58.9 | 71.9 | 23.3 | 45.7 | 2.7 | 8.6 | 25 | 21.8 | 23.2 | 36.5 | 2.46 | 1.1 | 2.72 | 1.13 | 254 | 197 | 2013 | 2013
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:50:00 | 2068.78 | 842.5 | 827571.38 | 802476.86 | 20.16 | 2516.634 | 1911.462 | -430.838 | 45 | 185 | 35.2 | 48.7 | 33.4 | 51.7 | 0 | 0 | - | - | 37.9 | 45.4 | 254 | 197 | 58.4 | 58.7 | 65.9 | 23.2 | 41.8 | 2.4 | 9.4 | 23 | 58.4 | 71.4 | 23.2 | 45.6 | 2.7 | 8.7 | 24.6 | 21.7 | 23.1 | 36.6 | 2.49 | 1.11 | 2.72 | 1.13 | 254 | 197 | 2007 | 2007
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 12:55:00 | 2070.16 | 864.54 | 827573.06 | 802498.14 | 20.76 | 2546.157 | 1881.942 | 182.534 | 44 | 185 | 35 | 48.8 | 33.3 | 51.8 | 0 | 0 | - | - | 37.9 | 45.4 | 254 | 197 | 58.9 | 58.7 | 66 | 23.1 | 42.1 | 2.4 | 9.3 | 23.1 | 58.9 | 71.1 | 23.2 | 45.6 | 2.69 | 8.7 | 24.3 | 21.6 | 22.9 | 36.6 | 2.49 | 1.1 | 2.72 | 1.13 | 254 | 197 | 2010 | 2010
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:00:00 | 2073.32 | 874.9 | 827575.92 | 802508.82 | 21.37 | 2553.538 | 1874.562 | -338.129 | 44 | 185 | 34.9 | 48.9 | 33.2 | 51.8 | 0 | 0 | - | - | 37.8 | 45.3 | 254 | 197 | 58.8 | 58.7 | 66.1 | 22.9 | 42.2 | 2.42 | 9.2 | 22.9 | 58.9 | 71.1 | 23.1 | 45.7 | 2.7 | 8.6 | 24.3 | 21.4 | 22.8 | 36.6 | 2.5 | 1.1 | 2.72 | 1.12 | 254 | 197 | 2004 | 2004
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:05:00 | 2075.38 | 885.46 | 827578.12 | 802519.06 | 21.97 | 2568.3 | 1859.802 | 293.308 | 44 | 185 | 34.7 | 49 | 33 | 52 | 0 | 0 | - | - | 37.8 | 45.4 | 254 | 197 | 59.3 | 59.2 | 66.3 | 22.8 | 42.3 | 2.43 | 9.2 | 22.9 | 58.9 | 71.4 | 22.9 | 45.8 | 2.71 | 8.6 | 24.4 | 21.4 | 22.7 | 37 | 2.47 | 1.1 | 2.71 | 1.12 | 254 | 197 | 1978 | 1978
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:10:00 | 2110.62 | 885.46 | 827613.58 | 802519.06 | 22.58 | 2524.014 | 1904.082 | 327.208 | 45 | 185 | 34.6 | 49.1 | 32.9 | 52.1 | 0 | 0 | - | - | 37.7 | 45.4 | 254 | 197 | 58.3 | 58.2 | 65.9 | 22.7 | 41.7 | 2.4 | 9.2 | 23.1 | 58.3 | 71 | 22.8 | 45.4 | 2.69 | 8.6 | 24.3 | 21.2 | 22.6 | 36.6 | 2.44 | 1.09 | 2.7 | 1.11 | 254 | 197 | 2013 | 2010
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:15:00 | 2144.46 | 885.46 | 827647.46 | 802519.06 | 23.18 | 2494.494 | 1933.602 | 99.861 | 45 | 185 | 34.5 | 49.1 | 32.7 | 52.2 | 0 | 0 | - | - | 37.7 | 45.3 | 254 | 197 | 58.3 | 58.2 | 65.8 | 22.6 | 41.4 | 2.37 | 9.4 | 23.3 | 58.3 | 71 | 22.7 | 45.4 | 2.68 | 8.8 | 24.5 | 21.1 | 22.4 | 35.9 | 2.42 | 1.08 | 2.69 | 1.11 | 254 | 197 | 2055 | 2055
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:20:00 | 2145.34 | 896.62 | 827647.94 | 802530.66 | 23.8 | 2494.494 | 1933.602 | -516.947 | 45 | 185 | 34.4 | 49.2 | 32.6 | 52.3 | 0 | 0 | - | - | 37.6 | 45.3 | 254 | 197 | 58.3 | 58.2 | 65.6 | 22.3 | 41.3 | 2.37 | 9.5 | 23.2 | 58.3 | 71 | 22.4 | 45.2 | 2.67 | 8.7 | 24.6 | 20.8 | 22.2 | 35.6 | 2.46 | 1.08 | 2.7 | 1.1 | 254 | 197 | 2064 | 2064
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:25:00 | 2145.34 | 951 | 827647.94 | 802585.02 | 24.43 | 2553.538 | 1874.562 | -130.726 | 44 | 185 | 34.2 | 49.3 | 32.4 | 52.4 | 0 | 0 | - | - | 37.6 | 45.3 | 254 | 197 | 58.7 | 58.7 | 66 | 22.2 | 41.8 | 2.4 | 9.4 | 23.1 | 58.8 | 71 | 22.2 | 45.3 | 2.68 | 8.7 | 24.4 | 20.7 | 22.1 | 35.4 | 2.46 | 1.07 | 2.7 | 1.09 | 254 | 197 | 2074 | 2074
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:30:00 | 2147.84 | 952.74 | 827650.48 | 802586.34 | 25.09 | 2560.919 | 1867.182 | -25.842 | 44 | 185 | 34.1 | 49.2 | 32.3 | 52.4 | 0 | 0 | - | - | 37.5 | 45.2 | 254 | 197 | 58.7 | 58.7 | 66 | 22.1 | 41.7 | 2.39 | 9.2 | 23.4 | 58.8 | 71.6 | 22.1 | 45.4 | 2.68 | 8.6 | 25.2 | 20.2 | 21.8 | 35.4 | 2.56 | 1.06 | 2.75 | 1.06 | 254 | 197 | 2400 | 2400
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:35:00 | 2152.02 | 954.18 | 827654.62 | 802588 | 25.78 | 2560.919 | 1867.182 | -101.506 | 44 | 185 | 33.9 | 49.3 | 32.2 | 52.3 | 0 | 0 | - | - | 37.4 | 45.2 | 254 | 197 | 60.8 | 60.9 | 67.3 | 21.6 | 43 | 2.46 | 9 | 23.5 | 60.9 | 73.5 | 21.7 | 46.1 | 2.72 | 9.2 | 26.2 | 19.8 | 21.3 | 33.9 | 2.48 | 1.06 | 2.68 | 1.07 | 249 | 195 | 2166 | 2166
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:40:00 | 2152.02 | 978.22 | 827654.62 | 802612.98 | 26.43 | 2575.68 | 1852.422 | -634.707 | 43 | 185 | 33.8 | 49.3 | 32 | 52.5 | 0 | 0 | - | - | 37.3 | 45.3 | 249 | 195 | 58.4 | 58.4 | 65.9 | 21.3 | 41.9 | 2.4 | 8.8 | 23 | 58.4 | 72.2 | 21.4 | 45.1 | 2.66 | 8.7 | 26 | 19.7 | 21.2 | 33.4 | 2.47 | 1.04 | 2.67 | 1.06 | 249 | 195 | 2199 | 2199
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:45:00 | 2152.02 | 1039.88 | 827654.62 | 802674.86 | 27.09 | 2656.86 | 1771.236 | -905.471 | 42 | 185 | 33.7 | 49.3 | 31.8 | 52.6 | 0 | 0 | - | - | 37.2 | 45.3 | 249 | 195 | 57.8 | 57.9 | 66.1 | 21.2 | 41.9 | 2.38 | 9.1 | 23.5 | 57.8 | 72 | 21.3 | 44.9 | 2.64 | 8.9 | 26.1 | 19.6 | 21.1 | 32.2 | 2.41 | 1.03 | 2.66 | 1.05 | 249 | 195 | 2265 | 2265
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:50:00 | 2152.02 | 1109.42 | 827654.62 | 802743.78 | 27.76 | 2715.9 | 1712.196 | -523.821 | 40 | 185 | 33.4 | 49.4 | 31.5 | 52.8 | 0 | 0 | - | - | 37 | 45.4 | 249 | 195 | 57.7 | 57.9 | 65.2 | 20.8 | 40.6 | 2.33 | 9.5 | 23.4 | 58 | 71.6 | 20.9 | 44.6 | 2.63 | 9 | 25.7 | 19.2 | 20.7 | 31.7 | 2.4 | 1.02 | 2.65 | 1.04 | 249 | 195 | 2304 | 2304
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 13:55:00 | 2152.02 | 1128.72 | 827654.62 | 802762.5 | 28.07 | 2738.04 | 1690.056 | -141.465 | 40 | 185 | 33.1 | 49.7 | 31.2 | 53.2 | 0 | 0 | - | - | 36.8 | 45.6 | 243 | 195 | 57.7 | 57.4 | 64.9 | 20.6 | 40.4 | 2.28 | 8.4 | 23.9 | 57.4 | 71.1 | 20.7 | 44.4 | 2.58 | 8.1 | 25.9 | 21.9 | 21.8 | 31.3 | 1.82 | 1.22 | 1.77 | 1.42 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:00:00 | 2152.02 | 1158.78 | 827654.62 | 802793.36 | 28.24 | 2752.8 | 1675.296 | -445.158 | 39 | 185 | 32.8 | 50.5 | 30.9 | 53.9 | 0 | 0 | - | - | 36.6 | 45.8 | 0 | 0 | 0 | 0 | 45.9 | 28 | 34.9 | 1.71 | 5.9 | 16.9 | 0 | 35.3 | 39.8 | 33.4 | 1.69 | 17.1 | 7.3 | 23.3 | 23.2 | 31.1 | 1.57 | 1.46 | 1.51 | 1.47 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:05:00 | 2152.02 | 1184.46 | 827654.62 | 802818.76 | 28.4 | 2789.7 | 1638.396 | -446.214 | 38 | 185 | 32.4 | 51.2 | 30.7 | 54.4 | 0 | 0 | - | - | 36.3 | 46.1 | 0 | 0 | 0 | 0 | 30.9 | 39.2 | 33.6 | 1.52 | 15.9 | 6 | 0 | 29.7 | 45.2 | 31.2 | 1.49 | 21.6 | 5.9 | 23.8 | 23.7 | 30.6 | 1.52 | 1.48 | 1.49 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:10:00 | 2152.02 | 1215.34 | 827654.62 | 802849.12 | 28.57 | 2826.605 | 1601.496 | -362.805 | 38 | 185 | 32.1 | 51.8 | 30.4 | 55.1 | 0 | 0 | - | - | 36.1 | 46.5 | 0 | 0 | 0 | 0 | 29.2 | 41.7 | 32.9 | 1.48 | 18 | 4.9 | 0 | 30.1 | 43.6 | 31.1 | 1.5 | 19.7 | 6.4 | 24 | 23.9 | 28.2 | 1.51 | 1.49 | 1.5 | 1.5 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:15:00 | 2161.98 | 1222.96 | 827664.84 | 802856.56 | 28.73 | 2826.605 | 1601.496 | 266.205 | 38 | 185 | 31.6 | 52.6 | 30 | 55.8 | 0 | 0 | - | - | 35.6 | 46.9 | 0 | 0 | 0 | 0 | 28.9 | 40.4 | 32.1 | 1.49 | 16.5 | 4.6 | 0 | 30.3 | 41.4 | 30.6 | 1.5 | 17.4 | 6.3 | 24.2 | 24 | 26.6 | 1.51 | 1.5 | 1.5 | 1.5 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:20:00 | 2181.18 | 1222.96 | 827683.96 | 802856.56 | 28.88 | 2797.081 | 1631.016 | 78.601 | 38 | 185 | 31.2 | 53.3 | 29.6 | 56.5 | 0 | 0 | - | - | 35 | 47.6 | 0 | 0 | 0 | 0 | 28.6 | 39.1 | 30.8 | 1.49 | 15.1 | 4.2 | 0 | 29.9 | 39.2 | 29.7 | 1.5 | 15 | 6 | 24.2 | 24.1 | 26.2 | 1.51 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:25:00 | 2189.18 | 1223.2 | 827692.32 | 802856.8 | 29.02 | 2789.7 | 1638.396 | 224.826 | 38 | 185 | 30.5 | 54.5 | 29.2 | 57.1 | 0 | 0 | - | - | 34.4 | 48.5 | 0 | 0 | 0 | 0 | 28.2 | 37.4 | 29.9 | 1.49 | 13.3 | 3.9 | 0 | 29.6 | 36.7 | 29.1 | 1.51 | 12.5 | 5.5 | 24.2 | 24.1 | 25.8 | 1.51 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:30:00 | 2234.92 | 1223.2 | 827739.52 | 802856.8 | 29.17 | 2745.42 | 1682.676 | 965.576 | 39 | 185 | 29.9 | 55.5 | 28.9 | 57.8 | 0 | 0 | - | - | 33.7 | 49.3 | 0 | 0 | 0 | 0 | 28.1 | 35.9 | 29.3 | 1.49 | 11.8 | 3.8 | 0 | 29.2 | 34.9 | 28.4 | 1.51 | 10.6 | 5.1 | 24.3 | 24.2 | 26.3 | 1.52 | 1.51 | 1.51 | 1.51 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:35:00 | 2316.7 | 1223.2 | 827821.62 | 802856.8 | 29.32 | 2664.24 | 1763.856 | 913.829 | 41 | 185 | 29.6 | 56 | 28.5 | 58.4 | 0 | 0 | - | - | 33.1 | 50.1 | 0 | 0 | 0 | 0 | 27.8 | 35.1 | 28.7 | 1.49 | 10.8 | 3.4 | 0 | 28.7 | 33.7 | 27.8 | 1.51 | 9.3 | 4.5 | 24.4 | 24.3 | 26.6 | 1.52 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:40:00 | 2388.72 | 1223.2 | 827891.74 | 802856.8 | 29.47 | 2605.2 | 1822.902 | 816.199 | 43 | 185 | 29.5 | 56.3 | 28.3 | 58.9 | 0 | 0 | - | - | 32.7 | 50.7 | 0 | 0 | 0 | 0 | 27.7 | 34.6 | 28.4 | 1.5 | 10.1 | 3.1 | 0 | 28.4 | 33.1 | 27.5 | 1.52 | 8.4 | 4 | 24.6 | 24.5 | 26.7 | 1.53 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:45:00 | 2443.48 | 1223.2 | 827946.44 | 802856.8 | 29.6 | 2546.157 | 1881.942 | 252.055 | 44 | 185 | 29.3 | 56.6 | 28.2 | 59.3 | 0 | 0 | - | - | 32.3 | 51.2 | 0 | 0 | 0 | 0 | 27.8 | 33.9 | 28.2 | 1.51 | 9.3 | 3 | 0 | 28.2 | 32.6 | 27.3 | 1.53 | 7.8 | 3.7 | 24.8 | 24.8 | 26.7 | 1.54 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:50:00 | 2467.16 | 1223.2 | 827970.5 | 802856.8 | 29.73 | 2516.634 | 1911.462 | 377.448 | 45 | 185 | 29.1 | 56.9 | 28.1 | 59.5 | 0 | 0 | - | - | 32.1 | 51.6 | 0 | 0 | 0 | 0 | 27.8 | 33.1 | 28.2 | 1.51 | 8.3 | 2.9 | 0 | 28.2 | 32.1 | 27.3 | 1.54 | 7.1 | 3.4 | 25 | 24.9 | 26.4 | 1.55 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 14:55:00 | 2505.26 | 1223.2 | 828008.36 | 802856.8 | 29.86 | 2479.734 | 1948.362 | 323.312 | 46 | 185 | 28.9 | 57.3 | 28 | 59.8 | 0 | 0 | - | - | 31.8 | 52 | 0 | 0 | 0 | 0 | 27.9 | 32.4 | 28.1 | 1.52 | 7.3 | 2.8 | 0 | 28.1 | 31.7 | 27.2 | 1.54 | 6.5 | 3.1 | 25.2 | 25.1 | 26.6 | 1.55 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:00:00 | 2511.44 | 1232.48 | 828014.04 | 802866.98 | 29.98 | 2479.734 | 1948.362 | -216.24 | 46 | 185 | 28.6 | 57.9 | 27.9 | 59 | 0 | 0 | - | - | 31.6 | 52.3 | 0 | 0 | 0 | 0 | 27.9 | 31.6 | 27.9 | 1.53 | 6.4 | 2.7 | 0 | 27.9 | 31.2 | 27.2 | 1.55 | 5.8 | 2.8 | 25.2 | 25.2 | 26.5 | 1.55 | 1.55 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:05:00 | 2518.76 | 1238.34 | 828021.54 | 802871.94 | 30.09 | 2479.734 | 1948.362 | 344.101 | 46 | 185 | 28.5 | 58.3 | 27.9 | 59.1 | 0 | 0 | - | - | 31.4 | 52.6 | 0 | 0 | 0 | 0 | 27.9 | 30.9 | 27.8 | 1.53 | 5.7 | 2.6 | 0 | 27.8 | 30.7 | 27.2 | 1.55 | 5.2 | 2.6 | 25.3 | 25.2 | 26.2 | 1.56 | 1.55 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:10:00 | 2526.84 | 1242.66 | 828029.64 | 802876.26 | 30.19 | 2479.734 | 1948.362 | 86.883 | 46 | 185 | 28.3 | 58.8 | 27.8 | 59.3 | 0 | 0 | - | - | 31.2 | 52.9 | 0 | 0 | 0 | 0 | 27.9 | 30.4 | 27.7 | 1.53 | 5.2 | 2.6 | 0 | 27.7 | 30.3 | 27.1 | 1.55 | 4.9 | 2.6 | 25.3 | 25.3 | 25.7 | 1.55 | 1.55 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:15:00 | 2544.82 | 1242.66 | 828048.48 | 802876.26 | 30.29 | 2457.594 | 1970.502 | 385.46 | 46 | 185 | 28.1 | 59.1 | 27.7 | 59.5 | 0 | 0 | - | - | 31 | 53.1 | 0 | 0 | 0 | 0 | 27.8 | 29.9 | 27.6 | 1.53 | 4.8 | 2.6 | 0 | 27.6 | 29.7 | 26.9 | 1.55 | 4.3 | 2.3 | 25.3 | 25.3 | 25.7 | 1.55 | 1.54 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:20:00 | 2560.58 | 1242.66 | 828063.38 | 802876.26 | 30.39 | 2450.214 | 1977.882 | 188.769 | 46 | 185 | 28 | 59.4 | 27.6 | 59.7 | 0 | 0 | - | - | 30.8 | 53.4 | 0 | 0 | 0 | 0 | 27.7 | 29.4 | 27.3 | 1.52 | 4.4 | 2.6 | 0 | 27.4 | 29.2 | 26.7 | 1.55 | 3.8 | 2.3 | 25.4 | 25.3 | 25.2 | 1.54 | 1.54 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:25:00 | 2574.64 | 1242.66 | 828077.4 | 802876.26 | 30.49 | 2435.454 | 1992.642 | 127.607 | 47 | 185 | 27.8 | 59.8 | 27.6 | 59.9 | 0 | 0 | - | - | 30.6 | 53.6 | 0 | 0 | 0 | 0 | 27.6 | 29.1 | 27.2 | 1.51 | 4.1 | 2.7 | 0 | 27.2 | 28.8 | 26.7 | 1.55 | 3.4 | 2.2 | 25.4 | 25.4 | 25.2 | 1.53 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:30:00 | 2591.66 | 1242.66 | 828094.46 | 802876.26 | 30.58 | 2413.314 | 2014.782 | 188.335 | 47 | 185 | 27.6 | 59.1 | 27.5 | 59.9 | 0 | 0 | - | - | 30.4 | 53.9 | 0 | 0 | 0 | 0 | 27.3 | 28.7 | 26.9 | 1.5 | 3.8 | 2.7 | 0 | 27 | 28.4 | 26.4 | 1.55 | 3.1 | 2 | 25.4 | 25.4 | 25.1 | 1.52 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:35:00 | 2595.76 | 1245.76 | 828098.36 | 802879.5 | 30.67 | 2413.314 | 2014.782 | -117.849 | 47 | 185 | 27.5 | 59.5 | 27.4 | 60.2 | 0 | 0 | - | - | 30.3 | 54.1 | 0 | 0 | 0 | 0 | 27.2 | 28.3 | 26.8 | 1.5 | 3.5 | 2.6 | 0 | 26.8 | 28 | 26.3 | 1.54 | 2.8 | 1.9 | 25.5 | 25.5 | 25.1 | 1.52 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:40:00 | 2595.76 | 1252.8 | 828098.36 | 802886.48 | 30.75 | 2428.074 | 2000.022 | -66.459 | 47 | 185 | 27.4 | 59.8 | 27.3 | 60.3 | 0 | 0 | - | - | 30.1 | 54.5 | 0 | 0 | 0 | 0 | 27.2 | 28.2 | 26.8 | 1.5 | 3.2 | 2.5 | 0 | 26.7 | 27.8 | 26.2 | 1.54 | 2.5 | 1.8 | 25.5 | 25.5 | 25.3 | 1.52 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:45:00 | 2595.9 | 1256.16 | 828098.54 | 802889.76 | 30.84 | 2428.074 | 2000.022 | 25.033 | 47 | 185 | 27.3 | 60.1 | 27.1 | 60.8 | 0 | 0 | - | - | 30 | 54.8 | 0 | 0 | 0 | 0 | 27.1 | 28 | 26.8 | 1.5 | 3.1 | 2.4 | 0 | 26.7 | 27.6 | 26.2 | 1.54 | 2.3 | 1.7 | 25.6 | 25.5 | 25.6 | 1.53 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:50:00 | 2596.46 | 1257.6 | 828099.08 | 802891.2 | 30.91 | 2428.074 | 2000.022 | 4.305 | 47 | 185 | 27.1 | 60.3 | 27 | 61.1 | 0 | 0 | - | - | 29.9 | 55 | 0 | 0 | 0 | 0 | 27 | 27.8 | 26.7 | 1.5 | 3 | 2.3 | 0 | 26.6 | 27.4 | 26.2 | 1.54 | 2.1 | 1.6 | 25.6 | 25.5 | 25.8 | 1.53 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 15:55:00 | 2597.48 | 1260.14 | 828100.08 | 802894 | 30.99 | 2428.074 | 2000.022 | -134.031 | 47 | 185 | 27.1 | 60.4 | 27.1 | 60.9 | 0 | 0 | - | - | 29.8 | 55.2 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.7 | 1.51 | 2.8 | 2.1 | 0 | 26.5 | 27.3 | 26.3 | 1.55 | 1.9 | 1.5 | 25.6 | 25.6 | 25.9 | 1.53 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:00:00 | 2597.88 | 1264.5 | 828100.56 | 802898.1 | 31.06 | 2435.454 | 1992.642 | 106.806 | 47 | 185 | 27 | 60.6 | 27.1 | 60.8 | 0 | 0 | - | - | 29.7 | 55.3 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.8 | 1.51 | 2.8 | 2.1 | 0 | 26.5 | 27.2 | 26.3 | 1.54 | 1.9 | 1.6 | 25.6 | 25.6 | 26.1 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:05:00 | 2606.44 | 1265.94 | 828109.5 | 802899.54 | 31.14 | 2428.074 | 2000.022 | 457.519 | 47 | 185 | 27 | 60.8 | 27.1 | 60.9 | 0 | 0 | - | - | 29.7 | 55.4 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.8 | 1.51 | 2.7 | 2 | 0 | 26.5 | 27.2 | 26.4 | 1.55 | 1.9 | 1.5 | 25.6 | 25.6 | 26.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:10:00 | 2643.48 | 1265.94 | 828146.78 | 802899.54 | 31.23 | 2391.174 | 2036.922 | 391.189 | 48 | 185 | 26.9 | 60.9 | 27 | 61.1 | 0 | 0 | - | - | 29.6 | 55.5 | 0 | 0 | 0 | 0 | 26.9 | 27.6 | 26.8 | 1.51 | 2.6 | 2 | 0 | 26.5 | 27.2 | 26.5 | 1.55 | 1.8 | 1.5 | 25.6 | 25.6 | 26.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:15:00 | 2674.64 | 1265.94 | 828177.76 | 802899.54 | 31.31 | 2361.654 | 2066.446 | 296.841 | 49 | 185 | 26.9 | 61 | 27 | 61.2 | 0 | 0 | - | - | 29.6 | 55.6 | 0 | 0 | 0 | 0 | 26.9 | 27.6 | 26.9 | 1.51 | 2.6 | 2 | 0 | 26.5 | 27.2 | 26.5 | 1.55 | 1.8 | 1.6 | 25.7 | 25.6 | 26.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:20:00 | 2699.9 | 1265.94 | 828202.66 | 802899.54 | 31.38 | 2339.513 | 2088.588 | 319.302 | 49 | 185 | 26.8 | 61.2 | 27 | 61.2 | 0 | 0 | - | - | 29.5 | 55.6 | 0 | 0 | 0 | 0 | 26.9 | 27.6 | 26.9 | 1.51 | 2.5 | 1.9 | 0 | 26.5 | 27.2 | 26.6 | 1.55 | 1.8 | 1.5 | 25.7 | 25.7 | 26.1 | 1.53 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:25:00 | 2723.86 | 1265.94 | 828226.64 | 802899.54 | 31.46 | 2302.608 | 2125.488 | 136.793 | 50 | 185 | 26.8 | 61.3 | 27 | 61.3 | 0 | 0 | - | - | 29.5 | 55.7 | 0 | 0 | 0 | 0 | 26.8 | 27.6 | 26.8 | 1.51 | 2.4 | 2 | 0 | 26.5 | 27.2 | 26.6 | 1.54 | 1.7 | 1.6 | 25.8 | 25.8 | 25.8 | 1.53 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:30:00 | 2737.92 | 1265.94 | 828240.76 | 802899.54 | 31.53 | 2295.228 | 2132.868 | 191.181 | 50 | 185 | 26.7 | 61.5 | 26.9 | 61.4 | 0 | 0 | - | - | 29.4 | 55.8 | 0 | 0 | 0 | 0 | 26.7 | 27.4 | 26.7 | 1.51 | 2.4 | 1.9 | 0 | 26.4 | 27 | 26.6 | 1.54 | 1.5 | 1.5 | 25.8 | 25.8 | 25.7 | 1.53 | 1.55 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:35:00 | 2756.12 | 1265.94 | 828259.24 | 802899.54 | 31.6 | 2273.088 | 2155.008 | 231.273 | 51 | 185 | 26.7 | 61.6 | 26.9 | 61.5 | 0 | 0 | - | - | 29.4 | 55.9 | 0 | 0 | 0 | 0 | 26.7 | 27.4 | 26.7 | 1.5 | 2.3 | 1.9 | 0 | 26.3 | 26.9 | 26.4 | 1.54 | 1.5 | 1.5 | 25.9 | 25.9 | 25.7 | 1.53 | 1.54 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:40:00 | 2776.54 | 1265.94 | 828279.64 | 802899.54 | 31.67 | 2258.328 | 2169.768 | 253.776 | 51 | 185 | 26.6 | 61.8 | 26.8 | 61.6 | 0 | 0 | - | - | 29.3 | 56 | 0 | 0 | 0 | 0 | 26.6 | 27.3 | 26.6 | 1.5 | 2.3 | 2 | 0 | 26.2 | 26.8 | 26.3 | 1.53 | 1.4 | 1.5 | 25.9 | 26 | 25.7 | 1.52 | 1.54 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:45:00 | 2797.08 | 1265.94 | 828300.2 | 802899.54 | 31.73 | 2214.048 | 2214.048 | 267.483 | 52 | 185 | 26.6 | 61.8 | 26.8 | 61.8 | 0 | 0 | - | - | 29.2 | 56.2 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.6 | 1.5 | 2.3 | 1.8 | 0 | 26.2 | 26.8 | 26.3 | 1.54 | 1.3 | 1.5 | 26 | 26 | 25.8 | 1.53 | 1.54 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:50:00 | 2811.88 | 1265.94 | 828314.64 | 802899.54 | 31.8 | 2199.288 | 2228.808 | 90.152 | 52 | 185 | 26.5 | 62 | 26.7 | 61.9 | 0 | 0 | - | - | 29.2 | 56.2 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.6 | 1.5 | 2.3 | 1.9 | 0 | 26.2 | 26.8 | 26.2 | 1.53 | 1.3 | 1.4 | 26.1 | 26.1 | 25.8 | 1.52 | 1.54 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 16:55:00 | 2814.2 | 1271.06 | 828316.8 | 802905.08 | 31.86 | 2191.908 | 2236.188 | -185.107 | 52 | 185 | 26.5 | 62.1 | 26.8 | 61.9 | 0 | 0 | - | - | 29.1 | 56.3 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.6 | 1.5 | 2.2 | 1.8 | 0 | 26.2 | 26.9 | 26.2 | 1.53 | 1.3 | 1.4 | 26.1 | 26.1 | 25.8 | 1.52 | 1.54 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:00:00 | 2814.2 | 1302.6 | 828316.8 | 802936.82 | 31.94 | 2214.048 | 2214.048 | -441.307 | 51 | 185 | 26.5 | 62.2 | 26.7 | 62 | 0 | 0 | - | - | 29.1 | 56.4 | 0 | 0 | 0 | 0 | 26.3 | 27.2 | 26.4 | 1.5 | 2.2 | 1.8 | 0 | 26.1 | 26.8 | 26.2 | 1.53 | 1.3 | 1.4 | 26.1 | 26.1 | 25.8 | 1.52 | 1.54 | 1.52 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:05:00 | 2814.2 | 1320.28 | 828316.8 | 802953.92 | 32 | 2273.088 | 2155.008 | -4.438 | 51 | 185 | 26.5 | 62.3 | 26.7 | 62.1 | 0 | 0 | - | - | 29 | 56.5 | 0 | 0 | 0 | 0 | 26.3 | 27.2 | 26.4 | 1.5 | 2.2 | 1.8 | 0 | 26.1 | 26.8 | 26.2 | 1.53 | 1.2 | 1.4 | 26.1 | 26.1 | 25.7 | 1.52 | 1.54 | 1.52 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:10:00 | 2814.82 | 1321.8 | 828317.42 | 802955.5 | 32.06 | 2273.088 | 2155.008 | -50.679 | 51 | 185 | 26.4 | 62.4 | 26.8 | 62 | 0 | 0 | - | - | 28.9 | 56.7 | 0 | 0 | 0 | 0 | 26.2 | 27.1 | 26.4 | 1.49 | 2.2 | 1.8 | 0 | 26.1 | 26.7 | 26.2 | 1.53 | 1.2 | 1.4 | 26.2 | 26.2 | 25.7 | 1.52 | 1.54 | 1.52 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:15:00 | 2814.88 | 1326.56 | 828317.48 | 802960.3 | 32.12 | 2273.088 | 2155.008 | -108.532 | 50 | 185 | 26.4 | 62.5 | 26.7 | 62 | 0 | 0 | - | - | 28.9 | 56.8 | 0 | 0 | 0 | 0 | 26.2 | 27.1 | 26.4 | 1.49 | 2.2 | 1.7 | 0 | 25.9 | 26.7 | 26.2 | 1.53 | 1.2 | 1.3 | 26.2 | 26.2 | 25.7 | 1.52 | 1.54 | 1.52 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:20:00 | 2814.88 | 1339.28 | 828317.48 | 802973.28 | 32.19 | 2273.088 | 2155.008 | -194.656 | 50 | 185 | 26.4 | 62.5 | 26.6 | 62.2 | 0 | 0 | - | - | 28.9 | 56.9 | 0 | 0 | 0 | 0 | 26.2 | 27.1 | 26.4 | 1.5 | 2.2 | 1.6 | 0 | 25.9 | 26.7 | 26.2 | 1.53 | 1.1 | 1.2 | 26.2 | 26.2 | 25.7 | 1.52 | 1.53 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:25:00 | 2814.88 | 1359.74 | 828317.48 | 802993.46 | 32.25 | 2302.608 | 2125.488 | -230.122 | 50 | 185 | 26.4 | 62.6 | 26.6 | 62.4 | 0 | 0 | - | - | 28.8 | 57 | 0 | 0 | 0 | 0 | 26.2 | 27.1 | 26.4 | 1.5 | 2.3 | 1.6 | 0 | 25.9 | 26.7 | 26.2 | 1.53 | 1.2 | 1.3 | 26.2 | 26.2 | 25.9 | 1.52 | 1.53 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:30:00 | 2814.88 | 1380.82 | 828317.48 | 803015.02 | 32.32 | 2317.37 | 2110.728 | -282.469 | 49 | 185 | 26.4 | 62.6 | 26.5 | 62.5 | 0 | 0 | - | - | 28.8 | 57.1 | 0 | 0 | 0 | 0 | 26.2 | 27.1 | 26.4 | 1.5 | 2.3 | 1.7 | 0 | 25.9 | 26.7 | 26.2 | 1.53 | 1.2 | 1.3 | 26.2 | 26.2 | 25.9 | 1.52 | 1.53 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:35:00 | 2814.88 | 1407.22 | 828317.48 | 803041.38 | 32.44 | 2346.894 | 2081.208 | -340.377 | 48 | 185 | 26.4 | 62.6 | 26.5 | 62.6 | 0 | 0 | - | - | 28.7 | 57.3 | 0 | 0 | -59.9 | -59.9 | 26.2 | 27.1 | 26.5 | 1.5 | 2.3 | 1.6 | -60.3 | 25.9 | 26.7 | 26.2 | 1.53 | 1.2 | 1.4 | 26.1 | 26.1 | 25.3 | 1.52 | 1.53 | 1.52 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:40:00 | 2814.88 | 1436.64 | 828317.48 | 803070.58 | 32.51 | 2369.034 | 2059.065 | -379.38 | 48 | 185 | 26.4 | 62.6 | 26.5 | 62.6 | 0 | 0 | - | - | 28.7 | 57.3 | 0 | 0 | 0 | 0 | 26.1 | 26.8 | 26.3 | 1.5 | 2.1 | 1.5 | 0 | 25.7 | 26.4 | 26.2 | 1.53 | 1 | 1.3 | 26.1 | 26.1 | 25.5 | 1.52 | 1.53 | 1.52 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:45:00 | 2814.88 | 1464.48 | 828317.48 | 803098.6 | 32.58 | 2398.554 | 2029.542 | -327.284 | 47 | 185 | 26.4 | 62.7 | 26.5 | 62.6 | 0 | 0 | - | - | 28.7 | 57.5 | 0 | 0 | 0 | 0 | 26 | 26.8 | 26.2 | 1.5 | 2.1 | 1.5 | 0 | 25.7 | 26.4 | 26.1 | 1.53 | 1 | 1.2 | 26.1 | 26.1 | 25.6 | 1.52 | 1.53 | 1.52 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:50:00 | 2814.88 | 1488.54 | 828317.48 | 803122.56 | 32.65 | 2435.454 | 1992.642 | -225.845 | 47 | 185 | 26.4 | 62.7 | 26.5 | 62.6 | 0 | 0 | - | - | 28.6 | 57.5 | 0 | 0 | 0 | 0 | 26 | 26.8 | 26.2 | 1.5 | 2.2 | 1.4 | 0 | 25.7 | 26.4 | 26.1 | 1.53 | 1 | 1.1 | 26.1 | 26.1 | 25.8 | 1.52 | 1.53 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 17:55:00 | 2814.88 | 1505.2 | 828317.48 | 803139 | 32.72 | 2457.594 | 1970.502 | -257.876 | 46 | 185 | 26.4 | 62.7 | 26.5 | 62.6 | 0 | 0 | - | - | 28.6 | 57.6 | 0 | 0 | 0 | 0 | 26 | 26.9 | 26.3 | 1.5 | 2.2 | 1.4 | 0 | 25.7 | 26.4 | 26.1 | 1.53 | 1 | 1.1 | 26.1 | 26.1 | 25.8 | 1.52 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:00:00 | 2814.88 | 1541.26 | 828317.48 | 803175.54 | 32.79 | 2479.734 | 1948.362 | -311.266 | 45 | 185 | 26.4 | 62.7 | 26.5 | 62.6 | 0 | 0 | - | - | 28.6 | 57.6 | 0 | 0 | 0 | 0 | 26.1 | 26.9 | 26.3 | 1.5 | 2.2 | 1.4 | 0 | 25.7 | 26.4 | 26.1 | 1.53 | 1.2 | 1 | 26.1 | 26.1 | 25.8 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:05:00 | 2814.88 | 1566.48 | 828317.48 | 803200.08 | 32.86 | 2509.254 | 1918.842 | -322.742 | 45 | 185 | 26.4 | 62.8 | 26.5 | 62.6 | 0 | 0 | - | - | 28.6 | 57.8 | 0 | 0 | 0 | 0 | 26.1 | 26.9 | 26.3 | 1.5 | 2.2 | 1.4 | 0 | 25.8 | 26.4 | 26.1 | 1.54 | 1.2 | 1 | 26.1 | 26 | 25.7 | 1.52 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:10:00 | 2814.88 | 1591.94 | 828317.48 | 803226.2 | 32.93 | 2531.395 | 1896.702 | -321.846 | 44 | 185 | 26.3 | 62.7 | 26.5 | 62.7 | 0 | 0 | - | - | 28.5 | 57.9 | 0 | 0 | 0 | 0 | 26.1 | 26.9 | 26.3 | 1.5 | 2.2 | 1.4 | 0 | 25.8 | 26.5 | 26.1 | 1.54 | 1.2 | 1 | 26.1 | 26 | 25.7 | 1.52 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:15:00 | 2814.88 | 1630.3 | 828317.48 | 803264.96 | 33.01 | 2575.68 | 1852.422 | -734.596 | 43 | 185 | 26.3 | 62.8 | 26.5 | 62.7 | 0 | 0 | - | - | 28.5 | 57.9 | 0 | 0 | 0 | 0 | 26.1 | 26.9 | 26.3 | 1.5 | 2.2 | 1.4 | 0 | 25.8 | 26.5 | 26.1 | 1.54 | 1.2 | 1 | 26 | 26 | 25.7 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:20:00 | 2814.88 | 1688.52 | 828317.48 | 803322.38 | 33.08 | 2634.72 | 1793.379 | -469.342 | 42 | 185 | 26.4 | 62.8 | 26.5 | 62.7 | 0 | 0 | - | - | 28.5 | 58 | 0 | 0 | 0 | 0 | 26.1 | 26.9 | 26.3 | 1.5 | 2.2 | 1.4 | 0 | 25.8 | 26.5 | 26.1 | 1.54 | 1.2 | 0.9 | 25.9 | 25.9 | 25.8 | 1.53 | 1.53 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:25:00 | 2814.88 | 1734.44 | 828317.48 | 803368.92 | 33.16 | 2679 | 1749.096 | -603.168 | 41 | 185 | 26.4 | 62.8 | 26.6 | 62.6 | 0 | 0 | - | - | 28.5 | 58 | 0 | 0 | 0 | 0 | 26.1 | 26.9 | 26.3 | 1.5 | 2.2 | 1.4 | 0 | 25.8 | 26.5 | 26.1 | 1.54 | 1.3 | 1 | 25.9 | 25.9 | 25.8 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:30:00 | 2814.88 | 1794.56 | 828317.48 | 803429.8 | 33.25 | 2752.8 | 1675.296 | -789.719 | 39 | 185 | 26.4 | 62.7 | 26.6 | 62.5 | 0 | 0 | - | - | 28.5 | 58 | 0 | 0 | 0 | 0 | 26.1 | 26.9 | 26.3 | 1.5 | 2.2 | 1.5 | 0 | 25.8 | 26.6 | 26.2 | 1.54 | 1.3 | 1 | 25.9 | 25.8 | 25.7 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:35:00 | 2814.88 | 1871.04 | 828317.48 | 803505.1 | 33.33 | 2833.986 | 1594.116 | -766.838 | 37 | 185 | 26.4 | 62.7 | 26.6 | 62.6 | 0 | 0 | - | - | 28.5 | 58 | 0 | 0 | 0 | 0 | 26.1 | 26.9 | 26.3 | 1.5 | 2.3 | 1.4 | 0 | 25.8 | 26.6 | 26.2 | 1.54 | 1.4 | 1 | 25.8 | 25.8 | 25.9 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:40:00 | 2814.88 | 1929.16 | 828317.48 | 803563.84 | 33.42 | 2885.646 | 1542.455 | -714.524 | 36 | 185 | 26.4 | 62.8 | 26.4 | 62.8 | 0 | 0 | - | - | 28.5 | 58.1 | 0 | 0 | 0 | 0 | 26.1 | 27 | 26.4 | 1.5 | 2.3 | 1.5 | 0 | 25.8 | 26.6 | 26.2 | 1.54 | 1.4 | 1 | 25.8 | 25.8 | 25.8 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:45:00 | 2814.88 | 1997.14 | 828317.48 | 803631.7 | 33.51 | 2966.826 | 1461.27 | -874.51 | 34 | 185 | 26.4 | 62.7 | 26.5 | 62.7 | 0 | 0 | - | - | 28.5 | 58.1 | 0 | 0 | 0 | 0 | 26.1 | 26.9 | 26.4 | 1.5 | 2.3 | 1.4 | 0 | 25.8 | 26.6 | 26.2 | 1.54 | 1.4 | 1 | 25.8 | 25.8 | 25.9 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:50:00 | 2814.88 | 2078.52 | 828317.48 | 803713.08 | 33.6 | 3048.006 | 1380.09 | -901.83 | 32 | 185 | 26.5 | 62.5 | 26.7 | 62.3 | 0 | 0 | - | - | 28.5 | 58.1 | 0 | 0 | 0 | 0 | 26.2 | 27 | 26.5 | 1.5 | 2.4 | 1.5 | 0 | 25.8 | 26.6 | 26.2 | 1.54 | 1.4 | 1 | 25.8 | 25.8 | 25.8 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 18:55:00 | 2814.88 | 2154.14 | 828317.48 | 803788.78 | 33.69 | 3136.572 | 1291.53 | -969.786 | 31 | 185 | 26.3 | 62.9 | 27 | 61.8 | 0 | 0 | - | - | 28.5 | 58.1 | 0 | 0 | 0 | 0 | 26.2 | 27 | 26.5 | 1.5 | 2.3 | 1.5 | 0 | 25.8 | 26.7 | 26.2 | 1.54 | 1.4 | 1 | 25.8 | 25.8 | 25.8 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:00:00 | 2814.88 | 2213.94 | 828317.48 | 803848.78 | 33.78 | 3180.852 | 1247.245 | -632.473 | 29 | 185 | 26.2 | 63.2 | 27.1 | 61.6 | 0 | 0 | - | - | 28.6 | 58.2 | 0 | 0 | 0 | 0 | 26.2 | 27.1 | 26.5 | 1.5 | 2.4 | 1.6 | 0 | 25.8 | 26.7 | 26.3 | 1.54 | 1.4 | 1 | 25.9 | 25.9 | 25.8 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:05:00 | 2814.88 | 2265.26 | 828317.48 | 803899.72 | 33.87 | 3232.512 | 1195.584 | -578.265 | 28 | 185 | 26.3 | 63 | 27.1 | 61.6 | 0 | 0 | - | - | 28.5 | 58.2 | 0 | 0 | 0 | 0 | 26.2 | 27.1 | 26.5 | 1.5 | 2.3 | 1.5 | 0 | 25.9 | 26.7 | 26.2 | 1.54 | 1.4 | 1 | 26 | 26 | 25.8 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:10:00 | 2814.88 | 2310.04 | 828317.48 | 803944.4 | 33.95 | 3276.792 | 1151.304 | -556.952 | 27 | 185 | 26.4 | 62.9 | 27.1 | 61.7 | 0 | 0 | - | - | 28.5 | 58.2 | 0 | 0 | 0 | 0 | 26.2 | 27.1 | 26.5 | 1.5 | 2.3 | 1.5 | 0 | 25.8 | 26.7 | 26.3 | 1.54 | 1.4 | 1 | 26.1 | 26.1 | 25.9 | 1.53 | 1.53 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:15:00 | 2814.88 | 2355.74 | 828317.48 | 803990.54 | 34.04 | 3343.215 | 1084.884 | -627.731 | 26 | 185 | 26.5 | 62.8 | 27 | 61.7 | 0 | 0 | - | - | 28.6 | 58.2 | 0 | 0 | 0 | 0 | 26.3 | 27.1 | 26.6 | 1.5 | 2.3 | 1.6 | 0 | 25.9 | 26.7 | 26.3 | 1.54 | 1.4 | 1 | 26.2 | 26.2 | 25.8 | 1.53 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:20:00 | 2814.88 | 2406.12 | 828317.48 | 804040.76 | 34.13 | 3394.878 | 1033.22 | -523.336 | 25 | 185 | 26.5 | 62.7 | 27 | 61.7 | 0 | 0 | - | - | 28.6 | 58.3 | 0 | 0 | 0 | 0 | 26.2 | 27.2 | 26.6 | 1.5 | 2.2 | 1.4 | 0 | 25.9 | 26.7 | 26.3 | 1.55 | 1.3 | 1 | 26.3 | 26.3 | 25.7 | 1.53 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:25:00 | 2814.88 | 2453.28 | 828317.48 | 804087.16 | 34.21 | 3446.538 | 981.558 | -580.216 | 24 | 185 | 26.6 | 62.7 | 27.1 | 61.8 | 0 | 0 | - | - | 28.5 | 58.3 | 0 | 0 | 0 | 0 | 26.2 | 27.2 | 26.5 | 1.5 | 2.1 | 1.5 | 0 | 25.9 | 26.7 | 26.3 | 1.54 | 1.4 | 1 | 26.4 | 26.4 | 25.7 | 1.53 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:30:00 | 2814.88 | 2500.92 | 828317.48 | 804135.94 | 34.29 | 3498.198 | 929.898 | -558.16 | 22 | 185 | 26.6 | 62.8 | 27.1 | 61.8 | 0 | 0 | - | - | 28.5 | 58.3 | 0 | 0 | 0 | 0 | 26.2 | 27.2 | 26.4 | 1.5 | 1.9 | 1.5 | 0 | 25.9 | 26.7 | 26.3 | 1.55 | 1.3 | 0.9 | 26.6 | 26.6 | 25.7 | 1.53 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:35:00 | 2814.88 | 2532.76 | 828317.48 | 804166.76 | 34.37 | 3527.718 | 900.378 | -197.989 | 22 | 185 | 26.6 | 62.8 | 27.1 | 61.8 | 0 | 0 | - | - | 28.5 | 58.4 | 0 | 0 | 0 | 0 | 26.2 | 27.2 | 26.4 | 1.5 | 1.9 | 1.5 | 0 | 25.9 | 26.7 | 26.2 | 1.55 | 1.3 | 0.9 | 26.7 | 26.7 | 25.7 | 1.53 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:40:00 | 2814.88 | 2550.34 | 828317.48 | 804184.42 | 34.43 | 3549.858 | 878.238 | -188.413 | 21 | 185 | 26.5 | 62.9 | 27.2 | 61.6 | 0 | 0 | - | - | 28.5 | 58.4 | 0 | 0 | 0 | 0 | 26.2 | 27.2 | 26.4 | 1.5 | 1.8 | 1.4 | 0 | 25.9 | 26.7 | 26.3 | 1.55 | 1.2 | 0.9 | 26.8 | 26.8 | 25.7 | 1.53 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:45:00 | 2814.88 | 2565.04 | 828317.48 | 804198.94 | 34.5 | 3557.238 | 870.858 | -236.056 | 21 | 185 | 26.5 | 63 | 27.3 | 61.6 | 0 | 0 | - | - | 28.5 | 58.4 | 0 | 0 | 0 | 0 | 26.2 | 27.2 | 26.4 | 1.51 | 1.8 | 1.5 | 0 | 26 | 26.7 | 26.3 | 1.55 | 1.2 | 0.9 | 26.9 | 26.9 | 25.8 | 1.53 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:50:00 | 2814.88 | 2584.3 | 828317.48 | 804218.1 | 34.56 | 3586.759 | 841.338 | -151.324 | 20 | 185 | 26.4 | 63.1 | 27.3 | 61.7 | 0 | 0 | - | - | 28.5 | 58.5 | 0 | 0 | 0 | 0 | 26.3 | 27.3 | 26.5 | 1.51 | 1.7 | 1.4 | 0 | 26 | 26.8 | 26.3 | 1.55 | 1.2 | 0.8 | 27 | 27 | 25.8 | 1.53 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 19:55:00 | 2814.88 | 2606.64 | 828317.48 | 804240.88 | 34.63 | 3601.52 | 826.578 | -210.757 | 20 | 185 | 26.5 | 63.2 | 27.2 | 62 | 0 | 0 | - | - | 28.5 | 58.7 | 0 | 0 | 0 | 0 | 26.3 | 27.3 | 26.5 | 1.51 | 1.7 | 1.4 | 0 | 26.1 | 26.8 | 26.3 | 1.56 | 1.1 | 0.9 | 27 | 27 | 25.7 | 1.53 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:00:00 | 2814.88 | 2639.4 | 828317.48 | 804273.52 | 34.76 | 3638.424 | 789.677 | -332.84 | 19 | 185 | 26.6 | 63.1 | 27.1 | 62.2 | 0 | 0 | - | - | 28.4 | 58.7 | 0 | 0 | 0 | 0 | 26.2 | 27.3 | 26.4 | 1.5 | 1.7 | 1.4 | 0 | 26.3 | 26.7 | 26.3 | 1.56 | 1 | 1.1 | 25.2 | 27.1 | 25.6 | 2.24 | 0.94 | 2.15 | 0.87 | 194 | 218 | 2400 | 2400
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:05:00 | 2814.88 | 2657.28 | 828317.48 | 804290.96 | 35.35 | 3660.564 | 767.534 | -4.877 | 19 | 185 | 26.5 | 63 | 27.1 | 62.1 | 0 | 0 | - | - | 28.4 | 58.8 | 264 | 243 | 0 | 47.1 | 57.6 | 26.5 | 39.4 | 2.34 | 13.5 | 15.6 | 46.5 | 59 | 26.4 | 38.5 | 2.42 | 11.9 | 16.4 | 22.7 | 24.7 | 27.2 | 2.54 | 1.17 | 2.66 | 1.17 | 261 | 242 | 2400 | 2400
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:10:00 | 2815.4 | 2660.64 | 828318 | 804294.3 | 36.01 | 3667.944 | 760.153 | -51.837 | 19 | 185 | 26.4 | 63 | 27 | 62 | 0 | 0 | - | - | 28.4 | 58.9 | 260 | 240 | 0 | 55.7 | 62.7 | 23.9 | 42.7 | 2.46 | 8.4 | 18.7 | 55.9 | 68.3 | 23.8 | 44.7 | 2.67 | 8.4 | 21.9 | 21.6 | 23.3 | 27.3 | 2.33 | 1.13 | 2.55 | 1.15 | 249 | 212 | 2400 | 2400
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:15:00 | 2815.4 | 2668.08 | 828318 | 804302 | 36.66 | 3675.324 | 752.773 | -181.606 | 18 | 185 | 26.4 | 62.9 | 26.9 | 62.1 | 0 | 0 | - | - | 28.4 | 59 | 249 | 206 | 50.9 | 50.9 | 59.6 | 22.8 | 39.1 | 2.23 | 8.8 | 19.5 | 50.8 | 66.7 | 22.8 | 42.6 | 2.52 | 8.3 | 22.7 | 20.8 | 22.7 | 27.2 | 2.31 | 1.11 | 2.53 | 1.11 | 249 | 205 | 2400 | 2400
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:20:00 | 2815.4 | 2674.8 | 828318 | 804308.42 | 37.31 | 3682.704 | 745.392 | -7.22 | 18 | 185 | 26.3 | 62.8 | 26.7 | 62.1 | 0 | 0 | - | - | 28.3 | 59.1 | 249 | 204 | 50.9 | 50.9 | 59.1 | 22.2 | 38.9 | 2.23 | 8.5 | 18.9 | 50.8 | 66.9 | 22.3 | 42.4 | 2.5 | 8.5 | 23.1 | 20.4 | 22.2 | 27.4 | 2.3 | 1.09 | 2.53 | 1.1 | 249 | 204 | 2400 | 2400
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:25:00 | 2815.44 | 2678.04 | 828318.04 | 804311.78 | 37.96 | 3682.704 | 745.392 | -54.468 | 18 | 185 | 26.3 | 62.7 | 26.6 | 62 | 0 | 0 | - | - | 28.3 | 59.1 | 248 | 204 | 50.9 | 51 | 59.1 | 21.8 | 38.9 | 2.23 | 8.5 | 19 | 51.3 | 67.2 | 22.1 | 42.4 | 2.51 | 8.5 | 23.4 | 20.2 | 21.9 | 27.6 | 2.3 | 1.08 | 2.53 | 1.09 | 248 | 203 | 2400 | 2400
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:30:00 | 2815.5 | 2682.12 | 828318.1 | 804315.82 | 38.6 | 3690.084 | 738.012 | -38.506 | 18 | 185 | 26.2 | 62.5 | 26.5 | 62 | 0 | 0 | - | - | 28.3 | 59.2 | 247 | 203 | 51.4 | 51.5 | 59.1 | 21.6 | 38.9 | 2.23 | 8.6 | 19 | 51.3 | 67.4 | 21.7 | 42.4 | 2.5 | 8.5 | 23.7 | 19.9 | 21.7 | 27.7 | 2.3 | 1.08 | 2.52 | 1.08 | 247 | 202 | 2400 | 2400
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:35:00 | 2815.5 | 2685.54 | 828318.1 | 804319.28 | 39.24 | 3697.464 | 730.632 | -105.706 | 18 | 185 | 26.1 | 62.3 | 26.4 | 61.8 | 0 | 0 | - | - | 28.3 | 59.2 | 246 | 202 | 51.4 | 51.5 | 59.3 | 21.3 | 39 | 2.23 | 8.4 | 19.2 | 51.3 | 67.5 | 21.5 | 42.3 | 2.5 | 8.6 | 23.8 | 19.7 | 21.4 | 27.8 | 2.31 | 1.07 | 2.53 | 1.07 | 245 | 202 | 2400 | 2400
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:40:00 | 2815.5 | 2692.68 | 828318.1 | 804326.42 | 39.89 | 3697.464 | 730.632 | -68.293 | 18 | 185 | 26.1 | 62.1 | 26.3 | 61.8 | 0 | 0 | - | - | 28.3 | 59.1 | 245 | 202 | 52.2 | 52 | 59.6 | 21.1 | 39.1 | 2.23 | 8.5 | 19.4 | 51.9 | 67.7 | 21.2 | 42.4 | 2.5 | 8.6 | 23.9 | 19.4 | 21.2 | 27.9 | 2.3 | 1.06 | 2.52 | 1.06 | 245 | 202 | 2400 | 2400
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:45:00 | 2815.52 | 2698.56 | 828318.12 | 804332.22 | 40.53 | 3712.224 | 715.872 | -45.106 | 18 | 185 | 26 | 61.9 | 26.2 | 61.6 | 0 | 0 | - | - | 28.3 | 59.1 | 244 | 201 | 51.3 | 51.5 | 59.4 | 20.9 | 38.9 | 2.23 | 8.4 | 19.5 | 51.4 | 67.6 | 21.1 | 42.2 | 2.49 | 8.6 | 24 | 19.2 | 21.1 | 27.9 | 2.29 | 1.05 | 2.51 | 1.05 | 244 | 201 | 2400 | 2400
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:50:00 | 2815.52 | 2705.72 | 828318.12 | 804339.44 | 41.17 | 3712.224 | 715.872 | -99.952 | 18 | 185 | 26 | 61.7 | 26.1 | 61.6 | 0 | 0 | - | - | 28.3 | 59 | 244 | 201 | 51.8 | 51.5 | 59.7 | 20.7 | 38.6 | 2.21 | 8.9 | 20 | 51.9 | 67.6 | 20.8 | 42.1 | 2.49 | 8.6 | 24.1 | 19.2 | 20.8 | 28 | 2.25 | 1.02 | 2.42 | 1.11 | 244 | 199 | 2400 | 1500
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 20:55:00 | 2815.52 | 2719.06 | 828318.12 | 804352.92 | 41.55 | 3726.984 | 701.112 | -195.439 | 17 | 185 | 25.9 | 61.8 | 26.1 | 61.6 | 0 | 0 | - | - | 28.3 | 59 | 244 | 0 | 47.8 | 48.3 | 60.8 | 20.6 | 38.4 | 2.22 | 8.8 | 20.9 | 47.7 | 62.9 | 21.2 | 34.1 | 1.79 | 13.6 | 32.9 | 20.6 | 21.7 | 27.7 | 2.38 | 1.08 | 1.66 | 1.4 | 244 | 0 | 2400 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:00:00 | 2815.52 | 2731.94 | 828318.12 | 804365.72 | 41.91 | 3741.744 | 686.352 | -114.431 | 17 | 185 | 25.9 | 61.8 | 26 | 61.6 | 0 | 0 | - | - | 28.3 | 59 | 244 | 0 | 45.3 | 45.4 | 62.2 | 21.8 | 40.1 | 2.31 | 8.6 | 20.7 | 45.3 | 32.8 | 39.7 | 30.2 | 1.64 | 17.7 | 5.6 | 21.1 | 22.2 | 27.7 | 2.4 | 1.09 | 1.49 | 1.43 | 244 | 0 | 2400 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:05:00 | 2815.52 | 2740.82 | 828318.12 | 804374.54 | 42.27 | 3756.504 | 671.592 | -93.001 | 17 | 185 | 25.8 | 61.9 | 26 | 61.6 | 0 | 0 | - | - | 28.3 | 59 | 244 | 0 | 45.8 | 46 | 62.5 | 22 | 40.5 | 2.33 | 8.6 | 20.7 | 45.9 | 32 | 43.3 | 27.9 | 1.44 | 21 | 9.4 | 21.1 | 22.2 | 27.8 | 2.4 | 1.09 | 1.43 | 1.43 | 242 | 0 | 2400 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:10:00 | 2815.52 | 2745.96 | 828318.12 | 804379.66 | 42.63 | 3756.504 | 671.592 | -83.285 | 17 | 185 | 25.8 | 61.9 | 26 | 61.6 | 0 | 0 | - | - | 28.2 | 58.9 | 242 | 0 | 45.8 | 46 | 62.4 | 22 | 40.6 | 2.32 | 8.5 | 20.7 | 45.5 | 31.7 | 41.9 | 27.7 | 1.44 | 19.5 | 9.2 | 21.1 | 22.2 | 28 | 2.4 | 1.09 | 1.43 | 1.43 | 242 | 0 | 2400 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:15:00 | 2815.56 | 2748.52 | 828318.16 | 804382.22 | 42.99 | 3756.504 | 671.592 | -8.066 | 17 | 185 | 25.8 | 61.9 | 25.9 | 61.7 | 0 | 0 | - | - | 28.2 | 58.9 | 242 | 0 | 45.8 | 46 | 62.6 | 22 | 40.5 | 2.33 | 8.6 | 20.8 | 45.9 | 31.6 | 40.7 | 27.4 | 1.43 | 18.4 | 9.2 | 21.1 | 22.2 | 28.4 | 2.4 | 1.09 | 1.43 | 1.43 | 242 | 0 | 2400 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:20:00 | 2815.56 | 2753.88 | 828318.16 | 804387.62 | 43.35 | 3756.504 | 671.592 | -51.606 | 16 | 185 | 25.8 | 61.8 | 25.8 | 61.7 | 0 | 0 | - | - | 28.2 | 58.9 | 242 | 0 | 45.8 | 46 | 62.6 | 21.9 | 40.5 | 2.33 | 8.7 | 20.8 | 45.9 | 31.4 | 39.9 | 27.2 | 1.43 | 17.5 | 9.1 | 21.1 | 22.2 | 28.7 | 2.39 | 1.08 | 1.42 | 1.43 | 242 | 0 | 2400 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:25:00 | 2815.56 | 2758.78 | 828318.16 | 804392.5 | 43.71 | 3756.504 | 671.592 | -41.297 | 16 | 185 | 25.7 | 61.8 | 25.8 | 61.7 | 0 | 0 | - | - | 28.2 | 58.8 | 242 | 0 | 45.9 | 46 | 62.6 | 21.8 | 40.5 | 2.33 | 8.6 | 20.9 | 46 | 31.4 | 39.2 | 27.2 | 1.43 | 17 | 9.2 | 20.9 | 22 | 28.4 | 2.39 | 1.08 | 1.41 | 1.42 | 242 | 0 | 2400 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:30:00 | 2815.56 | 2762.16 | 828318.16 | 804395.84 | 44.05 | 3771.264 | 656.832 | -24.737 | 16 | 185 | 25.6 | 61.8 | 25.7 | 61.8 | 0 | 0 | - | - | 28.3 | 58.8 | 242 | 0 | 45.4 | 45.5 | 62.6 | 21.7 | 40.4 | 2.32 | 8.7 | 20.9 | 45.5 | 31.2 | 38.1 | 27.3 | 1.42 | 15.9 | 9.3 | 21 | 21.9 | 28.6 | 2.09 | 0.46 | 1.4 | 1.41 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:35:00 | 2820.3 | 2763 | 828322.96 | 804396.6 | 44.13 | 3756.504 | 671.592 | 64.592 | 16 | 185 | 25.6 | 61.9 | 25.7 | 61.9 | 0 | 0 | - | - | 28.3 | 58.7 | 0 | 0 | 0 | 0 | 57.2 | 21.5 | 32.4 | 1.72 | 15.6 | 27.8 | 0 | 30.7 | 35.4 | 27.5 | 1.41 | 13.2 | 8.8 | 22.9 | 22.9 | 28.6 | 1.59 | 1.43 | 1.41 | 1.44 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:40:00 | 2821.54 | 2765.18 | 828324.14 | 804398.82 | 44.21 | 3763.884 | 664.212 | 9.149 | 16 | 185 | 25.6 | 62 | 25.7 | 62 | 0 | 0 | - | - | 28.2 | 58.6 | 0 | 0 | 0 | 0 | 36.6 | 30.7 | 30.2 | 1.52 | 7.9 | 11.6 | 0 | 30.1 | 32.4 | 27.6 | 1.42 | 9.6 | 8 | 23.5 | 23.4 | 28.2 | 1.49 | 1.47 | 1.43 | 1.46 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:45:00 | 2824.7 | 2765.7 | 828327.48 | 804399.3 | 44.29 | 3756.504 | 671.592 | 103.272 | 16 | 185 | 25.5 | 62.1 | 25.7 | 62 | 0 | 0 | - | - | 28.3 | 58.6 | 0 | 0 | 0 | 0 | 30.7 | 34.3 | 29.4 | 1.47 | 10.8 | 6.9 | 0 | 29.7 | 30.7 | 27.6 | 1.43 | 7.5 | 7.3 | 23.8 | 23.7 | 28.1 | 1.49 | 1.48 | 1.43 | 1.47 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:50:00 | 2832.86 | 2765.7 | 828335.68 | 804399.3 | 44.36 | 3756.504 | 671.592 | 196.425 | 17 | 185 | 25.5 | 62.1 | 25.7 | 62 | 0 | 0 | - | - | 28.2 | 58.6 | 0 | 0 | 0 | 0 | 29.7 | 33.9 | 29.1 | 1.48 | 10.3 | 5.8 | 0 | 29.2 | 29.7 | 27.4 | 1.44 | 6.4 | 6.6 | 23.9 | 23.8 | 28 | 1.5 | 1.49 | 1.44 | 1.47 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 21:55:00 | 2838.36 | 2765.94 | 828341 | 804399.58 | 44.44 | 3756.504 | 671.592 | -83.012 | 17 | 185 | 25.5 | 62.2 | 25.6 | 62 | 0 | 0 | - | - | 28.2 | 58.6 | 0 | 0 | 0 | 0 | 29.2 | 33.7 | 28.7 | 1.48 | 10 | 5.2 | 0 | 29 | 29.2 | 27.4 | 1.45 | 5.8 | 6.2 | 24 | 23.9 | 27.8 | 1.5 | 1.49 | 1.45 | 1.48 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:00:00 | 2838.42 | 2776.46 | 828341.02 | 804410.18 | 44.51 | 3756.504 | 671.592 | -109.212 | 16 | 185 | 25.5 | 62.3 | 25.7 | 62.1 | 0 | 0 | - | - | 28.2 | 58.7 | 0 | 0 | 0 | 0 | 28.8 | 33.6 | 28.4 | 1.48 | 9.9 | 4.8 | 0 | 28.7 | 28.8 | 27.3 | 1.46 | 5.3 | 5.9 | 24 | 23.9 | 27.7 | 1.5 | 1.49 | 1.45 | 1.48 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:05:00 | 2838.52 | 2782.5 | 828341.12 | 804416.16 | 44.59 | 3763.884 | 664.212 | -95.911 | 16 | 185 | 25.5 | 62.3 | 25.6 | 62.1 | 0 | 0 | - | - | 28.1 | 58.7 | 0 | 0 | 0 | 0 | 28.6 | 33.4 | 28.2 | 1.48 | 9.5 | 4.5 | 0 | 28.5 | 28.4 | 27.3 | 1.46 | 4.9 | 5.6 | 24.1 | 24 | 27.6 | 1.5 | 1.49 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:10:00 | 2841.18 | 2784.86 | 828344.1 | 804418.46 | 44.66 | 3756.504 | 671.592 | 123.438 | 16 | 185 | 25.5 | 62.4 | 25.6 | 62.1 | 0 | 0 | - | - | 28.1 | 58.7 | 0 | 0 | 0 | 0 | 28.4 | 33.4 | 28 | 1.48 | 9.4 | 4.2 | 0 | 28.3 | 28.2 | 27.2 | 1.46 | 4.6 | 5.2 | 24.1 | 24 | 27.3 | 1.51 | 1.5 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:15:00 | 2859.96 | 2784.86 | 828363 | 804418.46 | 44.73 | 3749.124 | 678.972 | 298.657 | 17 | 185 | 25.4 | 62.4 | 25.6 | 62.2 | 0 | 0 | - | - | 28 | 58.8 | 0 | 0 | 0 | 0 | 28.2 | 33.2 | 27.8 | 1.48 | 9.3 | 4 | 0 | 28.2 | 28.1 | 27.2 | 1.47 | 4.3 | 5 | 24.1 | 24.1 | 27.2 | 1.51 | 1.5 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:20:00 | 2885.6 | 2784.86 | 828388.42 | 804418.46 | 44.81 | 3719.604 | 708.492 | 391.409 | 17 | 185 | 25.4 | 62.5 | 25.6 | 62.3 | 0 | 0 | - | - | 28 | 58.9 | 0 | 0 | 0 | 0 | 28.2 | 32.9 | 27.7 | 1.49 | 9 | 3.9 | 0 | 28 | 27.8 | 27.2 | 1.47 | 4.1 | 4.9 | 24.1 | 24.1 | 27.2 | 1.51 | 1.5 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:25:00 | 2920.52 | 2784.86 | 828424.04 | 804418.46 | 44.89 | 3682.704 | 745.392 | 432.762 | 18 | 185 | 25.4 | 62.5 | 25.6 | 62.3 | 0 | 0 | - | - | 28 | 58.9 | 0 | 0 | 0 | 0 | 27.9 | 32.9 | 27.6 | 1.48 | 8.8 | 3.8 | 0 | 27.9 | 27.7 | 27.2 | 1.47 | 4 | 4.7 | 24.1 | 24.1 | 27.2 | 1.5 | 1.5 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:30:00 | 2959.04 | 2784.86 | 828462.18 | 804418.46 | 44.97 | 3645.804 | 782.296 | 501.723 | 19 | 185 | 25.3 | 62.6 | 25.5 | 62.4 | 0 | 0 | - | - | 27.9 | 58.9 | 0 | 0 | 0 | 0 | 27.9 | 32.6 | 27.6 | 1.48 | 8.5 | 3.8 | 0 | 27.7 | 27.7 | 27.2 | 1.47 | 3.9 | 4.5 | 24.1 | 24.1 | 27.1 | 1.5 | 1.5 | 1.46 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:35:00 | 2994.58 | 2784.86 | 828497.28 | 804418.46 | 45.06 | 3608.901 | 819.198 | 157.364 | 20 | 185 | 25.3 | 62.7 | 25.6 | 62.4 | 0 | 0 | - | - | 27.9 | 59 | 0 | 0 | 0 | 0 | 27.7 | 32.2 | 27.4 | 1.48 | 8.2 | 3.6 | 0 | 27.7 | 27.5 | 27.2 | 1.47 | 3.8 | 4.5 | 24.1 | 24.1 | 27.1 | 1.5 | 1.5 | 1.46 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:40:00 | 2996.06 | 2789.96 | 828498.68 | 804423.58 | 45.12 | 3608.901 | 819.198 | -11.592 | 20 | 185 | 25.3 | 62.7 | 25.6 | 62.2 | 0 | 0 | - | - | 27.9 | 59.1 | 0 | 0 | 0 | 0 | 27.7 | 31.9 | 27.4 | 1.48 | 7.8 | 3.5 | 0 | 27.6 | 27.4 | 27.1 | 1.47 | 3.7 | 4.3 | 24.2 | 24.1 | 27.3 | 1.5 | 1.5 | 1.46 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:45:00 | 2996.84 | 2799.24 | 828499.44 | 804433.1 | 45.18 | 3616.282 | 811.818 | -188.264 | 20 | 185 | 25.3 | 62.8 | 25.6 | 62.3 | 0 | 0 | - | - | 27.8 | 59.2 | 0 | 0 | 0 | 0 | 27.7 | 31.6 | 27.4 | 1.48 | 7.5 | 3.6 | 0 | 27.5 | 27.4 | 27.1 | 1.47 | 3.6 | 4.3 | 24.2 | 24.1 | 27.2 | 1.5 | 1.5 | 1.46 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:50:00 | 2996.84 | 2819.48 | 828499.44 | 804453.38 | 45.25 | 3638.424 | 789.677 | -140.799 | 19 | 185 | 25.3 | 62.8 | 25.3 | 62.7 | 0 | 0 | - | - | 27.8 | 59.2 | 0 | 0 | 0 | 0 | 27.7 | 31.3 | 27.3 | 1.48 | 7.2 | 3.5 | 0 | 27.4 | 27.3 | 27.1 | 1.47 | 3.6 | 4.2 | 24.2 | 24.2 | 27.2 | 1.5 | 1.5 | 1.46 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 22:55:00 | 2997.18 | 2826.02 | 828499.78 | 804459.74 | 45.32 | 3645.804 | 782.296 | 4.552 | 19 | 185 | 25.2 | 62.9 | 25.3 | 62.9 | 0 | 0 | - | - | 27.8 | 59.3 | 0 | 0 | 0 | 0 | 27.7 | 31.1 | 27.3 | 1.48 | 6.9 | 3.4 | 0 | 27.3 | 27.3 | 27.1 | 1.47 | 3.5 | 4.1 | 24.2 | 24.2 | 27.2 | 1.51 | 1.5 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:00:00 | 2999.84 | 2829.86 | 828502.46 | 804463.46 | 45.38 | 3653.184 | 774.915 | 36.514 | 19 | 185 | 25.2 | 62.8 | 25.4 | 62.5 | 0 | 0 | - | - | 27.7 | 59.3 | 0 | 0 | 0 | 0 | 27.6 | 30.7 | 27.2 | 1.48 | 6.5 | 3.3 | 0 | 27.2 | 27.2 | 27.1 | 1.47 | 3.4 | 4 | 24.2 | 24.2 | 27.1 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:05:00 | 3000.26 | 2840.94 | 828502.86 | 804475.28 | 45.45 | 3660.564 | 767.534 | -382.325 | 19 | 185 | 25.2 | 62.6 | 25.5 | 62.5 | 0 | 0 | - | - | 27.7 | 59.3 | 0 | 0 | 0 | 0 | 27.4 | 30.3 | 27.2 | 1.48 | 6.2 | 3.2 | 0 | 27.2 | 27.2 | 27.1 | 1.47 | 3.4 | 3.9 | 24.3 | 24.2 | 27 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:10:00 | 3000.26 | 2869.26 | 828502.86 | 804503.26 | 45.53 | 3697.464 | 730.632 | -243.868 | 18 | 185 | 25.1 | 62.3 | 25.5 | 62.3 | 0 | 0 | - | - | 27.7 | 59.4 | 0 | 0 | 0 | 0 | 27.3 | 30.1 | 27.1 | 1.48 | 5.9 | 3.1 | 0 | 27.2 | 27.2 | 27.1 | 1.47 | 3.3 | 3.9 | 24.3 | 24.2 | 26.8 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:15:00 | 3000.26 | 2888.54 | 828502.86 | 804522.18 | 45.6 | 3712.224 | 715.872 | -86.783 | 18 | 185 | 25.1 | 62.2 | 25.5 | 62.1 | 0 | 0 | - | - | 27.7 | 59.4 | 0 | 0 | 0 | 0 | 27.3 | 29.8 | 27 | 1.49 | 5.6 | 3 | 0 | 27.1 | 27.1 | 26.9 | 1.47 | 3.2 | 3.8 | 24.3 | 24.3 | 26.8 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:20:00 | 3002.34 | 2891.62 | 828504.94 | 804525.42 | 45.67 | 3712.224 | 715.872 | -157.268 | 18 | 185 | 25.1 | 62.2 | 25.5 | 62.1 | 0 | 0 | - | - | 27.6 | 59.5 | 0 | 0 | 0 | 0 | 27.2 | 29.6 | 27 | 1.49 | 5.3 | 2.9 | 0 | 27 | 26.9 | 26.9 | 1.47 | 3.1 | 3.7 | 24.4 | 24.3 | 26.7 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:25:00 | 3002.58 | 2899.04 | 828505.18 | 804532.8 | 45.73 | 3712.224 | 715.872 | -133.933 | 17 | 185 | 25.1 | 62.1 | 25.5 | 62 | 0 | 0 | - | - | 27.6 | 59.4 | 0 | 0 | 0 | 0 | 27.2 | 29.3 | 26.9 | 1.49 | 4.9 | 2.7 | 0 | 26.9 | 26.9 | 26.9 | 1.48 | 3 | 3.5 | 24.4 | 24.4 | 26.9 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:30:00 | 3003.88 | 2903.58 | 828506.64 | 804537.18 | 45.8 | 3726.984 | 701.112 | 28.222 | 17 | 185 | 25.1 | 62 | 25.5 | 61.9 | 0 | 0 | - | - | 27.6 | 59.5 | 0 | 0 | 0 | 0 | 27.2 | 29.2 | 26.9 | 1.49 | 4.8 | 2.8 | 0 | 26.9 | 26.9 | 26.9 | 1.48 | 3 | 3.6 | 24.4 | 24.3 | 26.9 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:35:00 | 3004.28 | 2909.38 | 828506.88 | 804543 | 45.86 | 3726.984 | 701.112 | 17.322 | 17 | 185 | 25.1 | 61.9 | 25.5 | 61.8 | 0 | 0 | - | - | 27.5 | 59.6 | 0 | 0 | 0 | 0 | 27.2 | 29.1 | 27 | 1.49 | 4.8 | 2.9 | 0 | 26.9 | 26.9 | 26.9 | 1.48 | 3 | 3.6 | 24.4 | 24.3 | 26.7 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:40:00 | 3011.46 | 2909.5 | 828514.18 | 804543.1 | 45.93 | 3719.604 | 708.492 | 79.962 | 17 | 185 | 25.1 | 61.9 | 25.5 | 61.7 | 0 | 0 | - | - | 27.5 | 59.5 | 0 | 0 | 0 | 0 | 27.2 | 28.9 | 26.9 | 1.49 | 4.6 | 2.9 | 0 | 26.9 | 26.9 | 26.9 | 1.48 | 3 | 3.5 | 24.4 | 24.4 | 26.7 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:45:00 | 3018.26 | 2910.22 | 828520.88 | 804543.82 | 45.99 | 3712.224 | 715.872 | 8.183 | 17 | 185 | 25.1 | 61.8 | 25.5 | 61.7 | 0 | 0 | - | - | 27.5 | 59.6 | 0 | 0 | 0 | 0 | 27.2 | 28.8 | 26.8 | 1.49 | 4.5 | 2.8 | 0 | 26.8 | 26.9 | 26.9 | 1.48 | 3 | 3.5 | 24.4 | 24.4 | 26.6 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:50:00 | 3019.88 | 2911.06 | 828522.48 | 804544.7 | 46.06 | 3712.224 | 715.872 | -44.07 | 17 | 185 | 25.1 | 61.8 | 25.5 | 61.6 | 0 | 0 | - | - | 27.5 | 59.6 | 0 | 0 | 0 | 0 | 27.1 | 28.7 | 26.7 | 1.49 | 4.3 | 2.6 | 0 | 26.7 | 26.8 | 26.8 | 1.48 | 2.9 | 3.4 | 24.4 | 24.4 | 26.6 | 1.51 | 1.51 | 1.47 | 1.5 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-17/B17-ESS03 | 2026-06-02 23:55:00 | 3019.88 | 2932.48 | 828522.48 | 804566.5 | 46.13 | 3734.364 | 693.732 | -297.458 | 17 | 185 | 25.1 | 61.7 | 25.4 | 61.5 | 0 | 0 | - | - | 27.4 | 59.6 | 0 | 0 | 0 | 0 | 27 | 28.6 | 26.8 | 1.49 | 4.2 | 2.7 | 0 | 26.7 | 26.8 | 26.8 | 1.48 | 2.9 | 3.4 | 24.5 | 24.4 | 26.7 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0