## 5 minutes
Time range: | 2026-06-02 00:00:00 - 2026-06-02 23:59:59
Export time: | 2026-06-03 00:38:48
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge energy(kWh) | Total discharge energy(kWh) | Daily auxiliary power consumption(kWh) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge power(kW) | SOC(%) | Equivalent number of cycles | Battery cabin temperature 1(℃) | Battery cabin humidity 1(%) | Battery cabin temperature 2(℃) | Battery cabin humidity 2(%) | CO concentration 1(ppm) | CO concentration 2(ppm) | H2 concentration 1(ppm) | H2 concentration 2(ppm) | Control unit cabin temperature 1(℃) | Control unit cabin humidity 1(%) | Control status of EEV 1(step) | Control status of EEV 2(step) | Running status of outdoor fan 1(%) | Running status of outdoor fan 2(%) | Discharge temperature of compressor 1(℃) | Suction temperature of refrigerant system 1(℃) | Condenser outlet temperature of refrigerant system 1(℃) | Condenser outlet pressure of refrigerant system 1(Mpa) | Suction superheat degree of refrigerant system 1(℃) | Discharge superheat degree of compressor 1(℃) | Running status of outdoor fan 3(%) | Discharge temperature of compressor 2(℃) | Suction temperature of refrigerant system 2(℃) | Condenser outlet temperature of refrigerant system 2(℃) | Condenser outlet pressure of refrigerant system 2(Mpa) | Suction superheat degree of refrigerant system 2(℃) | Discharge superheat degree of compressor 2(℃) | Battery-side supply water temperature(℃) | Battery-side return water temperature(℃) | Air intake temperature(℃) | Discharge pressure of refrigerant system 1(Mpa) | Suction pressure of refrigerant system 1(Mpa) | Discharge pressure of refrigerant system 2(Mpa) | Suction pressure of refrigerant system 2(Mpa) | Running status of EEV 1(step) | Running status of EEV 2(step) | Compressor 1 running status(rpm) | Compressor 2 running status(rpm)
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:00:00 | 0 | 1.98 | 838919.58 | 814126.44 | 0.01 | 3809.36 | 663.466 | -218.302 | 15 | 187 | 25.7 | 56.9 | 25.8 | 57 | 0 | 0 | - | - | 28.7 | 51 | 0 | 0 | 0 | 0 | 27.3 | 28.8 | 27.2 | 1.59 | 2.6 | 1.8 | 0 | 27.1 | 28.3 | 27.3 | 1.54 | 2.4 | 1.5 | 24.4 | 24.4 | 26.4 | 1.56 | 1.59 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:05:00 | 0 | 16.92 | 838919.58 | 814141.46 | 0.11 | 3846.63 | 626.196 | -187.075 | 15 | 187 | 25.8 | 57 | 25.8 | 57 | 0 | 0 | - | - | 28.7 | 51 | 0 | 0 | 0 | 0 | 27.2 | 28.7 | 27.2 | 1.59 | 2.5 | 1.7 | 0 | 27.1 | 28.2 | 27.3 | 1.54 | 2.2 | 1.4 | 24.5 | 24.4 | 26.4 | 1.56 | 1.59 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:10:00 | 0 | 34.18 | 838919.58 | 814158.66 | 0.23 | 3846.63 | 626.196 | -126.132 | 15 | 187 | 25.7 | 57 | 25.8 | 57 | 0 | 0 | - | - | 28.6 | 51.1 | 0 | 0 | 0 | 0 | 27.2 | 28.6 | 27.2 | 1.59 | 2.4 | 1.8 | 0 | 27 | 28.1 | 27.3 | 1.54 | 2.1 | 1.4 | 24.5 | 24.5 | 26.3 | 1.56 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:15:00 | 0.5 | 38.4 | 838920.12 | 814162.64 | 0.33 | 3846.63 | 626.196 | -75.123 | 15 | 187 | 25.7 | 57 | 25.9 | 57 | 0 | 0 | - | - | 28.6 | 51.1 | 0 | 0 | 0 | 0 | 27.2 | 28.6 | 27.2 | 1.59 | 2.3 | 1.7 | 0 | 26.9 | 28.1 | 27.3 | 1.54 | 2.1 | 1.3 | 24.6 | 24.5 | 26.2 | 1.56 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:20:00 | 6.86 | 38.68 | 838926.52 | 814162.92 | 0.44 | 3846.63 | 626.196 | 158.924 | 15 | 187 | 25.7 | 57.1 | 25.9 | 57 | 0 | 0 | - | - | 28.5 | 51.2 | 0 | 0 | 0 | 0 | 27.2 | 28.6 | 27.1 | 1.59 | 2.3 | 1.7 | 0 | 26.9 | 27.9 | 27.3 | 1.54 | 2 | 1.3 | 24.6 | 24.6 | 26.2 | 1.56 | 1.59 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:25:00 | 23.76 | 38.68 | 838943.64 | 814162.92 | 0.55 | 3846.63 | 626.196 | 214.155 | 15 | 187 | 25.7 | 57.2 | 25.8 | 57.1 | 0 | 0 | - | - | 28.5 | 51.2 | 0 | 0 | 0 | 0 | 27.2 | 28.5 | 27.1 | 1.59 | 2.2 | 1.7 | 0 | 26.8 | 27.9 | 27.3 | 1.54 | 2 | 1.2 | 24.6 | 24.6 | 26.2 | 1.56 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:30:00 | 44.94 | 38.68 | 838964.92 | 814162.92 | 0.66 | 3801.906 | 670.92 | 232.081 | 16 | 187 | 25.7 | 57.2 | 25.8 | 57.1 | 0 | 0 | - | - | 28.5 | 51.3 | 0 | 0 | 0 | 0 | 27.2 | 28.5 | 27.1 | 1.59 | 2.2 | 1.6 | 0 | 26.8 | 27.9 | 27.3 | 1.54 | 1.9 | 1.2 | 24.6 | 24.6 | 26.1 | 1.56 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:35:00 | 56.96 | 38.68 | 838976.64 | 814162.92 | 0.76 | 3801.906 | 670.92 | 87.908 | 16 | 187 | 25.7 | 57.3 | 25.8 | 57.2 | 0 | 0 | - | - | 28.4 | 51.3 | 0 | 0 | 0 | 0 | 27.3 | 28.6 | 27.1 | 1.59 | 2.3 | 1.8 | 0 | 26.8 | 27.8 | 27.2 | 1.54 | 1.9 | 1.2 | 24.6 | 24.6 | 26.1 | 1.57 | 1.6 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:40:00 | 61.68 | 38.74 | 838981.34 | 814162.98 | 0.87 | 3801.906 | 670.92 | 63.893 | 16 | 187 | 25.6 | 57.3 | 25.9 | 57.1 | 0 | 0 | - | - | 28.4 | 51.3 | 0 | 0 | 0 | 0 | 27.3 | 28.6 | 27.1 | 1.59 | 2.2 | 1.7 | 0 | 26.8 | 27.8 | 27.2 | 1.55 | 1.8 | 1.1 | 24.6 | 24.6 | 25.9 | 1.57 | 1.6 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:45:00 | 66.2 | 40.16 | 838985.78 | 814164.66 | 0.98 | 3801.906 | 670.92 | -87.077 | 16 | 187 | 25.6 | 57.4 | 25.9 | 57.1 | 0 | 0 | - | - | 28.4 | 51.4 | 0 | 0 | 0 | 0 | 27.2 | 28.6 | 26.9 | 1.59 | 2.1 | 1.6 | 0 | 26.7 | 27.7 | 27.1 | 1.55 | 1.7 | 1 | 24.6 | 24.6 | 26 | 1.57 | 1.6 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:50:00 | 67.64 | 42.42 | 838987.26 | 814166.68 | 1.1 | 3801.906 | 670.92 | -28.754 | 16 | 187 | 25.6 | 57.4 | 25.9 | 57.1 | 0 | 0 | - | - | 28.3 | 51.5 | 0 | 0 | 0 | 0 | 27.1 | 28.4 | 26.8 | 1.59 | 2 | 1.5 | 0 | 26.7 | 27.7 | 27.1 | 1.54 | 1.6 | 1 | 24.6 | 24.6 | 26.2 | 1.57 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 00:55:00 | 67.68 | 47.04 | 838987.26 | 814171.32 | 1.21 | 3801.906 | 670.92 | -30.894 | 16 | 187 | 25.6 | 57.4 | 25.8 | 57.2 | 0 | 0 | - | - | 28.3 | 51.5 | 0 | 0 | 0 | 0 | 27.1 | 28.3 | 26.9 | 1.59 | 1.9 | 1.4 | 0 | 26.7 | 27.7 | 27.1 | 1.55 | 1.6 | 1 | 24.7 | 24.7 | 26.3 | 1.57 | 1.6 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:00:00 | 68.02 | 51 | 838987.6 | 814175.24 | 1.33 | 3801.906 | 670.92 | -10.159 | 16 | 187 | 25.6 | 57.4 | 25.9 | 57.1 | 0 | 0 | - | - | 28.3 | 51.6 | 0 | 0 | 0 | 0 | 27.1 | 28.3 | 27 | 1.6 | 1.9 | 1.4 | 0 | 26.7 | 27.6 | 27.1 | 1.55 | 1.6 | 1 | 24.7 | 24.7 | 26.3 | 1.57 | 1.6 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:05:00 | 71.1 | 51.66 | 838990.68 | 814175.94 | 1.44 | 3801.906 | 670.92 | -25.638 | 16 | 187 | 25.6 | 57.4 | 25.9 | 57.2 | 0 | 0 | - | - | 28.2 | 51.7 | 0 | 0 | 0 | 0 | 27.1 | 28.2 | 27 | 1.6 | 1.8 | 1.4 | 0 | 26.8 | 27.6 | 27.1 | 1.55 | 1.6 | 1.1 | 24.7 | 24.7 | 26.4 | 1.57 | 1.6 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:10:00 | 71.56 | 56.06 | 838991.14 | 814180.36 | 1.56 | 3801.906 | 670.92 | -59.383 | 16 | 187 | 25.6 | 57.4 | 25.9 | 57.1 | 0 | 0 | - | - | 28.2 | 51.7 | 0 | 0 | 0 | 0 | 27.1 | 28.2 | 27.1 | 1.6 | 1.8 | 1.3 | 0 | 26.8 | 27.6 | 27.2 | 1.55 | 1.5 | 1 | 24.7 | 24.7 | 26.4 | 1.57 | 1.6 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:15:00 | 71.78 | 64.9 | 838991.36 | 814189.24 | 1.67 | 3801.906 | 670.92 | -55.647 | 16 | 187 | 25.6 | 57.4 | 25.9 | 57.1 | 0 | 0 | - | - | 28.2 | 51.7 | 0 | 0 | 0 | 0 | 27 | 28.2 | 27.1 | 1.6 | 1.7 | 1.3 | 0 | 26.8 | 27.6 | 27.2 | 1.55 | 1.5 | 1 | 24.7 | 24.7 | 26.5 | 1.57 | 1.6 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:20:00 | 73.58 | 65.68 | 838993.2 | 814189.92 | 1.78 | 3801.906 | 670.92 | 33.23 | 16 | 187 | 25.7 | 57.4 | 25.9 | 57.1 | 0 | 0 | - | - | 28.2 | 51.8 | 0 | 0 | 0 | 0 | 27 | 28.2 | 27.1 | 1.6 | 1.8 | 1.3 | 0 | 26.8 | 27.6 | 27.2 | 1.55 | 1.5 | 1 | 24.8 | 24.7 | 26.4 | 1.57 | 1.6 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:25:00 | 75.08 | 68.9 | 838994.66 | 814193.14 | 1.89 | 3801.906 | 670.92 | 7.698 | 16 | 187 | 25.7 | 57.4 | 25.9 | 57.1 | 0 | 0 | - | - | 28.2 | 51.8 | 0 | 0 | 0 | 0 | 26.9 | 28.2 | 27.1 | 1.6 | 1.7 | 1.3 | 0 | 26.8 | 27.6 | 27.2 | 1.55 | 1.4 | 1 | 24.8 | 24.8 | 26.4 | 1.57 | 1.6 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:30:00 | 75.28 | 72.3 | 838994.86 | 814196.64 | 2.01 | 3801.906 | 670.92 | -86.448 | 16 | 187 | 25.7 | 57.4 | 25.9 | 57.1 | 0 | 0 | - | - | 28.2 | 51.8 | 0 | 0 | 0 | 0 | 26.9 | 28.2 | 27.1 | 1.6 | 1.7 | 1.3 | 0 | 26.7 | 27.6 | 27.2 | 1.55 | 1.4 | 0.9 | 24.8 | 24.8 | 26.3 | 1.57 | 1.6 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:35:00 | 75.28 | 77.22 | 838994.86 | 814201.6 | 2.13 | 3809.36 | 663.466 | -16.059 | 15 | 187 | 25.7 | 57.4 | 25.9 | 57.1 | 0 | 0 | - | - | 28.2 | 51.9 | 0 | 0 | 0 | 0 | 26.9 | 28.2 | 27 | 1.6 | 1.6 | 1.2 | 0 | 26.7 | 27.6 | 27.1 | 1.55 | 1.4 | 0.9 | 24.8 | 24.8 | 26.4 | 1.57 | 1.61 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:40:00 | 75.28 | 80.86 | 838994.86 | 814205.12 | 2.24 | 3824.268 | 648.558 | -23.428 | 15 | 187 | 25.7 | 57.4 | 26 | 57.1 | 0 | 0 | - | - | 28.1 | 51.9 | 0 | 0 | 0 | 0 | 27 | 28.2 | 27 | 1.6 | 1.6 | 1.3 | 0 | 26.8 | 27.6 | 27.1 | 1.55 | 1.3 | 0.9 | 24.8 | 24.8 | 26.3 | 1.57 | 1.61 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:45:00 | 75.7 | 83.72 | 838995.28 | 814208.02 | 2.36 | 3831.722 | 641.104 | 1.368 | 15 | 187 | 25.7 | 57.4 | 26 | 57.1 | 0 | 0 | - | - | 28.1 | 52 | 0 | 0 | 0 | 0 | 27.1 | 28.1 | 27 | 1.6 | 1.6 | 1.4 | 0 | 26.8 | 27.5 | 27.1 | 1.55 | 1.4 | 1 | 24.8 | 24.8 | 26.3 | 1.57 | 1.61 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:50:00 | 76.26 | 87.26 | 838995.84 | 814211.6 | 2.46 | 3846.63 | 626.196 | -55.67 | 15 | 187 | 25.7 | 57.4 | 26 | 57.1 | 0 | 0 | - | - | 28.1 | 52 | 0 | 0 | 0 | 0 | 27.1 | 28.1 | 26.9 | 1.6 | 1.5 | 1.3 | 0 | 26.8 | 27.4 | 26.9 | 1.55 | 1.3 | 0.9 | 24.8 | 24.8 | 26.3 | 1.57 | 1.61 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 01:55:00 | 79.56 | 89.68 | 838999.48 | 814213.92 | 2.58 | 3839.176 | 633.65 | 251.901 | 15 | 187 | 25.7 | 57.4 | 26 | 57.1 | 0 | 0 | - | - | 28.1 | 52 | 0 | 0 | 0 | 0 | 27.1 | 28.1 | 26.9 | 1.6 | 1.5 | 1.3 | 0 | 26.7 | 27.4 | 26.9 | 1.55 | 1.2 | 0.9 | 24.9 | 24.8 | 26.3 | 1.58 | 1.61 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:00:00 | 87.48 | 93.24 | 839007.06 | 814217.52 | 2.7 | 3824.268 | 648.558 | -96.138 | 15 | 187 | 25.8 | 57.4 | 26 | 57.1 | 0 | 0 | - | - | 28.1 | 52.1 | 0 | 0 | 0 | 0 | 27.1 | 28 | 26.9 | 1.6 | 1.5 | 1.2 | 0 | 26.8 | 27.4 | 26.9 | 1.55 | 1.2 | 0.9 | 24.9 | 24.8 | 26.3 | 1.57 | 1.61 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:05:00 | 87.48 | 98.62 | 839007.06 | 814222.92 | 2.81 | 3846.63 | 626.196 | -17.788 | 15 | 187 | 25.8 | 57.4 | 26 | 57.1 | 0 | 0 | - | - | 28.1 | 52.1 | 0 | 0 | 0 | 0 | 27.1 | 28 | 26.9 | 1.6 | 1.5 | 1.3 | 0 | 26.8 | 27.4 | 26.9 | 1.55 | 1.2 | 0.9 | 24.9 | 24.8 | 26.3 | 1.58 | 1.61 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:10:00 | 87.82 | 101 | 839007.4 | 814225.32 | 2.92 | 3846.63 | 626.196 | -32.471 | 15 | 187 | 25.8 | 57.4 | 26 | 57.1 | 0 | 0 | - | - | 28 | 52.2 | 0 | 0 | 0 | 0 | 27.1 | 27.9 | 26.9 | 1.6 | 1.4 | 1.2 | 0 | 26.8 | 27.4 | 26.9 | 1.55 | 1.2 | 0.9 | 24.9 | 24.8 | 26.3 | 1.58 | 1.61 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:15:00 | 88.4 | 101.32 | 839007.98 | 814225.56 | 3.04 | 3846.63 | 626.196 | 43.152 | 15 | 187 | 25.8 | 57.5 | 26 | 57.2 | 0 | 0 | - | - | 28 | 52.3 | 0 | 0 | 0 | 0 | 27.1 | 27.9 | 26.9 | 1.6 | 1.4 | 1.3 | 0 | 26.7 | 27.4 | 26.9 | 1.55 | 1.2 | 0.9 | 24.9 | 24.9 | 26.3 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:20:00 | 89.72 | 102.34 | 839009.3 | 814226.6 | 3.15 | 3846.63 | 626.196 | 5.928 | 15 | 187 | 25.7 | 57.5 | 26 | 57.1 | 0 | 0 | - | - | 28 | 52.3 | 0 | 0 | 0 | 0 | 26.9 | 27.9 | 26.9 | 1.6 | 1.3 | 1.1 | 0 | 26.7 | 27.3 | 26.9 | 1.55 | 1.1 | 0.8 | 24.9 | 24.9 | 26.3 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:25:00 | 90.9 | 102.46 | 839010.58 | 814226.7 | 3.27 | 3801.906 | 670.92 | 52.503 | 15 | 187 | 25.8 | 57.5 | 26.1 | 57.1 | 0 | 0 | - | - | 28 | 52.3 | 0 | 0 | 0 | 0 | 26.9 | 27.8 | 26.9 | 1.6 | 1.3 | 1.1 | 0 | 26.7 | 27.3 | 26.9 | 1.55 | 1.1 | 0.8 | 25 | 24.9 | 26.2 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:30:00 | 97.82 | 102.58 | 839017.56 | 814226.82 | 3.38 | 3809.36 | 663.466 | 94.41 | 15 | 187 | 25.8 | 57.4 | 26.1 | 57.1 | 0 | 0 | - | - | 27.9 | 52.4 | 0 | 0 | 0 | 0 | 26.9 | 27.9 | 26.9 | 1.6 | 1.3 | 1.1 | 0 | 26.7 | 27.3 | 26.9 | 1.55 | 1.1 | 0.8 | 25 | 24.9 | 26.2 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:35:00 | 101.08 | 105.72 | 839020.66 | 814230.04 | 3.5 | 3816.814 | 656.012 | -65.733 | 15 | 187 | 25.8 | 57.4 | 26.1 | 57.1 | 0 | 0 | - | - | 27.9 | 52.4 | 0 | 0 | 0 | 0 | 27 | 27.9 | 26.9 | 1.6 | 1.3 | 1.2 | 0 | 26.7 | 27.3 | 26.9 | 1.55 | 1.1 | 0.8 | 25 | 24.9 | 26.2 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:40:00 | 101.84 | 107.84 | 839021.44 | 814232.1 | 3.61 | 3824.268 | 648.558 | -33.571 | 15 | 187 | 25.8 | 57.4 | 26.1 | 57.1 | 0 | 0 | - | - | 27.9 | 52.4 | 0 | 0 | 0 | 0 | 26.9 | 27.9 | 26.8 | 1.61 | 1.3 | 1.1 | 0 | 26.7 | 27.3 | 26.9 | 1.56 | 1 | 0.7 | 25 | 24.9 | 26.2 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:45:00 | 103.02 | 109.26 | 839022.6 | 814233.5 | 3.73 | 3824.268 | 648.558 | 11.476 | 15 | 187 | 25.8 | 57.4 | 26.1 | 57 | 0 | 0 | - | - | 27.9 | 52.5 | 0 | 0 | 0 | 0 | 26.9 | 27.9 | 26.8 | 1.6 | 1.3 | 1.1 | 0 | 26.7 | 27.3 | 26.8 | 1.56 | 1.1 | 0.8 | 25 | 25 | 26.3 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:50:00 | 106.22 | 109.26 | 839025.86 | 814233.5 | 3.84 | 3809.36 | 663.466 | -12.068 | 15 | 187 | 25.9 | 57.4 | 26.1 | 57.1 | 0 | 0 | - | - | 27.9 | 52.5 | 0 | 0 | 0 | 0 | 26.9 | 27.8 | 26.8 | 1.6 | 1.2 | 1 | 0 | 26.7 | 27.2 | 26.9 | 1.56 | 1 | 0.7 | 25 | 25 | 26.3 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 02:55:00 | 108.9 | 109.7 | 839028.48 | 814234.04 | 3.95 | 3809.36 | 663.466 | -63.156 | 16 | 187 | 25.9 | 57.4 | 26.1 | 57.1 | 0 | 0 | - | - | 27.9 | 52.6 | 0 | 0 | 0 | 0 | 26.8 | 27.8 | 26.8 | 1.61 | 1.2 | 1 | 0 | 26.7 | 27.2 | 26.9 | 1.56 | 0.9 | 0.6 | 25 | 25 | 26.3 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:00:00 | 109.08 | 113.6 | 839028.66 | 814238.02 | 4.07 | 3816.814 | 656.012 | -38.009 | 15 | 187 | 25.9 | 57.4 | 26.1 | 57.1 | 0 | 0 | - | - | 27.9 | 52.6 | 0 | 0 | 0 | 0 | 26.8 | 27.8 | 26.8 | 1.61 | 1.2 | 0.9 | 0 | 26.7 | 27.2 | 26.9 | 1.56 | 0.9 | 0.6 | 25 | 25 | 26.2 | 1.58 | 1.61 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:05:00 | 109.08 | 118.28 | 839028.66 | 814242.56 | 4.18 | 3831.722 | 641.104 | -20.364 | 15 | 187 | 25.9 | 57.4 | 26 | 57.3 | 0 | 0 | - | - | 27.9 | 52.6 | 0 | 0 | 0 | 0 | 26.8 | 27.8 | 26.8 | 1.6 | 1.2 | 0.9 | 0 | 26.7 | 27.2 | 26.8 | 1.56 | 1 | 0.6 | 25.1 | 25 | 26.2 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:10:00 | 110.36 | 121.52 | 839029.94 | 814245.88 | 4.3 | 3846.63 | 626.196 | -75.293 | 15 | 187 | 25.9 | 57.4 | 26 | 57.4 | 0 | 0 | - | - | 27.8 | 52.7 | 0 | 0 | 0 | 0 | 26.7 | 27.8 | 26.7 | 1.61 | 1.1 | 0.9 | 0 | 26.6 | 27.2 | 26.8 | 1.56 | 0.9 | 0.6 | 25.1 | 25 | 26.2 | 1.58 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:15:00 | 110.36 | 127.56 | 839029.94 | 814251.98 | 4.41 | 3846.63 | 626.196 | -109.002 | 15 | 187 | 25.9 | 57.4 | 26.1 | 57.3 | 0 | 0 | - | - | 27.8 | 52.7 | 0 | 0 | 0 | 0 | 26.7 | 27.7 | 26.7 | 1.61 | 1.1 | 0.8 | 0 | 26.6 | 27.2 | 26.8 | 1.56 | 0.9 | 0.6 | 25.1 | 25.1 | 26.2 | 1.58 | 1.61 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:20:00 | 110.36 | 138.98 | 839029.94 | 814263.28 | 4.52 | 3846.63 | 626.196 | -122.248 | 15 | 187 | 25.9 | 57.4 | 26.1 | 57.2 | 0 | 0 | - | - | 27.8 | 52.8 | 0 | 0 | 0 | 0 | 26.7 | 27.7 | 26.7 | 1.61 | 1 | 0.8 | 0 | 26.6 | 27.2 | 26.8 | 1.56 | 0.9 | 0.5 | 25.1 | 25.1 | 26.2 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:25:00 | 110.36 | 152.86 | 839029.94 | 814277.22 | 4.64 | 3854.085 | 618.741 | -32.776 | 15 | 187 | 25.9 | 57.4 | 26.1 | 57.2 | 0 | 0 | - | - | 27.8 | 52.8 | 0 | 0 | 0 | 0 | 26.7 | 27.7 | 26.7 | 1.61 | 1 | 0.8 | 0 | 26.6 | 27.2 | 26.8 | 1.56 | 0.8 | 0.5 | 25.1 | 25.1 | 26.2 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:30:00 | 111 | 155.84 | 839030.58 | 814280.08 | 4.76 | 3854.085 | 618.741 | 26.079 | 14 | 187 | 25.9 | 57.5 | 25.9 | 57.5 | 0 | 0 | - | - | 27.8 | 52.8 | 0 | 0 | 0 | 0 | 26.7 | 27.7 | 26.7 | 1.61 | 1 | 0.8 | 0 | 26.6 | 27.2 | 26.8 | 1.56 | 0.8 | 0.6 | 25.2 | 25.1 | 26.2 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:35:00 | 113.8 | 156.66 | 839033.48 | 814280.9 | 4.87 | 3854.085 | 618.741 | 39.693 | 15 | 187 | 25.9 | 57.5 | 25.9 | 57.7 | 0 | 0 | - | - | 27.8 | 52.9 | 0 | 0 | 0 | 0 | 26.7 | 27.7 | 26.7 | 1.61 | 1 | 0.8 | 0 | 26.6 | 27.2 | 26.8 | 1.56 | 0.8 | 0.6 | 25.2 | 25.2 | 26.2 | 1.58 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:40:00 | 115.44 | 159.56 | 839035.02 | 814283.88 | 4.98 | 3854.085 | 618.741 | -104.224 | 14 | 187 | 25.9 | 57.5 | 26 | 57.5 | 0 | 0 | - | - | 27.8 | 52.9 | 0 | 0 | 0 | 0 | 26.7 | 27.7 | 26.7 | 1.61 | 0.9 | 0.8 | 0 | 26.6 | 27.2 | 26.8 | 1.56 | 0.8 | 0.5 | 25.2 | 25.2 | 26.2 | 1.58 | 1.62 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:45:00 | 117.92 | 161.6 | 839037.72 | 814285.84 | 5.09 | 3854.085 | 618.741 | 108.243 | 15 | 187 | 25.9 | 57.5 | 26.1 | 57.3 | 0 | 0 | - | - | 27.8 | 52.9 | 0 | 0 | 0 | 0 | 26.7 | 27.7 | 26.7 | 1.61 | 0.9 | 0.8 | 0 | 26.6 | 27.2 | 26.8 | 1.56 | 0.8 | 0.6 | 25.2 | 25.2 | 26.3 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:50:00 | 120.08 | 162.22 | 839039.66 | 814286.46 | 5.21 | 3854.085 | 618.741 | 36.816 | 15 | 187 | 25.9 | 57.6 | 26.1 | 57.3 | 0 | 0 | - | - | 27.7 | 53 | 0 | 0 | 0 | 0 | 26.8 | 27.6 | 26.8 | 1.61 | 0.9 | 0.8 | 0 | 26.6 | 27.2 | 26.9 | 1.56 | 0.8 | 0.6 | 25.2 | 25.2 | 26.3 | 1.58 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 03:55:00 | 120.84 | 163.06 | 839040.42 | 814287.32 | 5.32 | 3854.085 | 618.741 | -15.754 | 15 | 187 | 25.9 | 57.6 | 26.1 | 57.3 | 0 | 0 | - | - | 27.7 | 53 | 0 | 0 | 0 | 0 | 26.8 | 27.6 | 26.8 | 1.61 | 0.9 | 0.8 | 0 | 26.6 | 27.2 | 26.9 | 1.56 | 0.7 | 0.6 | 25.2 | 25.2 | 26.3 | 1.58 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:00:00 | 121.06 | 164.08 | 839040.64 | 814288.32 | 5.43 | 3854.085 | 618.741 | -5.215 | 15 | 187 | 25.9 | 57.7 | 26.1 | 57.3 | 0 | 0 | - | - | 27.8 | 53 | 0 | 0 | 0 | 0 | 26.8 | 27.6 | 26.8 | 1.61 | 0.9 | 0.8 | 0 | 26.6 | 27.2 | 26.9 | 1.56 | 0.8 | 0.6 | 25.2 | 25.2 | 26.2 | 1.58 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:05:00 | 121.66 | 164.44 | 839041.24 | 814288.68 | 5.54 | 3854.085 | 618.741 | 4.379 | 15 | 187 | 25.8 | 57.6 | 26.1 | 57.3 | 0 | 0 | - | - | 27.7 | 53 | 0 | 0 | 0 | 0 | 26.7 | 27.6 | 26.8 | 1.61 | 0.9 | 0.7 | 0 | 26.6 | 27.2 | 26.9 | 1.56 | 0.7 | 0.5 | 25.3 | 25.2 | 26.2 | 1.58 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:10:00 | 123.74 | 164.58 | 839043.32 | 814288.84 | 5.65 | 3846.63 | 626.196 | -10.197 | 15 | 187 | 25.9 | 57.8 | 26.1 | 57.3 | 0 | 0 | - | - | 27.7 | 53.1 | 0 | 0 | 0 | 0 | 26.7 | 27.6 | 26.8 | 1.61 | 0.9 | 0.8 | 0 | 26.6 | 27.2 | 26.9 | 1.56 | 0.7 | 0.5 | 25.2 | 25.2 | 26.2 | 1.58 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:15:00 | 124.38 | 166.26 | 839044.02 | 814290.5 | 5.77 | 3854.085 | 618.741 | 29.112 | 15 | 187 | 25.8 | 57.7 | 26.1 | 57.4 | 0 | 0 | - | - | 27.7 | 53.1 | 0 | 0 | 0 | 0 | 26.7 | 27.6 | 26.8 | 1.61 | 0.8 | 0.7 | 0 | 26.6 | 27.1 | 26.9 | 1.56 | 0.7 | 0.4 | 25.3 | 25.2 | 26.1 | 1.59 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:20:00 | 126.28 | 168.1 | 839045.86 | 814292.56 | 5.88 | 3854.085 | 618.741 | -91.975 | 15 | 187 | 25.8 | 57.8 | 26.1 | 57.4 | 0 | 0 | - | - | 27.7 | 53.1 | 0 | 0 | 0 | 0 | 26.7 | 27.6 | 26.7 | 1.61 | 0.9 | 0.7 | 0 | 26.6 | 27.1 | 26.8 | 1.56 | 0.7 | 0.4 | 25.3 | 25.3 | 26.1 | 1.59 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:25:00 | 126.28 | 177.86 | 839045.86 | 814302.18 | 6 | 3876.45 | 596.376 | -124.942 | 14 | 187 | 25.8 | 57.8 | 26.1 | 57.5 | 0 | 0 | - | - | 27.7 | 53.1 | 0 | 0 | 0 | 0 | 26.8 | 27.7 | 26.7 | 1.61 | 0.9 | 0.8 | 0 | 26.6 | 27.1 | 26.8 | 1.56 | 0.7 | 0.4 | 25.3 | 25.3 | 25.9 | 1.58 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:30:00 | 126.28 | 184.74 | 839045.86 | 814309.2 | 6.12 | 3891.36 | 581.466 | -108.601 | 14 | 187 | 25.8 | 57.9 | 26.1 | 57.5 | 0 | 0 | - | - | 27.7 | 53.2 | 0 | 0 | 0 | 0 | 26.8 | 27.7 | 26.7 | 1.61 | 1 | 0.9 | 0 | 26.6 | 27.1 | 26.8 | 1.56 | 0.7 | 0.5 | 25.3 | 25.3 | 26 | 1.58 | 1.61 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:35:00 | 126.28 | 193.18 | 839045.86 | 814317.54 | 6.23 | 3891.36 | 581.466 | -74.644 | 14 | 187 | 25.8 | 57.9 | 26.1 | 57.5 | 0 | 0 | - | - | 27.7 | 53.2 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.7 | 1.61 | 1 | 0.9 | 0 | 26.6 | 27.1 | 26.8 | 1.56 | 0.6 | 0.4 | 25.3 | 25.3 | 26.1 | 1.58 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:40:00 | 127.94 | 197.32 | 839047.52 | 814321.64 | 6.35 | 3891.36 | 581.466 | -93.116 | 14 | 187 | 25.8 | 57.9 | 26.1 | 57.5 | 0 | 0 | - | - | 27.7 | 53.3 | 0 | 0 | 0 | 0 | 26.9 | 27.8 | 26.8 | 1.61 | 1 | 1 | 0 | 26.6 | 27.2 | 26.8 | 1.56 | 0.7 | 0.5 | 25.4 | 25.3 | 26 | 1.58 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:45:00 | 128.08 | 202.76 | 839047.66 | 814327 | 6.47 | 3891.36 | 581.466 | -9.679 | 14 | 187 | 25.8 | 58 | 26.1 | 57.5 | 0 | 0 | - | - | 27.6 | 53.3 | 0 | 0 | 0 | 0 | 27 | 27.8 | 26.8 | 1.61 | 1 | 1.1 | 0 | 26.6 | 27.2 | 26.9 | 1.56 | 0.7 | 0.4 | 25.4 | 25.3 | 25.9 | 1.58 | 1.62 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:50:00 | 133.56 | 202.88 | 839053.16 | 814327.12 | 6.58 | 3891.36 | 581.466 | 26.612 | 14 | 187 | 25.8 | 58 | 26.1 | 57.6 | 0 | 0 | - | - | 27.6 | 53.3 | 0 | 0 | 0 | 0 | 26.9 | 27.8 | 26.7 | 1.61 | 1 | 1 | 0 | 26.6 | 27.2 | 26.8 | 1.56 | 0.7 | 0.3 | 25.4 | 25.4 | 25.9 | 1.58 | 1.62 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 04:55:00 | 134.88 | 204.94 | 839054.48 | 814329.18 | 6.7 | 3891.36 | 581.466 | 14.112 | 14 | 187 | 25.8 | 58 | 26.1 | 57.6 | 0 | 0 | - | - | 27.6 | 53.3 | 0 | 0 | 0 | 0 | 27 | 27.7 | 26.7 | 1.61 | 1 | 1 | 0 | 26.6 | 27.2 | 26.8 | 1.57 | 0.6 | 0.4 | 25.4 | 25.4 | 25.9 | 1.58 | 1.62 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:00:00 | 135.86 | 208 | 839055.44 | 814332.42 | 6.82 | 3891.36 | 581.466 | -42.546 | 14 | 187 | 25.8 | 58.1 | 26.1 | 57.6 | 0 | 0 | - | - | 27.6 | 53.4 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.7 | 1.61 | 0.9 | 0.9 | 0 | 26.6 | 27.1 | 26.7 | 1.57 | 0.6 | 0.3 | 25.4 | 25.4 | 26 | 1.59 | 1.62 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:05:00 | 135.98 | 211.66 | 839055.56 | 814336.1 | 6.93 | 3891.36 | 581.466 | -112.307 | 14 | 187 | 25.7 | 58.1 | 26.1 | 57.6 | 0 | 0 | - | - | 27.6 | 53.4 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.7 | 1.61 | 0.9 | 0.9 | 0 | 26.6 | 27.1 | 26.7 | 1.57 | 0.6 | 0.4 | 25.4 | 25.4 | 26 | 1.59 | 1.62 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:10:00 | 135.98 | 220.44 | 839055.56 | 814344.94 | 7.04 | 3898.815 | 574.011 | -124.858 | 14 | 187 | 25.8 | 58.1 | 26.1 | 57.6 | 0 | 0 | - | - | 27.6 | 53.5 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.7 | 1.61 | 0.9 | 0.9 | 0 | 26.5 | 27.1 | 26.8 | 1.57 | 0.5 | 0.3 | 25.4 | 25.4 | 25.9 | 1.59 | 1.62 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:15:00 | 136 | 228.62 | 839055.58 | 814353.02 | 7.16 | 3906.27 | 566.556 | -18.708 | 13 | 187 | 25.7 | 58.1 | 26.1 | 57.6 | 0 | 0 | - | - | 27.6 | 53.5 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.7 | 1.61 | 0.9 | 0.8 | 0 | 26.5 | 27.1 | 26.8 | 1.57 | 0.6 | 0.3 | 25.5 | 25.5 | 26.1 | 1.59 | 1.62 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:20:00 | 136 | 236.52 | 839055.58 | 814361.16 | 7.28 | 3936.09 | 536.736 | -151.992 | 13 | 187 | 25.7 | 58.1 | 26.1 | 57.7 | 0 | 0 | - | - | 27.6 | 53.5 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.7 | 1.61 | 0.9 | 0.9 | 0 | 26.5 | 27.2 | 26.8 | 1.57 | 0.5 | 0.3 | 25.5 | 25.5 | 26.1 | 1.59 | 1.62 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:25:00 | 136 | 253.3 | 839055.58 | 814378.02 | 7.4 | 3943.546 | 529.281 | -133.524 | 13 | 187 | 25.7 | 58.1 | 26.1 | 57.7 | 0 | 0 | - | - | 27.6 | 53.5 | 0 | 0 | 0 | 0 | 27 | 27.8 | 26.7 | 1.61 | 1 | 0.9 | 0 | 26.6 | 27.2 | 26.9 | 1.57 | 0.6 | 0.3 | 25.6 | 25.5 | 26.1 | 1.59 | 1.62 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:30:00 | 136 | 267.06 | 839055.58 | 814391.38 | 7.52 | 3951 | 521.826 | -199.712 | 12 | 187 | 25.8 | 58.2 | 26.1 | 57.8 | 0 | 0 | - | - | 27.6 | 53.5 | 0 | 0 | 0 | 0 | 27 | 27.7 | 26.7 | 1.62 | 0.9 | 0.9 | 0 | 26.6 | 27.2 | 26.9 | 1.57 | 0.6 | 0.3 | 25.6 | 25.6 | 26.1 | 1.59 | 1.62 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:35:00 | 136 | 283.32 | 839055.58 | 814408.16 | 7.64 | 3973.363 | 499.463 | -238.952 | 12 | 187 | 25.8 | 58.2 | 26.1 | 57.7 | 0 | 0 | - | - | 27.6 | 53.5 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.7 | 1.62 | 0.8 | 0.8 | 0 | 26.6 | 27.2 | 26.9 | 1.57 | 0.6 | 0.2 | 25.6 | 25.6 | 26.2 | 1.59 | 1.63 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:40:00 | 146.56 | 292.66 | 839066.6 | 814416.9 | 7.76 | 3995.728 | 477.098 | 409.312 | 12 | 187 | 25.8 | 58.2 | 26.1 | 57.8 | 0 | 0 | - | - | 27.6 | 53.6 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.8 | 1.62 | 0.8 | 0.8 | 0 | 26.6 | 27.2 | 27 | 1.57 | 0.6 | 0.2 | 25.7 | 25.7 | 26.2 | 1.59 | 1.63 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:45:00 | 181.56 | 292.66 | 839101.84 | 814416.9 | 7.88 | 3973.363 | 499.463 | 395.391 | 12 | 187 | 25.8 | 58.2 | 26.1 | 57.8 | 0 | 0 | - | - | 27.6 | 53.6 | 0 | 0 | 0 | 0 | 27 | 27.8 | 26.9 | 1.62 | 0.9 | 0.9 | 0 | 26.6 | 27.3 | 27.1 | 1.57 | 0.6 | 0.3 | 25.7 | 25.7 | 26.4 | 1.59 | 1.63 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:50:00 | 206.2 | 292.66 | 839126.46 | 814416.9 | 8.01 | 3936.089 | 536.737 | 351.729 | 13 | 187 | 25.8 | 58.2 | 26.1 | 57.8 | 0 | 0 | - | - | 27.7 | 53.6 | 0 | 0 | 0 | 0 | 27.1 | 27.9 | 26.9 | 1.62 | 0.9 | 0.9 | 0 | 26.7 | 27.3 | 27.1 | 1.57 | 0.6 | 0.3 | 25.7 | 25.7 | 26.7 | 1.6 | 1.63 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 05:55:00 | 244.9 | 292.66 | 839164.78 | 814416.9 | 8.13 | 3898.815 | 574.011 | 279.315 | 14 | 187 | 25.9 | 58.2 | 26.2 | 57.7 | 0 | 0 | - | - | 27.7 | 53.6 | 0 | 0 | 0 | 0 | 27.1 | 27.8 | 27 | 1.62 | 0.8 | 0.9 | 0 | 26.7 | 27.4 | 27.2 | 1.58 | 0.7 | 0.4 | 25.7 | 25.7 | 26.7 | 1.6 | 1.63 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:00:00 | 257.4 | 295.34 | 839176.98 | 814420.08 | 8.25 | 3891.36 | 581.466 | -260.543 | 14 | 187 | 25.9 | 58.2 | 26.3 | 57.7 | 0 | 0 | - | - | 27.7 | 53.5 | 0 | 0 | 0 | 0 | 27.1 | 27.8 | 27.1 | 1.62 | 0.8 | 0.8 | 0 | 26.8 | 27.4 | 27.2 | 1.58 | 0.6 | 0.3 | 25.7 | 25.7 | 26.6 | 1.6 | 1.63 | 1.61 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:05:00 | 257.4 | 314.58 | 839176.98 | 814439.06 | 8.38 | 3913.725 | 559.101 | -166.843 | 14 | 187 | 26 | 58.1 | 26.3 | 57.6 | 0 | 0 | - | - | 27.8 | 53.6 | 0 | 0 | 0 | 0 | 27.1 | 27.8 | 27.1 | 1.63 | 0.8 | 0.8 | 0 | 26.7 | 27.4 | 27.3 | 1.58 | 0.6 | 0.2 | 25.8 | 25.7 | 26.6 | 1.6 | 1.63 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:10:00 | 257.62 | 323.02 | 839177.28 | 814447.26 | 8.5 | 3928.635 | 544.191 | 50.156 | 14 | 187 | 26 | 58.1 | 26.4 | 57.5 | 0 | 0 | - | - | 27.8 | 53.5 | 0 | 0 | 0 | 0 | 27.1 | 27.9 | 27.1 | 1.63 | 0.9 | 0.8 | 0 | 26.7 | 27.4 | 27.4 | 1.58 | 0.7 | 0.3 | 25.8 | 25.8 | 26.8 | 1.6 | 1.63 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:15:00 | 262.24 | 323.5 | 839181.82 | 814447.74 | 8.62 | 3921.18 | 551.646 | 15.979 | 14 | 187 | 26.1 | 58 | 26.5 | 57.4 | 0 | 0 | - | - | 27.9 | 53.5 | 0 | 0 | 0 | 0 | 27.2 | 28 | 27.2 | 1.63 | 0.9 | 0.8 | 0 | 26.8 | 27.5 | 27.5 | 1.58 | 0.6 | 0.3 | 25.8 | 25.8 | 26.9 | 1.6 | 1.64 | 1.61 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:20:00 | 270.28 | 323.5 | 839190.04 | 814447.74 | 8.74 | 3913.725 | 559.101 | 108.516 | 14 | 187 | 26 | 58.1 | 26.5 | 57.4 | 0 | 0 | - | - | 27.9 | 53.5 | 0 | 0 | 0 | 0 | 27.3 | 28 | 27.3 | 1.63 | 0.9 | 0.9 | 0 | 26.9 | 27.6 | 27.5 | 1.58 | 0.7 | 0.4 | 25.8 | 25.8 | 27 | 1.6 | 1.64 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:25:00 | 285.88 | 323.5 | 839205.78 | 814447.74 | 8.86 | 3883.905 | 588.921 | 236.883 | 14 | 187 | 26 | 58.2 | 26.5 | 57.3 | 0 | 0 | - | - | 27.9 | 53.4 | 0 | 0 | 0 | 0 | 27.4 | 28.2 | 27.3 | 1.63 | 0.9 | 0.9 | 0 | 26.9 | 27.6 | 27.6 | 1.58 | 0.7 | 0.3 | 25.9 | 25.8 | 27 | 1.6 | 1.64 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:30:00 | 300.96 | 323.5 | 839220.8 | 814447.74 | 8.97 | 3883.905 | 588.921 | 113.105 | 15 | 187 | 26.1 | 58.1 | 26.6 | 57.3 | 0 | 0 | - | - | 28 | 53.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 25.8 | 25.8 | 27.1 | 1.61 | 1.64 | 1.61 | 1.63 | 0 | 0 | - | -
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:35:00 | 314.34 | 323.5 | 839234.18 | 814447.74 | 9.1 | 3868.996 | 603.83 | 168.719 | 15 | 187 | 26.2 | 58 | 26.6 | 57.2 | 0 | 0 | - | - | 28.1 | 53.3 | 0 | 0 | 0 | 0 | 27.5 | 28.4 | 27.4 | 1.64 | 1 | 1 | 0 | 27.1 | 27.8 | 27.7 | 1.59 | 0.7 | 0.5 | 25.9 | 25.9 | 27.2 | 1.61 | 1.64 | 1.62 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:40:00 | 335.04 | 323.5 | 839255.18 | 814447.74 | 9.22 | 3839.178 | 633.648 | 271.739 | 15 | 187 | 26.3 | 57.8 | 26.7 | 57.2 | 0 | 0 | - | - | 28.1 | 53.3 | 0 | 0 | 0 | 0 | 27.6 | 28.4 | 27.5 | 1.64 | 1 | 1 | 0 | 27.2 | 27.8 | 27.8 | 1.59 | 0.8 | 0.5 | 25.9 | 25.9 | 27.4 | 1.61 | 1.64 | 1.62 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:45:00 | 368.8 | 323.5 | 839289.12 | 814447.74 | 9.35 | 3809.359 | 663.467 | 423.076 | 16 | 187 | 26.4 | 57.7 | 26.7 | 57.2 | 0 | 0 | - | - | 28.2 | 53.2 | 0 | 0 | 0 | 0 | 27.7 | 28.5 | 27.7 | 1.64 | 1.1 | 1.1 | 0 | 27.3 | 27.9 | 27.9 | 1.59 | 0.9 | 0.6 | 25.9 | 25.9 | 28.1 | 1.61 | 1.65 | 1.62 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:50:00 | 405.6 | 323.5 | 839325.98 | 814447.74 | 9.49 | 3779.539 | 693.287 | 362.707 | 17 | 187 | 26.4 | 57.6 | 26.8 | 57.1 | 0 | 0 | - | - | 28.3 | 53.2 | 0 | 0 | 0 | 0 | 28 | 28.8 | 28 | 1.65 | 1.3 | 1.2 | 0 | 27.6 | 28.1 | 28.2 | 1.59 | 1 | 0.8 | 25.9 | 25.9 | 28.5 | 1.62 | 1.65 | 1.62 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 06:55:00 | 435.56 | 323.5 | 839355.62 | 814447.74 | 9.63 | 3749.721 | 723.105 | 307.101 | 18 | 187 | 26.6 | 57.4 | 26.9 | 56.9 | 0 | 0 | - | - | 28.4 | 53.1 | 0 | 0 | 0 | 0 | 28.3 | 29.1 | 28.4 | 1.65 | 1.5 | 1.4 | 0 | 27.9 | 28.4 | 28.5 | 1.6 | 1.2 | 1 | 26 | 25.9 | 28.7 | 1.63 | 1.66 | 1.63 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:00:00 | 445.04 | 323.72 | 839364.62 | 814448.06 | 9.74 | 3742.266 | 730.56 | -77.628 | 18 | 187 | 26.8 | 57.2 | 27.1 | 56.7 | 0 | 0 | - | - | 28.5 | 53 | 0 | 0 | 0 | 0 | 28.5 | 29.4 | 28.6 | 1.66 | 1.6 | 1.5 | 0 | 28.1 | 28.7 | 28.7 | 1.6 | 1.4 | 1.2 | 26 | 26 | 28.8 | 1.63 | 1.67 | 1.63 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:05:00 | 445.04 | 346.46 | 839364.62 | 814471.48 | 9.87 | 3749.721 | 723.105 | -458.695 | 17 | 187 | 27 | 56.9 | 27.2 | 56.6 | 0 | 0 | - | - | 28.7 | 52.7 | 0 | 0 | 0 | 0 | 28.6 | 29.6 | 28.8 | 1.66 | 1.7 | 1.5 | 0 | 28.3 | 28.9 | 28.8 | 1.61 | 1.4 | 1.2 | 26 | 26 | 28.8 | 1.63 | 1.67 | 1.63 | 1.65 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:10:00 | 445.04 | 404.6 | 839364.62 | 814531.24 | 10.01 | 3809.36 | 663.466 | -970.523 | 16 | 187 | 27.1 | 56.8 | 27.3 | 56.4 | 0 | 0 | - | - | 28.8 | 52.6 | 0 | 0 | 0 | 0 | 28.9 | 29.9 | 29.1 | 1.67 | 2 | 1.7 | 0 | 28.6 | 29.1 | 29 | 1.61 | 1.6 | 1.4 | 26.1 | 26.1 | 29.1 | 1.64 | 1.67 | 1.64 | 1.65 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:15:00 | 445.04 | 472.44 | 839364.62 | 814596.68 | 10.15 | 3816.814 | 656.012 | -651.543 | 16 | 187 | 27.3 | 56.6 | 27.4 | 56.3 | 0 | 0 | - | - | 29 | 52.4 | 0 | 0 | 0 | 0 | 29.1 | 30.2 | 29.4 | 1.67 | 2.1 | 1.9 | 0 | 28.8 | 29.4 | 29.3 | 1.61 | 1.8 | 1.6 | 26.2 | 26.2 | 29.3 | 1.65 | 1.68 | 1.64 | 1.66 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:20:00 | 446.54 | 496.72 | 839366.24 | 814620.96 | 10.29 | 3816.814 | 656.012 | 80.376 | 15 | 187 | 27.4 | 56.3 | 27.5 | 56.3 | 0 | 0 | - | - | 29.1 | 52.2 | 0 | 0 | 0 | 0 | 29.3 | 30.3 | 29.6 | 1.68 | 2.2 | 1.9 | 0 | 29.1 | 29.6 | 29.5 | 1.62 | 1.9 | 1.8 | 26.4 | 26.4 | 29.4 | 1.65 | 1.68 | 1.65 | 1.66 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:25:00 | 447 | 508.5 | 839366.58 | 814633.6 | 10.41 | 3846.631 | 626.195 | -544.078 | 15 | 187 | 27.6 | 56.2 | 27.7 | 56.1 | 0 | 0 | - | - | 29.3 | 52.1 | 0 | 0 | 0 | 0 | 29.6 | 30.5 | 29.9 | 1.68 | 2.2 | 2.1 | 0 | 29.3 | 29.8 | 29.6 | 1.62 | 1.9 | 1.8 | 26.5 | 26.4 | 29.1 | 1.65 | 1.69 | 1.65 | 1.67 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:30:00 | 447 | 545.38 | 839366.58 | 814669.72 | 10.55 | 3883.905 | 588.921 | -210.323 | 14 | 187 | 27.7 | 56.1 | 27.9 | 55.9 | 0 | 0 | - | - | 29.4 | 51.9 | 0 | 0 | 0 | 0 | 29.7 | 30.6 | 29.9 | 1.68 | 2.3 | 2.2 | 0 | 29.4 | 29.9 | 29.6 | 1.63 | 2 | 1.8 | 26.6 | 26.5 | 29 | 1.66 | 1.69 | 1.65 | 1.67 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:35:00 | 456.72 | 547.92 | 839376.68 | 814672.16 | 10.67 | 3883.905 | 588.921 | 240.027 | 15 | 187 | 27.8 | 55.9 | 28 | 55.8 | 0 | 0 | - | - | 29.5 | 51.8 | 0 | 0 | 0 | 0 | 29.9 | 30.7 | 30 | 1.69 | 2.3 | 2.2 | 0 | 29.5 | 30 | 29.7 | 1.63 | 2 | 1.8 | 26.6 | 26.6 | 29.2 | 1.66 | 1.69 | 1.66 | 1.68 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:40:00 | 472.82 | 547.92 | 839392.52 | 814672.16 | 10.8 | 3861.54 | 611.286 | 79.01 | 15 | 187 | 27.9 | 55.8 | 28 | 55.9 | 0 | 0 | - | - | 29.6 | 51.8 | 0 | 0 | 0 | 0 | 30 | 30.8 | 30.2 | 1.69 | 2.4 | 2.3 | 0 | 29.6 | 30.1 | 29.7 | 1.63 | 2 | 1.9 | 26.7 | 26.6 | 29.3 | 1.66 | 1.7 | 1.66 | 1.68 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:45:00 | 477.46 | 547.92 | 839397.34 | 814672.16 | 10.91 | 3861.54 | 611.286 | 186.676 | 15 | 187 | 28 | 55.7 | 28 | 56 | 0 | 0 | - | - | 29.7 | 51.6 | 0 | 0 | 0 | 0 | 30.1 | 30.8 | 30.2 | 1.69 | 2.3 | 2.3 | 0 | 29.7 | 30.2 | 29.9 | 1.64 | 2.1 | 1.9 | 26.7 | 26.7 | 29.7 | 1.66 | 1.7 | 1.66 | 1.68 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:50:00 | 504.7 | 547.92 | 839424.68 | 814672.16 | 11.04 | 3831.724 | 641.102 | 193.619 | 16 | 187 | 28.2 | 55.6 | 28.1 | 55.8 | 0 | 0 | - | - | 29.9 | 51.6 | 0 | 0 | 0 | 0 | 30.1 | 30.8 | 30.3 | 1.69 | 2.3 | 2.3 | 0 | 29.8 | 30.3 | 30.1 | 1.64 | 2.2 | 2 | 26.7 | 26.7 | 29.9 | 1.66 | 1.7 | 1.67 | 1.68 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 07:55:00 | 542.4 | 547.92 | 839462.52 | 814672.16 | 11.16 | 3794.449 | 678.377 | 306.026 | 17 | 187 | 28.3 | 55.4 | 28.3 | 55.5 | 0 | 0 | - | - | 30 | 51.4 | 0 | 0 | 0 | 0 | 30.2 | 31 | 30.5 | 1.69 | 2.5 | 2.5 | 0 | 29.9 | 30.4 | 30.4 | 1.64 | 2.3 | 2.1 | 26.7 | 26.7 | 30.2 | 1.67 | 1.7 | 1.67 | 1.68 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:00:00 | 556.3 | 550.78 | 839475.88 | 814676.38 | 11.29 | 3786.994 | 685.832 | -304.181 | 17 | 187 | 28.5 | 55.2 | 28.5 | 55.3 | 0 | 0 | - | - | 30.2 | 51.3 | 0 | 0 | 0 | 0 | 30.3 | 31.1 | 30.7 | 1.69 | 2.6 | 2.6 | 0 | 30.1 | 30.6 | 30.7 | 1.64 | 2.4 | 2.2 | 26.7 | 26.7 | 30.6 | 1.66 | 1.7 | 1.67 | 1.68 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:05:00 | 556.3 | 577.78 | 839475.88 | 814702.4 | 11.41 | 3816.814 | 656.012 | -240.284 | 16 | 187 | 28.7 | 55 | 28.7 | 55.2 | 0 | 0 | - | - | 30.3 | 51.1 | 0 | 0 | 0 | 0 | 30.6 | 31.2 | 30.9 | 1.7 | 2.6 | 2.8 | 0 | 30.3 | 30.7 | 31 | 1.64 | 2.5 | 2.4 | 26.7 | 26.7 | 30.8 | 1.67 | 1.7 | 1.67 | 1.69 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:10:00 | 556.3 | 596.66 | 839475.88 | 814720.94 | 11.54 | 3831.724 | 641.102 | -6.309 | 16 | 187 | 28.9 | 54.7 | 28.9 | 54.9 | 0 | 0 | - | - | 30.5 | 50.9 | 0 | 0 | 0 | 0 | 30.9 | 31.5 | 31.4 | 1.7 | 2.9 | 3 | 0 | 30.5 | 30.9 | 31.3 | 1.64 | 2.7 | 2.6 | 26.8 | 26.8 | 31 | 1.67 | 1.71 | 1.67 | 1.69 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:15:00 | 556.3 | 598.16 | 839475.88 | 814722.4 | 11.65 | 3831.724 | 641.102 | -4.79 | 16 | 187 | 29.2 | 54.3 | 29.1 | 54.7 | 0 | 0 | - | - | 30.7 | 50.7 | 0 | 0 | 0 | 0 | 31.1 | 31.8 | 31.8 | 1.7 | 3.1 | 3.2 | 0 | 30.7 | 31.2 | 31.5 | 1.65 | 2.8 | 2.7 | 26.9 | 26.8 | 31.1 | 1.67 | 1.71 | 1.68 | 1.69 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:20:00 | 556.3 | 606.06 | 839475.88 | 814730.54 | 11.77 | 3839.178 | 633.648 | -253.556 | 15 | 187 | 29.4 | 54.1 | 29.2 | 54.6 | 0 | 0 | - | - | 31 | 50.4 | 0 | 0 | 0 | 0 | 31.4 | 32 | 32.1 | 1.7 | 3.3 | 3.3 | 0 | 30.9 | 31.4 | 31.7 | 1.65 | 3 | 2.8 | 26.9 | 26.8 | 31.2 | 1.68 | 1.71 | 1.68 | 1.69 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:25:00 | 556.3 | 627.18 | 839475.88 | 814751.62 | 11.89 | 3868.995 | 603.831 | -114.709 | 15 | 187 | 29.6 | 53.9 | 29.4 | 54.4 | 0 | 0 | - | - | 31.2 | 50.2 | 0 | 0 | 0 | 0 | 31.5 | 32.2 | 32.2 | 1.7 | 3.4 | 3.5 | 0 | 31.1 | 31.5 | 31.9 | 1.65 | 3.1 | 3 | 26.9 | 26.9 | 31.3 | 1.68 | 1.71 | 1.68 | 1.7 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:30:00 | 558.1 | 634.16 | 839477.68 | 814758.88 | 12.01 | 3868.995 | 603.831 | -231.552 | 15 | 187 | 29.9 | 53.5 | 29.5 | 54.2 | 0 | 0 | - | - | 31.4 | 50 | 0 | 0 | 0 | 0 | 31.7 | 32.3 | 32.4 | 1.71 | 3.5 | 3.6 | 0 | 31.3 | 31.7 | 32.2 | 1.66 | 3.2 | 3.1 | 27 | 26.9 | 31.4 | 1.68 | 1.71 | 1.68 | 1.7 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:35:00 | 558.1 | 664.12 | 839477.68 | 814788.72 | 12.13 | 3906.27 | 566.556 | -231.568 | 14 | 187 | 30 | 53.4 | 29.7 | 54.1 | 0 | 0 | - | - | 31.5 | 50 | 0 | 0 | 0 | 0 | 31.9 | 32.5 | 32.6 | 1.71 | 3.7 | 3.8 | 0 | 31.4 | 31.8 | 32.3 | 1.66 | 3.3 | 3.2 | 27 | 27 | 31.2 | 1.68 | 1.72 | 1.69 | 1.7 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:40:00 | 558.1 | 675 | 839477.68 | 814799.24 | 12.25 | 3936.09 | 536.736 | -15.822 | 13 | 187 | 30.1 | 53.2 | 29.8 | 53.9 | 0 | 0 | - | - | 31.7 | 49.7 | 0 | 0 | 0 | 0 | 32 | 32.6 | 32.7 | 1.71 | 3.7 | 3.8 | 0 | 31.5 | 31.9 | 32.4 | 1.66 | 3.3 | 3.2 | 27.1 | 27.1 | 31.4 | 1.68 | 1.72 | 1.69 | 1.7 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:45:00 | 564.5 | 675.48 | 839484.72 | 814799.72 | 12.37 | 3906.27 | 566.556 | 256.625 | 14 | 187 | 30.3 | 52.8 | 29.9 | 53.8 | 0 | 0 | - | - | 31.9 | 49.6 | 0 | 0 | 0 | 0 | 32.1 | 32.7 | 32.8 | 1.71 | 3.7 | 3.8 | 0 | 31.6 | 32 | 32.5 | 1.66 | 3.4 | 3.3 | 27.1 | 27.1 | 31.5 | 1.69 | 1.72 | 1.69 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:50:00 | 590.54 | 675.48 | 839510.58 | 814799.72 | 12.48 | 3898.815 | 574.011 | 473.001 | 14 | 187 | 30.4 | 52.8 | 30 | 53.7 | 0 | 0 | - | - | 32 | 49.5 | 0 | 0 | 0 | 0 | 32.1 | 32.9 | 33 | 1.72 | 3.9 | 3.9 | 0 | 31.7 | 32.1 | 32.6 | 1.66 | 3.5 | 3.4 | 27.2 | 27.1 | 31.9 | 1.69 | 1.72 | 1.69 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 08:55:00 | 634.52 | 675.48 | 839554.74 | 814799.72 | 12.61 | 3854.086 | 618.74 | 603.54 | 15 | 187 | 30.6 | 52.7 | 30.1 | 53.6 | 0 | 0 | - | - | 32.2 | 49.4 | 0 | 0 | 0 | 0 | 32.4 | 33.1 | 33.1 | 1.72 | 4.1 | 4.1 | 0 | 31.9 | 32.3 | 32.8 | 1.66 | 3.6 | 3.5 | 27.2 | 27.2 | 32.2 | 1.69 | 1.72 | 1.69 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:00:00 | 683.66 | 675.48 | 839603.74 | 814799.72 | 12.74 | 3809.359 | 663.467 | 341.15 | 16 | 187 | 30.7 | 52.6 | 30.3 | 53.5 | 0 | 0 | - | - | 32.3 | 49.3 | 0 | 0 | 0 | 0 | 32.5 | 33.3 | 33.3 | 1.72 | 4.3 | 4.2 | 0 | 32 | 32.5 | 33 | 1.67 | 3.8 | 3.6 | 27.2 | 27.2 | 32.4 | 1.69 | 1.72 | 1.69 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:05:00 | 699.8 | 675.48 | 839619.4 | 814799.72 | 12.85 | 3786.996 | 685.83 | 70.264 | 17 | 187 | 30.9 | 52.3 | 30.5 | 53.2 | 0 | 0 | - | - | 32.5 | 49.1 | 0 | 0 | 0 | 0 | 32.6 | 33.5 | 33.4 | 1.72 | 4.5 | 4.3 | 0 | 32.2 | 32.7 | 33.2 | 1.67 | 3.9 | 3.8 | 27.2 | 27.2 | 32.6 | 1.69 | 1.73 | 1.7 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:10:00 | 701.36 | 680.18 | 839621.02 | 814804.42 | 12.97 | 3794.45 | 678.376 | 143.468 | 16 | 187 | 31.2 | 51.9 | 30.6 | 53 | 0 | 0 | - | - | 32.7 | 49 | 0 | 0 | 0 | 0 | 32.8 | 33.6 | 33.6 | 1.72 | 4.4 | 4.4 | 0 | 32.4 | 32.8 | 33.4 | 1.67 | 3.9 | 3.8 | 27.2 | 27.2 | 32.6 | 1.69 | 1.73 | 1.7 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:15:00 | 731.96 | 680.18 | 839652.56 | 814804.42 | 13.09 | 3764.631 | 708.195 | 655.136 | 17 | 187 | 31.4 | 51.8 | 30.8 | 52.9 | 0 | 0 | - | - | 32.9 | 48.8 | 0 | 0 | 0 | 0 | 32.9 | 33.7 | 33.8 | 1.72 | 4.5 | 4.5 | 0 | 32.5 | 32.9 | 33.5 | 1.67 | 4 | 4 | 27.3 | 27.3 | 33.2 | 1.7 | 1.73 | 1.7 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:20:00 | 789.28 | 680.18 | 839710.18 | 814804.42 | 13.23 | 3719.902 | 752.924 | 670.125 | 18 | 187 | 31.6 | 51.5 | 31 | 52.7 | 0 | 0 | - | - | 33.1 | 48.6 | 0 | 0 | 0 | 0 | 33.1 | 33.9 | 33.9 | 1.72 | 4.7 | 4.7 | 0 | 32.7 | 33.1 | 33.8 | 1.67 | 4.2 | 4.1 | 27.3 | 27.2 | 33 | 1.7 | 1.73 | 1.7 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:25:00 | 846.6 | 680.18 | 839766.7 | 814804.42 | 13.36 | 3652.812 | 820.014 | 508.823 | 20 | 187 | 31.7 | 51.4 | 31.2 | 52.4 | 0 | 0 | - | - | 33.3 | 48.4 | 0 | 0 | 0 | 0 | 33.2 | 33.9 | 34 | 1.73 | 4.6 | 4.7 | 0 | 32.8 | 33.2 | 33.9 | 1.68 | 4.2 | 4.2 | 27.4 | 27.3 | 33 | 1.7 | 1.74 | 1.7 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:30:00 | 880.42 | 680.18 | 839800.46 | 814804.42 | 13.5 | 3622.992 | 849.834 | 229.481 | 21 | 187 | 31.9 | 51.2 | 31.4 | 52.3 | 0 | 0 | - | - | 33.6 | 48.3 | 0 | 0 | 0 | 0 | 33.3 | 34 | 34.1 | 1.73 | 4.7 | 4.8 | 0 | 33 | 33.3 | 34.1 | 1.68 | 4.3 | 4.3 | 27.4 | 27.4 | 33.5 | 1.7 | 1.74 | 1.71 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:35:00 | 892.56 | 680.52 | 839812.14 | 814804.76 | 13.62 | 3608.082 | 864.744 | 12.835 | 21 | 187 | 32.2 | 50.9 | 31.5 | 52.2 | 0 | 0 | - | - | 33.7 | 48.1 | 0 | 0 | 0 | 0 | 33.6 | 34.2 | 34.4 | 1.73 | 4.8 | 5 | 0 | 33.1 | 33.5 | 34.3 | 1.68 | 4.4 | 4.4 | 27.4 | 27.4 | 33.5 | 1.7 | 1.74 | 1.71 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:40:00 | 892.68 | 694.7 | 839812.26 | 814819.06 | 13.74 | 3615.537 | 857.289 | -82.655 | 21 | 187 | 32.4 | 50.7 | 31.7 | 51.9 | 0 | 0 | - | - | 34 | 48 | 0 | 0 | 0 | 0 | 33.7 | 34.3 | 34.6 | 1.73 | 4.9 | 5.1 | 0 | 33.3 | 33.6 | 34.5 | 1.68 | 4.5 | 4.5 | 27.5 | 27.5 | 33.8 | 1.7 | 1.74 | 1.71 | 1.73 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:45:00 | 893.04 | 703.06 | 839812.62 | 814827.38 | 13.86 | 3630.447 | 842.379 | -73.562 | 20 | 187 | 32.6 | 50.5 | 31.8 | 51.8 | 0 | 0 | - | - | 34.1 | 47.8 | 0 | 0 | 0 | 0 | 33.9 | 34.4 | 34.7 | 1.74 | 5 | 5.2 | 0 | 33.4 | 33.8 | 34.8 | 1.69 | 4.6 | 4.6 | 27.5 | 27.5 | 33.9 | 1.71 | 1.74 | 1.71 | 1.73 | 120 | 120 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:50:00 | 893.04 | 720.62 | 839812.62 | 814845.28 | 14.51 | 3645.357 | 827.469 | -135.491 | 20 | 187 | 32.7 | 50.3 | 31.9 | 51.7 | 0 | 0 | - | - | 34.3 | 47.6 | 282 | 266 | 64 | 64.1 | 65.5 | 27.2 | 42.9 | 2.7 | 12.6 | 19.1 | 64.1 | 67.4 | 27.4 | 45 | 2.81 | 12.2 | 18.2 | 22.8 | 25.4 | 34 | 2.72 | 1.15 | 2.91 | 1.17 | 281 | 265 | 3000 | 3027
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 09:55:00 | 910.92 | 722.24 | 839831.9 | 814846.48 | 15.42 | 3630.447 | 842.379 | 563.041 | 20 | 187 | 32.9 | 49.9 | 32 | 51.4 | 0 | 0 | - | - | 34.5 | 47.5 | 281 | 265 | 63.9 | 64 | 68.7 | 24.4 | 43.1 | 2.66 | 9.7 | 22.9 | 63.8 | 71.2 | 25.1 | 45.7 | 2.81 | 10 | 22.1 | 21.6 | 23.4 | 32.9 | 2.62 | 1.14 | 2.85 | 1.15 | 281 | 265 | 2793 | 2793
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:00:00 | 939.18 | 722.24 | 839858.76 | 814846.48 | 16.17 | 3600.627 | 872.199 | 6.924 | 21 | 187 | 32.9 | 49.6 | 32 | 51.2 | 0 | 0 | - | - | 34.7 | 47.4 | 277 | 264 | 57.1 | 57.5 | 65.6 | 23.9 | 41.4 | 2.52 | 8.3 | 21.9 | 57.4 | 68.5 | 24.6 | 44.1 | 2.66 | 8.4 | 21.5 | 21.4 | 23.2 | 32.4 | 2.5 | 1.17 | 2.7 | 1.19 | 273 | 262 | 2262 | 2262
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:05:00 | 949.76 | 722.24 | 839869.92 | 814846.48 | 16.82 | 3593.172 | 879.654 | 380.581 | 21 | 187 | 33 | 49.3 | 32 | 51.1 | 0 | 0 | - | - | 34.8 | 47.2 | 271 | 261 | 57 | 56.8 | 64.6 | 23.8 | 41.4 | 2.52 | 8.6 | 21 | 57.2 | 66.8 | 24.6 | 43.8 | 2.64 | 8.7 | 20.1 | 21.4 | 23.1 | 32.6 | 2.5 | 1.16 | 2.7 | 1.18 | 271 | 261 | 2245 | 2245
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:10:00 | 980.52 | 722.24 | 839900.82 | 814846.48 | 17.46 | 3563.352 | 909.474 | 309.028 | 22 | 187 | 33 | 49.2 | 31.9 | 51 | 0 | 0 | - | - | 34.9 | 47.1 | 270 | 261 | 55.9 | 56.3 | 64.2 | 23.8 | 41.2 | 2.52 | 8.4 | 20.5 | 56.2 | 66.3 | 24.4 | 43.7 | 2.63 | 8.5 | 19.9 | 21.4 | 23.1 | 33.6 | 2.51 | 1.16 | 2.7 | 1.18 | 269 | 261 | 2185 | 2185
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:15:00 | 1014.56 | 722.24 | 839934.6 | 814846.48 | 18.11 | 3526.078 | 946.748 | 525.267 | 23 | 187 | 32.9 | 49.2 | 31.8 | 51 | 0 | 0 | - | - | 35 | 46.9 | 269 | 261 | 57.3 | 56.9 | 64.3 | 23.7 | 41.3 | 2.51 | 8.6 | 20.8 | 57.2 | 66.7 | 24.2 | 43.7 | 2.64 | 8.6 | 20 | 21.2 | 22.8 | 32.8 | 2.49 | 1.14 | 2.71 | 1.17 | 269 | 261 | 2235 | 2235
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:20:00 | 1062.14 | 722.24 | 839982.26 | 814846.48 | 18.75 | 3481.353 | 991.473 | 527.131 | 24 | 187 | 32.9 | 49.1 | 31.8 | 50.9 | 0 | 0 | - | - | 35.1 | 46.8 | 269 | 261 | 56.3 | 56.3 | 64.3 | 23.6 | 41.1 | 2.51 | 8.6 | 20.8 | 56.4 | 66.6 | 24.2 | 43.5 | 2.63 | 8.7 | 20.1 | 21.1 | 22.7 | 33 | 2.51 | 1.15 | 2.69 | 1.17 | 269 | 261 | 2220 | 2220
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:25:00 | 1098.06 | 722.24 | 840017.82 | 814846.48 | 19.4 | 3444.078 | 1028.748 | 370.048 | 25 | 187 | 32.9 | 48.9 | 31.7 | 50.9 | 0 | 0 | - | - | 35.2 | 46.7 | 267 | 261 | 56.3 | 56.4 | 64.5 | 23.4 | 41.4 | 2.52 | 8.4 | 20.9 | 56.4 | 66.4 | 24.1 | 43.7 | 2.62 | 8.6 | 20.2 | 21 | 22.6 | 33.8 | 2.52 | 1.15 | 2.69 | 1.17 | 265 | 261 | 2175 | 2175
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:30:00 | 1114.62 | 722.24 | 840034.24 | 814846.48 | 20.04 | 3429.168 | 1043.658 | 23.987 | 25 | 187 | 33.3 | 48.4 | 31.8 | 50.6 | 0 | 0 | - | - | 35.4 | 46.5 | 263 | 260 | 56.3 | 56.4 | 64.5 | 23.3 | 41.4 | 2.53 | 8.5 | 20.7 | 56.4 | 66.2 | 24.1 | 43.7 | 2.61 | 8.5 | 20 | 20.8 | 22.4 | 33.6 | 2.5 | 1.14 | 2.68 | 1.16 | 263 | 260 | 2185 | 2185
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:35:00 | 1125.12 | 722.24 | 840044.9 | 814846.48 | 20.66 | 3421.713 | 1051.113 | 81.915 | 25 | 187 | 33.6 | 48 | 31.9 | 50.4 | 0 | 0 | - | - | 35.5 | 46.3 | 262 | 259 | 56.3 | 56.4 | 64.5 | 23.2 | 41.5 | 2.53 | 8.4 | 20.7 | 56.4 | 66.3 | 23.8 | 43.7 | 2.63 | 8.4 | 19.9 | 20.8 | 22.4 | 34.1 | 2.5 | 1.14 | 2.69 | 1.16 | 261 | 259 | 2157 | 2155
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:40:00 | 1139.12 | 722.24 | 840058.8 | 814846.48 | 21.28 | 3399.349 | 1073.478 | 112.715 | 26 | 187 | 33.5 | 47.9 | 31.9 | 50.3 | 0 | 0 | - | - | 35.7 | 46.1 | 260 | 258 | 56.3 | 56.4 | 64.5 | 23.2 | 41.4 | 2.53 | 8.6 | 20.8 | 55.9 | 66.3 | 23.8 | 43.6 | 2.62 | 8.6 | 20 | 20.7 | 22.2 | 34 | 2.52 | 1.13 | 2.69 | 1.15 | 260 | 258 | 2160 | 2160
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:45:00 | 1141.2 | 730.08 | 840060.78 | 814854.52 | 21.9 | 3421.713 | 1051.113 | -185.056 | 26 | 187 | 33.4 | 47.8 | 31.8 | 50.2 | 0 | 0 | - | - | 35.8 | 45.8 | 257 | 256 | 56.3 | 56.5 | 64.5 | 23.1 | 41.3 | 2.53 | 8.5 | 20.7 | 56.4 | 66.2 | 23.7 | 43.7 | 2.62 | 8.4 | 19.9 | 20.6 | 22.2 | 34.4 | 2.5 | 1.13 | 2.67 | 1.15 | 257 | 256 | 2140 | 2140
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:50:00 | 1154.84 | 731.88 | 840074.94 | 814856.12 | 22.52 | 3391.894 | 1080.933 | 345.832 | 26 | 187 | 33.4 | 47.7 | 31.8 | 50.1 | 0 | 0 | - | - | 35.9 | 45.7 | 257 | 256 | 56.8 | 56.5 | 64.6 | 22.9 | 41.3 | 2.5 | 8.7 | 21.3 | 56.5 | 66.4 | 23.6 | 43.5 | 2.61 | 8.7 | 20.2 | 20.3 | 21.9 | 33.5 | 2.52 | 1.11 | 2.68 | 1.14 | 257 | 256 | 2194 | 2194
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 10:55:00 | 1189.94 | 731.88 | 840109.94 | 814856.12 | 23.16 | 3362.078 | 1110.753 | 273.041 | 27 | 187 | 33.3 | 47.7 | 31.8 | 50.1 | 0 | 0 | - | - | 36 | 45.5 | 257 | 256 | 56.3 | 56.6 | 64.9 | 22.7 | 41.3 | 2.52 | 8.6 | 21.4 | 56.4 | 66.7 | 23.3 | 43.3 | 2.61 | 8.7 | 20.6 | 20.2 | 21.7 | 33.7 | 2.51 | 1.12 | 2.66 | 1.14 | 257 | 256 | 2175 | 2176
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:00:00 | 1215.24 | 731.88 | 840135.86 | 814856.12 | 23.81 | 3324.804 | 1148.024 | 689.205 | 27 | 187 | 33.2 | 47.6 | 31.7 | 50 | 0 | 0 | - | - | 36 | 45.4 | 257 | 256 | 56.8 | 56.6 | 64.8 | 22.6 | 41.3 | 2.5 | 8.6 | 21.4 | 56.9 | 66.5 | 23.2 | 43.3 | 2.61 | 8.6 | 20.3 | 19.9 | 21.7 | 33.4 | 2.53 | 1.08 | 2.71 | 1.11 | 257 | 256 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:05:00 | 1281.64 | 731.88 | 840202.56 | 814856.12 | 24.51 | 3265.164 | 1207.662 | 936.9 | 29 | 187 | 33.2 | 47.6 | 31.6 | 50 | 0 | 0 | - | - | 36.1 | 45.2 | 257 | 256 | 58.6 | 58.5 | 66.1 | 22.2 | 41.5 | 2.51 | 9.2 | 22.6 | 58.6 | 67.7 | 22.8 | 43.6 | 2.63 | 9 | 21.3 | 19.7 | 21.2 | 32.7 | 2.48 | 1.1 | 2.67 | 1.12 | 257 | 255 | 2238 | 2238
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:10:00 | 1342.1 | 731.88 | 840261.76 | 814856.12 | 25.11 | 3198.072 | 1274.754 | -14.798 | 30 | 187 | 33.1 | 47.5 | 31.6 | 49.9 | 0 | 0 | - | - | 36.1 | 45 | 257 | 255 | 57.4 | 57 | 65.3 | 22 | 41.5 | 2.52 | 8.5 | 21.7 | 57.1 | 67 | 22.7 | 43.4 | 2.62 | 8.6 | 20.6 | 19.7 | 21.2 | 33.4 | 2.51 | 1.1 | 2.68 | 1.12 | 257 | 255 | 2202 | 2202
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:15:00 | 1352.68 | 732.28 | 840272.66 | 814856.52 | 25.75 | 3190.618 | 1282.208 | 229.542 | 31 | 187 | 33.1 | 47.3 | 31.5 | 49.8 | 0 | 0 | - | - | 36.1 | 45 | 256 | 255 | 56.9 | 57 | 65 | 22.1 | 41.2 | 2.5 | 8.5 | 21.8 | 57.2 | 66.8 | 22.7 | 43.4 | 2.6 | 8.7 | 20.8 | 19.7 | 21.2 | 33.1 | 2.5 | 1.09 | 2.67 | 1.11 | 256 | 255 | 2215 | 2215
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:20:00 | 1373.12 | 732.28 | 840292.84 | 814856.52 | 26.38 | 3190.618 | 1282.208 | 67.259 | 31 | 187 | 33.1 | 47.2 | 31.4 | 49.8 | 0 | 0 | - | - | 36.1 | 44.8 | 255 | 255 | 56.4 | 56.4 | 65 | 21.9 | 41.1 | 2.5 | 8.5 | 21.6 | 56.2 | 66.5 | 22.7 | 43.2 | 2.59 | 8.7 | 20.6 | 19.6 | 21.1 | 33.4 | 2.5 | 1.09 | 2.66 | 1.11 | 255 | 255 | 2191 | 2193
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:25:00 | 1377.78 | 733.96 | 840297.64 | 814858.2 | 26.66 | 3183.164 | 1289.662 | 136.497 | 31 | 187 | 33 | 47.4 | 31.5 | 49.7 | 0 | 0 | - | - | 36.2 | 44.7 | 0 | 0 | 0 | 0 | 39.4 | 34.9 | 33.6 | 1.8 | 10.8 | 9.4 | 0 | 39.4 | 35.4 | 37.4 | 1.83 | 11.6 | 7.7 | 22.7 | 22.5 | 33.9 | 1.71 | 1.51 | 1.8 | 1.5 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:30:00 | 1420.74 | 733.96 | 840342.66 | 814858.2 | 26.84 | 3145.89 | 1326.936 | 899.793 | 32 | 187 | 32.9 | 47.8 | 31.5 | 50 | 0 | 0 | - | - | 36.2 | 44.6 | 0 | 0 | 0 | 0 | 31.2 | 43.5 | 35.3 | 1.57 | 17.9 | 6.1 | 0 | 31.2 | 45.3 | 34.6 | 1.52 | 20.1 | 6 | 23.8 | 23.7 | 33.3 | 1.54 | 1.57 | 1.55 | 1.55 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:35:00 | 1502.36 | 733.96 | 840423.4 | 814858.2 | 27 | 3056.43 | 1416.396 | 958.399 | 34 | 187 | 32.9 | 47.9 | 31.5 | 50.1 | 0 | 0 | - | - | 36.3 | 44.5 | 0 | 0 | 0 | 0 | 31.9 | 42.1 | 35.4 | 1.58 | 16.2 | 6.6 | 0 | 32.4 | 43.4 | 34.2 | 1.53 | 17.8 | 7.1 | 24.2 | 24.1 | 32.7 | 1.56 | 1.59 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:40:00 | 1597.22 | 733.96 | 840519.62 | 814858.2 | 27.16 | 2966.976 | 1505.85 | 1406.373 | 36 | 187 | 33 | 48 | 31.6 | 50.1 | 0 | 0 | - | - | 36.3 | 44.4 | 0 | 0 | 0 | 0 | 32.9 | 41.3 | 35.3 | 1.59 | 15 | 7.3 | 0 | 33.5 | 41.9 | 33.9 | 1.54 | 15.9 | 7.9 | 24.4 | 24.4 | 33.1 | 1.57 | 1.6 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:45:00 | 1715.32 | 733.96 | 840637.2 | 814858.2 | 27.32 | 2832.792 | 1640.034 | 1454.697 | 39 | 187 | 33.1 | 48 | 31.8 | 50 | 0 | 0 | - | - | 36.4 | 44.3 | 0 | 0 | 0 | 0 | 33.7 | 40.7 | 35.2 | 1.61 | 14.1 | 7.7 | 0 | 34.2 | 40.5 | 33.7 | 1.56 | 14.2 | 8.2 | 24.8 | 24.9 | 33.2 | 1.59 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:50:00 | 1842.52 | 733.96 | 840765.18 | 814858.2 | 27.48 | 2706.06 | 1766.766 | 1566.095 | 42 | 187 | 33.1 | 48.1 | 32.2 | 49.7 | 0 | 0 | - | - | 36.5 | 44.2 | 0 | 0 | 0 | 0 | 34.3 | 40.1 | 35.3 | 1.63 | 13 | 7.8 | 0 | 34.6 | 39.4 | 33.9 | 1.58 | 12.6 | 8.2 | 25.3 | 25.3 | 33.6 | 1.61 | 1.64 | 1.61 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 11:55:00 | 1965.56 | 733.96 | 840887.9 | 814858.2 | 27.62 | 2586.784 | 1886.042 | 885.099 | 45 | 187 | 33.2 | 48.2 | 32.9 | 48.9 | 0 | 0 | - | - | 36.7 | 44.2 | 0 | 0 | 0 | 0 | 34.5 | 39.8 | 35.3 | 1.65 | 12.3 | 7.6 | 0 | 34.9 | 38.4 | 34.1 | 1.6 | 11.1 | 8 | 25.7 | 25.7 | 34.7 | 1.63 | 1.66 | 1.63 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:00:00 | 2020.12 | 733.96 | 840940.14 | 814858.2 | 27.76 | 2534.604 | 1938.222 | 447.945 | 46 | 188 | 33.4 | 48.1 | 33 | 49 | 0 | 0 | - | - | 36.8 | 44 | 0 | 0 | 0 | 0 | 34.8 | 39.6 | 35.6 | 1.67 | 11.6 | 7.6 | 0 | 35.3 | 37.4 | 34.4 | 1.62 | 9.8 | 8 | 26.2 | 26.1 | 34 | 1.65 | 1.68 | 1.65 | 1.66 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:05:00 | 2045.42 | 733.96 | 840965.3 | 814858.2 | 27.9 | 2512.239 | 1960.587 | 195.787 | 46 | 188 | 33.7 | 47.9 | 32.6 | 49.6 | 0 | 0 | - | - | 36.9 | 43.9 | 0 | 0 | 0 | 0 | 35 | 39.1 | 35.7 | 1.69 | 10.8 | 7.4 | 0 | 35.4 | 36.9 | 34.6 | 1.63 | 8.9 | 7.7 | 26.5 | 26.5 | 34.1 | 1.66 | 1.69 | 1.66 | 1.68 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:10:00 | 2050.66 | 735.68 | 840970.24 | 814860.08 | 28.01 | 2504.784 | 1968.042 | -165.057 | 46 | 188 | 34 | 47.7 | 32.7 | 49.7 | 0 | 0 | - | - | 37 | 43.9 | 0 | 0 | 0 | 0 | 35.1 | 38.7 | 35.8 | 1.7 | 10.2 | 7.3 | 0 | 35.4 | 36.7 | 34.8 | 1.64 | 8.5 | 7.6 | 26.7 | 26.6 | 34.6 | 1.67 | 1.7 | 1.67 | 1.69 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:15:00 | 2050.66 | 746.68 | 840970.24 | 814870.98 | 28.13 | 2519.694 | 1953.132 | -86.312 | 46 | 188 | 34.1 | 47.7 | 32.7 | 49.8 | 0 | 0 | - | - | 37.1 | 43.8 | 0 | 0 | 0 | 0 | 34.9 | 38.6 | 35.6 | 1.7 | 9.9 | 7 | 0 | 35.2 | 36.6 | 34.9 | 1.65 | 8.2 | 7.2 | 26.8 | 26.7 | 34.4 | 1.67 | 1.71 | 1.68 | 1.69 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:20:00 | 2058.74 | 747.98 | 840978.4 | 814872.22 | 28.25 | 2512.239 | 1960.587 | 143.867 | 46 | 188 | 34.2 | 47.7 | 32.8 | 49.8 | 0 | 0 | - | - | 37.2 | 43.8 | 0 | 0 | 0 | 0 | 34.9 | 38.2 | 35.6 | 1.71 | 9.5 | 6.9 | 0 | 35.1 | 36.5 | 35.1 | 1.65 | 8.1 | 7 | 26.8 | 26.8 | 34.2 | 1.68 | 1.71 | 1.68 | 1.7 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:25:00 | 2069.3 | 747.98 | 840989.08 | 814872.22 | 28.37 | 2497.329 | 1975.497 | 122.964 | 46 | 188 | 34.2 | 47.8 | 32.8 | 50 | 0 | 0 | - | - | 37.3 | 43.8 | 0 | 0 | 0 | 0 | 35 | 37.9 | 35.8 | 1.71 | 9.1 | 7 | 0 | 35.1 | 36.6 | 35.4 | 1.65 | 8.1 | 6.9 | 26.9 | 26.9 | 34.4 | 1.68 | 1.71 | 1.68 | 1.7 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:30:00 | 2071.12 | 755.46 | 840990.7 | 814880.06 | 28.48 | 2497.329 | 1975.497 | -340.948 | 46 | 188 | 34.2 | 47.9 | 32.8 | 50 | 0 | 0 | - | - | 37.3 | 43.8 | 0 | 0 | 0 | 0 | 35.2 | 37.9 | 36 | 1.71 | 9 | 7.1 | 0 | 35.1 | 36.6 | 35.4 | 1.66 | 8.1 | 6.9 | 27 | 26.9 | 34.3 | 1.68 | 1.72 | 1.68 | 1.7 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:35:00 | 2071.12 | 784.96 | 840990.7 | 814909.52 | 28.6 | 2519.694 | 1953.132 | -332.088 | 46 | 188 | 34.1 | 48.1 | 32.8 | 50.1 | 0 | 0 | - | - | 37.3 | 43.8 | 0 | 0 | 0 | 0 | 35.2 | 37.8 | 36.1 | 1.71 | 8.9 | 7 | 0 | 35.1 | 36.5 | 35.7 | 1.66 | 7.9 | 6.8 | 27 | 27 | 34.2 | 1.68 | 1.72 | 1.69 | 1.7 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:40:00 | 2071.12 | 825.18 | 840990.7 | 814949.8 | 28.73 | 2549.514 | 1923.312 | -396.35 | 45 | 188 | 34 | 48.3 | 32.8 | 50.2 | 0 | 0 | - | - | 37.3 | 43.8 | 0 | 0 | 0 | 0 | 35.2 | 37.8 | 36.1 | 1.72 | 8.9 | 7 | 0 | 35.1 | 36.6 | 35.9 | 1.66 | 7.9 | 6.7 | 27.1 | 27.1 | 34.5 | 1.69 | 1.72 | 1.69 | 1.7 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:45:00 | 2078.64 | 834.14 | 840999.14 | 814958.38 | 28.86 | 2579.33 | 1893.496 | 359.652 | 45 | 188 | 34 | 48.4 | 32.8 | 50.3 | 0 | 0 | - | - | 37.3 | 43.9 | 0 | 0 | 0 | 0 | 35.3 | 37.8 | 36.2 | 1.71 | 8.8 | 7.1 | 0 | 35.1 | 36.6 | 35.9 | 1.66 | 7.9 | 6.8 | 27.1 | 27.1 | 34.1 | 1.69 | 1.72 | 1.69 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:50:00 | 2088.58 | 846.76 | 841008.16 | 814971.88 | 28.99 | 2571.876 | 1900.95 | -432.284 | 45 | 188 | 34 | 48.5 | 32.8 | 50.4 | 0 | 0 | - | - | 37.3 | 44 | 0 | 0 | 0 | 0 | 35.3 | 37.5 | 36.3 | 1.72 | 8.4 | 7 | 0 | 35.1 | 36.6 | 36.1 | 1.66 | 7.8 | 6.7 | 27.2 | 27.1 | 34.4 | 1.69 | 1.72 | 1.69 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 12:55:00 | 2090.44 | 867.62 | 841010.32 | 814991.86 | 29.12 | 2594.238 | 1878.588 | 146.586 | 44 | 188 | 33.9 | 48.7 | 32.8 | 50.4 | 0 | 0 | - | - | 37.2 | 44 | 0 | 0 | 0 | 0 | 35.1 | 37.4 | 36 | 1.72 | 8.3 | 6.8 | 0 | 34.9 | 36.4 | 36.1 | 1.67 | 7.6 | 6.5 | 27.2 | 27.1 | 34.6 | 1.69 | 1.72 | 1.69 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:00:00 | 2093.12 | 878.86 | 841012.7 | 815003.78 | 29.24 | 2601.693 | 1871.133 | -339.013 | 44 | 188 | 33.9 | 48.7 | 32.8 | 50.5 | 0 | 0 | - | - | 37.2 | 44.1 | 0 | 0 | 0 | 0 | 34.9 | 37.4 | 35.7 | 1.72 | 8.3 | 6.5 | 0 | 34.6 | 36.2 | 35.9 | 1.67 | 7.5 | 6.2 | 27.2 | 27.2 | 34.8 | 1.69 | 1.73 | 1.69 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:05:00 | 2095.8 | 888.5 | 841015.68 | 815012.74 | 29.36 | 2616.603 | 1856.223 | 350.74 | 44 | 188 | 33.9 | 48.8 | 32.8 | 50.6 | 0 | 0 | - | - | 37.1 | 44.2 | 0 | 0 | 0 | 0 | 34.6 | 37.3 | 35.6 | 1.72 | 8.2 | 6.2 | 0 | 34.6 | 36.1 | 35.8 | 1.67 | 7.3 | 6 | 27.2 | 27.2 | 34.6 | 1.69 | 1.73 | 1.7 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:10:00 | 2130.42 | 888.5 | 841050.38 | 815012.74 | 29.49 | 2579.33 | 1893.496 | 330.957 | 45 | 188 | 33.9 | 48.8 | 32.8 | 50.6 | 0 | 0 | - | - | 37.1 | 44.3 | 0 | 0 | 0 | 0 | 34.8 | 37.1 | 35.9 | 1.72 | 8 | 6.5 | 0 | 34.6 | 36.1 | 35.9 | 1.67 | 7.3 | 6.2 | 27.2 | 27.2 | 34.6 | 1.69 | 1.73 | 1.7 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:15:00 | 2165.26 | 888.5 | 841085 | 815012.74 | 29.63 | 2542.059 | 1930.767 | 100.473 | 45 | 188 | 33.8 | 49 | 32.8 | 50.7 | 0 | 0 | - | - | 37 | 44.4 | 0 | 0 | 0 | 0 | 35.1 | 36.9 | 36.1 | 1.73 | 7.7 | 6.6 | 0 | 34.7 | 36.1 | 36 | 1.67 | 7.2 | 6.2 | 27.3 | 27.3 | 33.9 | 1.7 | 1.73 | 1.7 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:20:00 | 2165.9 | 899.52 | 841085.48 | 815024.36 | 29.76 | 2542.059 | 1930.767 | -518.09 | 45 | 188 | 33.8 | 49 | 32.8 | 50.8 | 0 | 0 | - | - | 37 | 44.5 | 0 | 0 | 0 | 0 | 35.1 | 36.7 | 36.1 | 1.73 | 7.4 | 6.5 | 0 | 34.6 | 36.1 | 36.1 | 1.68 | 7.1 | 6 | 27.4 | 27.4 | 33.8 | 1.7 | 1.73 | 1.71 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:25:00 | 2165.9 | 954.28 | 841085.48 | 815078.66 | 29.9 | 2594.238 | 1878.588 | -130.74 | 44 | 188 | 33.7 | 49.2 | 32.8 | 50.9 | 0 | 0 | - | - | 37 | 44.5 | 0 | 0 | 0 | 0 | 35 | 36.4 | 35.9 | 1.73 | 7.1 | 6.5 | 0 | 34.5 | 36 | 36.2 | 1.68 | 6.9 | 5.9 | 27.4 | 27.4 | 34.3 | 1.7 | 1.74 | 1.71 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:30:00 | 2168.44 | 955.98 | 841088.06 | 815080.26 | 30.04 | 2616.603 | 1856.223 | -25.796 | 44 | 188 | 33.7 | 49.2 | 32.8 | 50.9 | 0 | 0 | - | - | 36.9 | 44.7 | 0 | 0 | 0 | 0 | 35 | 36.2 | 35.7 | 1.73 | 6.9 | 6.4 | 0 | 34.4 | 35.9 | 36.1 | 1.68 | 6.9 | 5.7 | 27.5 | 27.4 | 34.1 | 1.7 | 1.74 | 1.71 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:35:00 | 2172.72 | 957.2 | 841092.3 | 815081.92 | 30.17 | 2609.148 | 1863.678 | -100.428 | 44 | 188 | 33.7 | 49.3 | 32.7 | 51 | 0 | 0 | - | - | 36.8 | 44.8 | 0 | 0 | 0 | 0 | 34.9 | 36.1 | 35.6 | 1.73 | 6.7 | 6.3 | 0 | 34.4 | 35.8 | 36.1 | 1.68 | 6.7 | 5.6 | 27.5 | 27.5 | 33.5 | 1.7 | 1.74 | 1.71 | 1.73 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:40:00 | 2172.72 | 981.24 | 841092.3 | 815105.76 | 30.3 | 2616.603 | 1856.223 | -639.107 | 43 | 188 | 33.6 | 49.4 | 32.6 | 51.2 | 0 | 0 | - | - | 36.8 | 44.8 | 0 | 0 | 0 | 0 | 34.9 | 35.9 | 35.6 | 1.73 | 6.5 | 6.3 | 0 | 34.4 | 35.7 | 36 | 1.68 | 6.6 | 5.7 | 27.5 | 27.5 | 33.4 | 1.7 | 1.74 | 1.71 | 1.73 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:45:00 | 2172.72 | 1043.56 | 841092.3 | 815169.64 | 30.45 | 2698.606 | 1774.22 | -909.253 | 42 | 188 | 33.6 | 49.6 | 32.6 | 51.3 | 0 | 0 | - | - | 36.7 | 45 | 0 | 0 | 0 | 0 | 34.9 | 35.9 | 35.6 | 1.74 | 6.4 | 6.2 | 0 | 34.2 | 35.8 | 35.9 | 1.68 | 6.7 | 5.4 | 27.5 | 27.5 | 33.1 | 1.7 | 1.74 | 1.71 | 1.73 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:50:00 | 2172.72 | 1113.8 | 841092.3 | 815238.58 | 30.6 | 2750.787 | 1722.039 | -527.353 | 40 | 188 | 33.5 | 49.8 | 32.5 | 51.5 | 0 | 0 | - | - | 36.6 | 45.2 | 0 | 0 | 0 | 0 | 34.7 | 35.7 | 35.4 | 1.73 | 6.3 | 6.1 | 0 | 34.1 | 35.8 | 35.9 | 1.68 | 6.7 | 5.3 | 27.5 | 27.5 | 32.6 | 1.7 | 1.74 | 1.71 | 1.73 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 13:55:00 | 2172.72 | 1132.62 | 841092.3 | 815257 | 30.74 | 2788.062 | 1684.764 | -141.503 | 40 | 188 | 33.3 | 50 | 32.4 | 51.7 | 0 | 0 | - | - | 36.5 | 45.3 | 0 | 0 | 0 | 0 | 34.5 | 35.6 | 35.2 | 1.73 | 6.3 | 5.9 | 0 | 33.9 | 35.8 | 35.7 | 1.68 | 6.7 | 5.2 | 27.5 | 27.5 | 32.4 | 1.7 | 1.74 | 1.71 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:00:00 | 2172.72 | 1162.12 | 841092.3 | 815287.82 | 30.89 | 2802.972 | 1669.854 | -446.042 | 39 | 188 | 33.2 | 50.2 | 32.2 | 52 | 0 | 0 | - | - | 36.3 | 45.5 | 0 | 0 | 0 | 0 | 34.4 | 35.6 | 35.1 | 1.73 | 6.2 | 5.8 | 0 | 33.7 | 35.7 | 35.6 | 1.68 | 6.7 | 5 | 27.5 | 27.5 | 32.1 | 1.7 | 1.74 | 1.71 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:05:00 | 2172.72 | 1188.2 | 841092.3 | 815313.16 | 31.04 | 2847.701 | 1625.125 | -453.462 | 38 | 188 | 33 | 50.5 | 32.1 | 52.2 | 0 | 0 | - | - | 36.2 | 45.7 | 0 | 0 | 0 | 0 | 34.1 | 35.1 | 34.6 | 1.73 | 5.7 | 5.6 | 0 | 33.1 | 35.2 | 34.9 | 1.68 | 6.2 | 4.4 | 27.4 | 27.4 | 27.8 | 1.69 | 1.73 | 1.71 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:10:00 | 2172.72 | 1219.06 | 841092.3 | 815344 | 31.19 | 2877.52 | 1595.306 | -362.054 | 38 | 188 | 32.7 | 50.8 | 31.9 | 52.5 | 0 | 0 | - | - | 35.8 | 46 | 0 | 0 | 0 | 0 | 32.9 | 33.6 | 32.9 | 1.72 | 4.4 | 4.5 | 0 | 31.7 | 33.9 | 33.4 | 1.67 | 4.8 | 3.1 | 27.4 | 27.4 | 27.9 | 1.69 | 1.73 | 1.7 | 1.72 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:15:00 | 2182.9 | 1227.12 | 841102.74 | 815351.36 | 31.33 | 2877.52 | 1595.306 | 270.936 | 38 | 188 | 32.5 | 51.2 | 31.6 | 52.9 | 0 | 0 | - | - | 35.3 | 46.6 | 0 | 0 | 0 | 0 | 31.8 | 32.6 | 31.7 | 1.71 | 3.7 | 3.7 | 0 | 31.1 | 32.9 | 32.2 | 1.67 | 4 | 2.6 | 27.4 | 27.4 | 28 | 1.68 | 1.72 | 1.69 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:20:00 | 2202.1 | 1227.12 | 841121.8 | 815351.36 | 31.47 | 2862.611 | 1610.215 | 82.337 | 38 | 188 | 32.1 | 51.6 | 31.2 | 53.4 | 0 | 0 | - | - | 34.6 | 47.3 | 0 | 0 | 0 | 0 | 30.3 | 31.4 | 30.7 | 1.7 | 2.6 | 2.4 | 0 | 30.1 | 31.7 | 30.9 | 1.65 | 3 | 1.9 | 27.4 | 27.4 | 27.7 | 1.67 | 1.71 | 1.68 | 1.71 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:25:00 | 2210.36 | 1227.36 | 841130.3 | 815351.6 | 31.6 | 2855.156 | 1617.67 | 226.776 | 38 | 188 | 31.7 | 52.2 | 30.9 | 53.9 | 0 | 0 | - | - | 34.1 | 48 | 0 | 0 | 0 | 0 | 29.4 | 30.6 | 29.8 | 1.69 | 1.9 | 1.8 | 0 | 29.3 | 30.7 | 30.1 | 1.65 | 2.1 | 1.3 | 27.4 | 27.4 | 27.4 | 1.66 | 1.7 | 1.67 | 1.7 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:30:00 | 2256.08 | 1227.36 | 841176.12 | 815351.6 | 31.74 | 2802.972 | 1669.854 | 967.711 | 40 | 188 | 31.3 | 52.8 | 30.6 | 54.4 | 0 | 0 | - | - | 33.6 | 48.6 | 0 | 0 | 0 | 0 | 28.7 | 29.9 | 29.1 | 1.68 | 1.4 | 1.3 | 0 | 28.8 | 30.1 | 29.3 | 1.63 | 1.6 | 1.2 | 27.5 | 27.4 | 27.2 | 1.65 | 1.7 | 1.66 | 1.7 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:35:00 | 2340.1 | 1227.36 | 841261.58 | 815351.6 | 32.23 | 2713.514 | 1759.312 | 916.285 | 41 | 188 | 31 | 53.2 | 30.3 | 54.8 | 0 | 0 | - | - | 33.1 | 49.2 | 288 | 263 | 57 | 0 | 64.9 | 27.1 | 38.4 | 2.52 | 14.4 | 21.1 | 57.2 | 63.3 | 27.2 | 40 | 2.61 | 12.4 | 17.1 | 23.2 | 26.1 | 28.1 | 2.6 | 1.1 | 2.79 | 1.16 | 297 | 261 | 3187 | 3187
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:40:00 | 2410.34 | 1227.36 | 841331.6 | 815351.6 | 33.15 | 2638.968 | 1833.858 | 818.655 | 43 | 188 | 30.7 | 53.4 | 30 | 55 | 0 | 0 | - | - | 32.7 | 49.7 | 295 | 259 | 58.1 | 58.2 | 66.5 | 24.2 | 39.9 | 2.5 | 9.7 | 23.1 | 58.3 | 67.9 | 24.4 | 42.6 | 2.65 | 9.6 | 21.1 | 21.3 | 23.4 | 28.6 | 2.49 | 1.14 | 2.71 | 1.15 | 295 | 259 | 2838 | 2838
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:45:00 | 2466.82 | 1227.36 | 841386.74 | 815351.6 | 33.87 | 2594.238 | 1878.588 | 254.566 | 44 | 188 | 30.6 | 53.5 | 29.8 | 55.2 | 0 | 0 | - | - | 32.4 | 50.1 | 288 | 256 | 52.9 | 53 | 62.9 | 23.8 | 38.9 | 2.42 | 8.4 | 20.9 | 52.9 | 65.1 | 24.2 | 41.5 | 2.56 | 8.4 | 19.8 | 21.4 | 23.3 | 28.8 | 2.42 | 1.16 | 2.63 | 1.17 | 288 | 256 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:50:00 | 2490.16 | 1227.36 | 841410.36 | 815351.6 | 34.54 | 2571.876 | 1900.95 | 381.787 | 45 | 188 | 30.3 | 53.6 | 29.6 | 55.3 | 0 | 0 | - | - | 32.1 | 50.5 | 288 | 256 | 52.9 | 53.1 | 62.2 | 23.8 | 38.6 | 2.41 | 8.6 | 20.2 | 52.9 | 64.6 | 24.2 | 41.4 | 2.56 | 8.6 | 19.3 | 21.4 | 23.2 | 29.8 | 2.41 | 1.16 | 2.62 | 1.17 | 288 | 256 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 14:55:00 | 2529.1 | 1227.36 | 841449.2 | 815351.6 | 35.21 | 2527.149 | 1945.677 | 332.852 | 46 | 188 | 30.2 | 53.7 | 29.3 | 55.4 | 0 | 0 | - | - | 31.9 | 50.7 | 288 | 256 | 52.9 | 53.1 | 62.1 | 23.7 | 38.6 | 2.41 | 8.5 | 20.1 | 52.9 | 64.5 | 24.2 | 41.4 | 2.55 | 8.6 | 19.2 | 21.3 | 23.2 | 30.2 | 2.41 | 1.16 | 2.62 | 1.17 | 288 | 256 | 2386 | 2386
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:00:00 | 2535.48 | 1237.1 | 841455.06 | 815361.78 | 35.86 | 2527.149 | 1945.677 | -216.332 | 46 | 188 | 29.9 | 53.9 | 29.2 | 55.5 | 0 | 0 | - | - | 31.7 | 50.9 | 286 | 256 | 52.4 | 52.6 | 61.9 | 23.7 | 38.2 | 2.39 | 8.5 | 20.2 | 52.4 | 64.4 | 24.1 | 41.4 | 2.53 | 8.6 | 19.5 | 21.2 | 22.9 | 30.7 | 2.39 | 1.15 | 2.6 | 1.16 | 286 | 256 | 2356 | 2356
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:05:00 | 2542.44 | 1242.5 | 841462.66 | 815366.74 | 36.51 | 2527.149 | 1945.677 | 347.684 | 46 | 188 | 29.7 | 54.1 | 29 | 55.5 | 0 | 0 | - | - | 31.5 | 51.1 | 284 | 256 | 52.4 | 52.1 | 61.8 | 23.4 | 38.2 | 2.39 | 8.5 | 20.2 | 52.4 | 64.2 | 23.8 | 41.4 | 2.53 | 8.6 | 19.3 | 21 | 22.7 | 30.5 | 2.38 | 1.14 | 2.6 | 1.16 | 283 | 256 | 2370 | 2370
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:10:00 | 2551.08 | 1246.8 | 841470.74 | 815371.04 | 37.14 | 2527.149 | 1945.677 | 88.117 | 46 | 188 | 29.5 | 54.2 | 28.9 | 55.6 | 0 | 0 | - | - | 31.4 | 51.3 | 283 | 256 | 52.4 | 52 | 61.6 | 23.2 | 38.1 | 2.38 | 8.5 | 20.1 | 52.4 | 64.2 | 23.7 | 41.4 | 2.52 | 8.6 | 19.5 | 20.7 | 22.6 | 30.1 | 2.38 | 1.14 | 2.58 | 1.15 | 283 | 256 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:15:00 | 2569.18 | 1246.8 | 841489.62 | 815371.04 | 37.8 | 2504.784 | 1968.042 | 389.74 | 46 | 188 | 29.3 | 54.3 | 28.7 | 55.7 | 0 | 0 | - | - | 31.2 | 51.3 | 281 | 256 | 52.4 | 52.1 | 61.8 | 23.1 | 38.1 | 2.38 | 8.6 | 20.4 | 52.4 | 64.1 | 23.4 | 41.4 | 2.52 | 8.5 | 19.4 | 20.6 | 22.3 | 30.2 | 2.38 | 1.13 | 2.57 | 1.14 | 281 | 256 | 2386 | 2386
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:20:00 | 2584.92 | 1246.8 | 841504.88 | 815371.04 | 38.43 | 2482.419 | 1990.407 | 190.438 | 47 | 188 | 29 | 54.5 | 28.4 | 55.8 | 0 | 0 | - | - | 31.1 | 51.4 | 277 | 254 | 51.4 | 51.8 | 61.4 | 22.8 | 37.7 | 2.36 | 8.6 | 20.4 | 51.8 | 63.9 | 23.3 | 41.1 | 2.5 | 8.6 | 19.5 | 20.4 | 22.2 | 30.3 | 2.36 | 1.12 | 2.57 | 1.14 | 277 | 254 | 2379 | 2379
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:25:00 | 2599.16 | 1246.8 | 841519.24 | 815371.04 | 39.07 | 2482.419 | 1990.407 | 128.491 | 47 | 188 | 28.8 | 54.7 | 28.3 | 55.9 | 0 | 0 | - | - | 30.9 | 51.4 | 277 | 253 | 51.4 | 51.3 | 61.1 | 22.7 | 37.6 | 2.35 | 8.6 | 20.2 | 51.8 | 63.7 | 23.2 | 40.9 | 2.5 | 8.5 | 19.4 | 20.2 | 22.1 | 30.6 | 2.34 | 1.12 | 2.56 | 1.13 | 277 | 253 | 2359 | 2359
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:30:00 | 2617.42 | 1246.8 | 841537.28 | 815371.04 | 39.75 | 2460.054 | 2012.772 | 155.131 | 47 | 188 | 28.5 | 54.9 | 28.1 | 56 | 0 | 0 | - | - | 30.8 | 51.5 | 276 | 253 | 50.9 | 50.8 | 61 | 22.5 | 37.6 | 2.34 | 8.6 | 20.3 | 51.2 | 63.5 | 22.9 | 40.8 | 2.48 | 8.6 | 19.5 | 20.1 | 21.8 | 30.1 | 2.34 | 1.11 | 2.54 | 1.12 | 276 | 253 | 2398 | 2397
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:35:00 | 2620.62 | 1249.9 | 841540.2 | 815374.38 | 40.39 | 2452.599 | 2020.227 | -115.869 | 47 | 188 | 28.3 | 55 | 27.8 | 56.2 | 0 | 0 | - | - | 30.6 | 51.7 | 275 | 253 | 51.4 | 51.4 | 60.9 | 22.2 | 37.4 | 2.33 | 8.5 | 20.2 | 51.2 | 63.5 | 22.7 | 40.8 | 2.48 | 8.5 | 19.5 | 19.8 | 21.7 | 29.4 | 2.33 | 1.1 | 2.54 | 1.12 | 275 | 253 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:40:00 | 2620.62 | 1256.98 | 841540.2 | 815381.36 | 41.02 | 2467.509 | 2005.317 | -66.539 | 47 | 188 | 28 | 55.2 | 27.5 | 56.4 | 0 | 0 | - | - | 30.5 | 51.8 | 274 | 253 | 50.9 | 50.9 | 60.7 | 22.1 | 37.6 | 2.32 | 8.5 | 20.4 | 51.2 | 63.4 | 22.6 | 40.7 | 2.47 | 8.5 | 19.5 | 19.7 | 21.4 | 28.4 | 2.33 | 1.1 | 2.52 | 1.11 | 274 | 253 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:45:00 | 2620.86 | 1260.34 | 841540.44 | 815384.58 | 41.65 | 2467.509 | 2005.317 | 24.468 | 47 | 188 | 27.8 | 55.2 | 27.4 | 56.4 | 0 | 0 | - | - | 30.4 | 51.8 | 271 | 253 | 50.9 | 50.4 | 60.9 | 21.8 | 37.9 | 2.34 | 8.5 | 20.2 | 50.7 | 63.3 | 22.3 | 40.4 | 2.46 | 8.5 | 19.6 | 19.5 | 21.2 | 27.4 | 2.34 | 1.09 | 2.52 | 1.11 | 270 | 253 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:50:00 | 2621.34 | 1261.74 | 841541.02 | 815385.98 | 42.28 | 2467.509 | 2005.317 | 4.632 | 47 | 188 | 27.8 | 55.1 | 27.2 | 56.3 | 0 | 0 | - | - | 30.3 | 51.8 | 270 | 253 | 51.4 | 51.4 | 61.1 | 21.6 | 37.7 | 2.32 | 8.5 | 20.7 | 51.2 | 63.7 | 22.2 | 40.5 | 2.47 | 8.5 | 19.9 | 19.3 | 21.1 | 27.1 | 2.33 | 1.08 | 2.54 | 1.1 | 270 | 253 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 15:55:00 | 2622.44 | 1264.28 | 841542.02 | 815388.52 | 42.91 | 2467.509 | 2005.317 | -134.539 | 47 | 188 | 27.8 | 55 | 27.2 | 56.3 | 0 | 0 | - | - | 30.2 | 51.8 | 270 | 252 | 51.4 | 51.3 | 60.9 | 21.4 | 37.4 | 2.29 | 8.6 | 20.9 | 51.3 | 63.5 | 21.9 | 40.4 | 2.45 | 8.5 | 19.9 | 19.2 | 20.8 | 26.6 | 2.29 | 1.07 | 2.51 | 1.09 | 270 | 252 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:00:00 | 2622.76 | 1268.62 | 841542.5 | 815392.86 | 43.54 | 2482.419 | 1990.407 | 107.507 | 47 | 188 | 27.6 | 54.9 | 27 | 56.3 | 0 | 0 | - | - | 30.1 | 51.7 | 270 | 250 | 51.5 | 51.3 | 60.8 | 21.2 | 37.6 | 2.3 | 8.5 | 20.8 | 51.3 | 63.5 | 21.7 | 40.4 | 2.46 | 8.5 | 19.9 | 18.9 | 20.6 | 26.4 | 2.28 | 1.07 | 2.51 | 1.09 | 270 | 250 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:05:00 | 2631.54 | 1270.1 | 841551.6 | 815394.34 | 44.16 | 2467.509 | 2005.317 | 463.853 | 47 | 188 | 27.3 | 55.3 | 26.7 | 56.5 | 0 | 0 | - | - | 30 | 51.7 | 269 | 248 | 51 | 50.9 | 60.5 | 20.9 | 37.4 | 2.29 | 8.5 | 20.7 | 50.8 | 63.4 | 21.6 | 40.1 | 2.44 | 8.5 | 20 | 18.7 | 20.4 | 26.2 | 2.28 | 1.06 | 2.49 | 1.08 | 267 | 248 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:10:00 | 2668.8 | 1270.1 | 841588.74 | 815394.34 | 44.8 | 2430.234 | 2042.592 | 397.216 | 48 | 188 | 27.2 | 55.2 | 26.5 | 56.6 | 0 | 0 | - | - | 29.8 | 51.6 | 268 | 248 | 50.5 | 50.9 | 60.4 | 20.8 | 37.1 | 2.28 | 8.5 | 20.7 | 50.8 | 63.4 | 21.3 | 40 | 2.43 | 8.6 | 20.1 | 18.6 | 20.3 | 26.3 | 2.29 | 1.06 | 2.49 | 1.07 | 268 | 248 | 2400 | 2400
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:15:00 | 2699.94 | 1270.1 | 841620.56 | 815394.34 | 45.35 | 2392.962 | 2079.864 | 300.377 | 49 | 188 | 27.1 | 55 | 26.5 | 56.4 | 0 | 0 | - | - | 29.7 | 51.8 | 0 | 0 | 51.1 | 51.2 | 59.7 | 20.6 | 36.6 | 2.1 | 35 | 23.6 | 50.7 | 62.4 | 21.2 | 39.2 | 2.29 | 29.9 | 21.8 | 20 | 20.2 | 26.1 | 1.72 | 0.78 | 1.88 | 0.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:20:00 | 2725.22 | 1270.1 | 841645.24 | 815394.34 | 45.49 | 2378.054 | 2094.772 | 321.85 | 49 | 188 | 26.9 | 55.6 | 26.5 | 56.7 | 0 | 0 | - | - | 29.5 | 51.8 | 0 | 0 | 0 | 0 | 31.8 | 31.6 | 26.4 | 1.59 | 7.5 | 6.4 | 0 | 27.8 | 35.1 | 30.7 | 1.56 | 11.3 | 2 | 22.7 | 22.6 | 25.7 | 1.55 | 1.51 | 1.56 | 1.5 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:25:00 | 2750.02 | 1270.1 | 841669.68 | 815394.34 | 45.64 | 2348.235 | 2124.591 | 136.677 | 50 | 188 | 26.8 | 56 | 26.5 | 56.9 | 0 | 0 | - | - | 29.3 | 52 | 0 | 0 | 0 | 0 | 27.2 | 34.8 | 27 | 1.56 | 9.6 | 2.6 | 0 | 26.5 | 37.7 | 29 | 1.5 | 12.8 | 1.8 | 23.5 | 23.4 | 25.3 | 1.53 | 1.55 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:30:00 | 2764.8 | 1270.1 | 841684.48 | 815394.34 | 45.79 | 2333.325 | 2139.501 | 196.75 | 50 | 188 | 26.7 | 56.4 | 26.5 | 57.1 | 0 | 0 | - | - | 29.1 | 52.2 | 0 | 0 | 0 | 0 | 26.5 | 34.4 | 27.2 | 1.57 | 8.8 | 1.5 | 0 | 26.5 | 35.4 | 27.9 | 1.52 | 10.1 | 1.4 | 23.8 | 23.8 | 25.2 | 1.54 | 1.57 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:35:00 | 2783.98 | 1270.1 | 841703.82 | 815394.34 | 45.93 | 2310.96 | 2161.866 | 261.199 | 51 | 188 | 26.6 | 56.7 | 26.5 | 57.2 | 0 | 0 | - | - | 28.8 | 52.5 | 0 | 0 | 0 | 0 | 26.3 | 33.1 | 27 | 1.58 | 7.2 | 1.1 | 0 | 26.4 | 33.4 | 27.2 | 1.53 | 7.9 | 1.2 | 24 | 24 | 25.1 | 1.55 | 1.58 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:40:00 | 2804.26 | 1270.1 | 841723.96 | 815394.34 | 46.06 | 2288.595 | 2184.231 | 253.237 | 51 | 188 | 26.5 | 56.9 | 26.4 | 57.4 | 0 | 0 | - | - | 28.6 | 52.7 | 0 | 0 | 0 | 0 | 26.4 | 31.6 | 26.8 | 1.58 | 5.5 | 1.1 | 0 | 26.3 | 31.8 | 26.8 | 1.53 | 6.1 | 1 | 24.2 | 24.2 | 25.2 | 1.55 | 1.59 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:45:00 | 2825.22 | 1270.1 | 841745.04 | 815394.34 | 46.19 | 2281.14 | 2191.686 | 242.134 | 52 | 188 | 26.5 | 57 | 26.4 | 57.5 | 0 | 0 | - | - | 28.5 | 52.9 | 0 | 0 | 0 | 0 | 26.5 | 30.4 | 26.7 | 1.59 | 4.3 | 1.1 | 0 | 26.4 | 30.4 | 26.7 | 1.54 | 4.6 | 1 | 24.3 | 24.3 | 25.2 | 1.56 | 1.59 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:50:00 | 2839.38 | 1270.12 | 841759.04 | 815394.36 | 46.31 | 2258.778 | 2214.051 | 95.858 | 52 | 188 | 26.4 | 57.2 | 26.4 | 57.6 | 0 | 0 | - | - | 28.3 | 53.1 | 0 | 0 | 0 | 0 | 26.4 | 29.7 | 26.6 | 1.59 | 3.4 | 0.9 | 0 | 26.3 | 29.4 | 26.4 | 1.54 | 3.6 | 0.7 | 24.4 | 24.4 | 24.9 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 16:55:00 | 2841.22 | 1276.22 | 841760.8 | 815401.2 | 46.43 | 2258.778 | 2214.051 | -256.245 | 52 | 188 | 26.4 | 57.3 | 26.4 | 57.6 | 0 | 0 | - | - | 28.2 | 53.2 | 0 | 0 | 0 | 0 | 26.3 | 28.9 | 26.3 | 1.59 | 2.6 | 0.8 | 0 | 26.2 | 28.7 | 26.2 | 1.54 | 2.7 | 0.5 | 24.4 | 24.4 | 24.8 | 1.56 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:00:00 | 2841.22 | 1308.7 | 841760.8 | 815433.58 | 46.55 | 2288.595 | 2184.231 | -441.746 | 51 | 188 | 26.3 | 57.4 | 26.3 | 57.8 | 0 | 0 | - | - | 28 | 53.4 | 0 | 0 | 0 | 0 | 26.4 | 28.3 | 26.2 | 1.59 | 2.1 | 0.9 | 0 | 26.1 | 28.2 | 25.9 | 1.54 | 2.2 | 0.4 | 24.5 | 24.4 | 24.8 | 1.56 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:05:00 | 2841.22 | 1324.7 | 841760.8 | 815448.94 | 46.66 | 2310.96 | 2161.866 | 21.304 | 51 | 188 | 26.3 | 57.5 | 26.3 | 57.8 | 0 | 0 | - | - | 27.9 | 53.6 | 0 | 0 | 0 | 0 | 26.3 | 28.1 | 26.1 | 1.59 | 1.7 | 0.8 | 0 | 25.9 | 27.7 | 25.9 | 1.54 | 1.8 | 0.3 | 24.5 | 24.5 | 25 | 1.56 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:10:00 | 2841.88 | 1326.28 | 841761.46 | 815450.58 | 46.77 | 2310.96 | 2161.866 | -50.941 | 51 | 188 | 26.2 | 57.6 | 26.3 | 57.8 | 0 | 0 | - | - | 27.8 | 53.8 | 0 | 0 | 0 | 0 | 26.2 | 27.9 | 26.1 | 1.59 | 1.7 | 0.7 | 0 | 25.9 | 27.6 | 25.9 | 1.54 | 1.7 | 0.4 | 24.5 | 24.5 | 24.9 | 1.56 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:15:00 | 2841.9 | 1331.3 | 841761.48 | 815455.76 | 46.87 | 2310.96 | 2161.866 | -139.511 | 50 | 188 | 26.2 | 57.6 | 26.3 | 57.8 | 0 | 0 | - | - | 27.7 | 53.9 | 0 | 0 | 0 | 0 | 26.2 | 27.7 | 26 | 1.59 | 1.5 | 0.7 | 0 | 25.8 | 27.3 | 25.9 | 1.54 | 1.5 | 0.3 | 24.5 | 24.5 | 24.8 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:20:00 | 2841.9 | 1344.32 | 841761.48 | 815468.86 | 46.97 | 2333.325 | 2139.501 | -195.93 | 50 | 188 | 26.2 | 57.8 | 26.2 | 57.9 | 0 | 0 | - | - | 27.6 | 54 | 0 | 0 | 0 | 0 | 26.1 | 27.7 | 25.9 | 1.59 | 1.5 | 0.6 | 0 | 25.7 | 27.2 | 25.8 | 1.54 | 1.3 | 0.2 | 24.5 | 24.5 | 24.7 | 1.56 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:25:00 | 2841.9 | 1364.82 | 841761.48 | 815489.42 | 47.07 | 2340.78 | 2132.046 | -230.606 | 50 | 188 | 26.1 | 57.8 | 26.2 | 58 | 0 | 0 | - | - | 27.6 | 54.1 | 0 | 0 | 0 | 0 | 26.1 | 27.7 | 25.9 | 1.59 | 1.5 | 0.6 | 0 | 25.7 | 27.1 | 25.8 | 1.54 | 1.2 | 0.2 | 24.5 | 24.5 | 24.8 | 1.56 | 1.59 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:30:00 | 2841.9 | 1387.28 | 841761.48 | 815511.82 | 47.18 | 2370.599 | 2102.227 | -310.983 | 49 | 188 | 26.1 | 57.9 | 26.1 | 58 | 0 | 0 | - | - | 27.5 | 54.2 | 0 | 0 | 0 | 0 | 26.1 | 27.6 | 25.9 | 1.59 | 1.4 | 0.6 | 0 | 25.7 | 26.9 | 25.8 | 1.54 | 1.1 | 0.2 | 24.5 | 24.5 | 24.8 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:35:00 | 2841.9 | 1414.08 | 841761.48 | 815539 | 47.29 | 2392.962 | 2079.864 | -339.795 | 48 | 188 | 26 | 57.9 | 26.1 | 58 | 0 | 0 | - | - | 27.5 | 54.3 | 0 | 0 | 0 | 0 | 26.1 | 27.5 | 25.8 | 1.59 | 1.3 | 0.6 | 0 | 25.7 | 26.8 | 25.8 | 1.54 | 1 | 0.1 | 24.5 | 24.5 | 25 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:40:00 | 2841.9 | 1443.08 | 841761.48 | 815568.04 | 47.4 | 2422.779 | 2050.047 | -351.482 | 48 | 188 | 26 | 58 | 26.1 | 58.1 | 0 | 0 | - | - | 27.4 | 54.4 | 0 | 0 | 0 | 0 | 26.1 | 27.4 | 25.9 | 1.59 | 1.3 | 0.6 | 0 | 25.6 | 26.8 | 25.8 | 1.54 | 0.9 | 0.1 | 24.5 | 24.4 | 24.8 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:45:00 | 2841.9 | 1471.24 | 841761.48 | 815595.96 | 47.51 | 2452.599 | 2020.227 | -329.315 | 47 | 188 | 26 | 58 | 26.1 | 58.1 | 0 | 0 | - | - | 27.3 | 54.4 | 0 | 0 | 0 | 0 | 25.9 | 27.4 | 25.8 | 1.59 | 1.3 | 0.5 | 0 | 25.6 | 26.7 | 25.8 | 1.54 | 0.9 | 0.1 | 24.4 | 24.4 | 24.7 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:50:00 | 2841.9 | 1494.72 | 841761.48 | 815619.44 | 47.61 | 2482.419 | 1990.407 | -197.444 | 47 | 188 | 26 | 58.1 | 26.1 | 58.1 | 0 | 0 | - | - | 27.3 | 54.5 | 0 | 0 | 0 | 0 | 25.9 | 27.3 | 25.8 | 1.59 | 1.2 | 0.5 | 0 | 25.6 | 26.7 | 25.8 | 1.54 | 0.8 | 0.1 | 24.4 | 24.4 | 25 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 17:55:00 | 2841.9 | 1511.88 | 841761.48 | 815636.58 | 47.71 | 2497.329 | 1975.497 | -401.809 | 46 | 188 | 25.9 | 58.1 | 26.1 | 58 | 0 | 0 | - | - | 27.3 | 54.5 | 0 | 0 | 0 | 0 | 26 | 27.5 | 26 | 1.59 | 1.3 | 0.5 | 0 | 25.7 | 26.7 | 25.8 | 1.54 | 0.9 | 0.2 | 24.4 | 24.4 | 25.1 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:00:00 | 2841.9 | 1548.7 | 841761.48 | 815673.22 | 47.83 | 2527.149 | 1945.677 | -238.799 | 45 | 188 | 25.9 | 58.1 | 26.1 | 58.1 | 0 | 0 | - | - | 27.2 | 54.6 | 0 | 0 | 0 | 0 | 26 | 27.6 | 26.1 | 1.59 | 1.4 | 0.5 | 0 | 25.7 | 26.7 | 25.9 | 1.54 | 0.9 | 0.2 | 24.4 | 24.4 | 25.1 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:05:00 | 2841.9 | 1573.7 | 841761.48 | 815698.22 | 47.95 | 2556.968 | 1915.858 | -294.611 | 45 | 188 | 25.9 | 58.2 | 26.1 | 58 | 0 | 0 | - | - | 27.2 | 54.6 | 0 | 0 | 0 | 0 | 25.9 | 27.6 | 26.1 | 1.59 | 1.3 | 0.4 | 0 | 25.7 | 26.7 | 25.9 | 1.54 | 0.9 | 0.2 | 24.4 | 24.4 | 25 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:10:00 | 2841.9 | 1597.6 | 841761.48 | 815722.16 | 48.05 | 2571.876 | 1900.95 | -323.47 | 44 | 188 | 25.9 | 58.2 | 26 | 58 | 0 | 0 | - | - | 27.2 | 54.6 | 0 | 0 | 0 | 0 | 25.8 | 27.6 | 26.1 | 1.59 | 1.4 | 0.4 | 0 | 25.7 | 26.7 | 25.9 | 1.54 | 0.9 | 0.2 | 24.4 | 24.4 | 25 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:15:00 | 2841.9 | 1637 | 841761.48 | 815761.6 | 48.17 | 2624.058 | 1848.768 | -740.417 | 43 | 188 | 25.8 | 58.2 | 26 | 58.1 | 0 | 0 | - | - | 27.2 | 54.6 | 0 | 0 | 0 | 0 | 25.7 | 27.6 | 25.9 | 1.59 | 1.4 | 0.3 | 0 | 25.7 | 26.7 | 25.9 | 1.54 | 0.9 | 0.2 | 24.4 | 24.4 | 24.9 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:20:00 | 2841.9 | 1694.14 | 841761.48 | 815818.92 | 48.3 | 2691.152 | 1781.674 | -471.56 | 42 | 188 | 25.8 | 58.2 | 26 | 58.1 | 0 | 0 | - | - | 27.2 | 54.6 | 0 | 0 | 0 | 0 | 25.7 | 27.6 | 25.9 | 1.59 | 1.4 | 0.2 | 0 | 25.7 | 26.7 | 25.9 | 1.54 | 0.9 | 0.2 | 24.4 | 24.3 | 24.9 | 1.56 | 1.59 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:25:00 | 2841.9 | 1741.02 | 841761.48 | 815866.48 | 48.43 | 2735.877 | 1736.949 | -607.42 | 41 | 188 | 25.8 | 58.3 | 26.1 | 58.1 | 0 | 0 | - | - | 27.2 | 54.7 | 0 | 0 | 0 | 0 | 25.7 | 27.6 | 25.9 | 1.59 | 1.5 | 0.3 | 0 | 25.7 | 26.7 | 25.9 | 1.53 | 1 | 0.2 | 24.4 | 24.3 | 25 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:30:00 | 2841.9 | 1802.02 | 841761.48 | 815927.08 | 48.62 | 2817.882 | 1654.944 | -798.669 | 39 | 188 | 25.8 | 58.2 | 26.1 | 58 | 0 | 0 | - | - | 27.2 | 54.7 | 0 | 0 | 0 | 0 | 25.4 | 27.8 | 25.8 | 1.59 | 1.6 | 0 | 0 | 25.6 | 27.3 | 25.9 | 1.54 | 1.5 | 0 | 24.3 | 24.3 | 25.1 | 1.56 | 1.59 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:35:00 | 2841.9 | 1878.44 | 841761.48 | 816003.98 | 48.75 | 2907.337 | 1565.489 | -772.307 | 38 | 188 | 25.8 | 58.3 | 26.1 | 58 | 0 | 0 | - | - | 27.2 | 54.7 | 0 | 0 | 0 | 0 | 25.5 | 27.7 | 25.9 | 1.59 | 1.5 | 0 | 0 | 25.6 | 27.2 | 25.9 | 1.54 | 1.4 | 0.1 | 24.3 | 24.3 | 25.2 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:40:00 | 2841.9 | 1936.78 | 841761.48 | 816062.12 | 48.9 | 2952.066 | 1520.76 | -718.399 | 36 | 188 | 25.8 | 58.2 | 26.1 | 57.9 | 0 | 0 | - | - | 27.1 | 54.7 | 0 | 0 | 0 | 0 | 25.5 | 27.7 | 25.9 | 1.59 | 1.5 | 0.1 | 0 | 25.6 | 27.1 | 26 | 1.54 | 1.3 | 0.1 | 24.3 | 24.3 | 25.2 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:45:00 | 2841.9 | 2005.98 | 841761.48 | 816132.18 | 49.05 | 3034.067 | 1438.759 | -890.614 | 34 | 188 | 25.9 | 58.2 | 26.2 | 57.8 | 0 | 0 | - | - | 27.2 | 54.6 | 0 | 0 | 0 | 0 | 25.5 | 27.6 | 25.9 | 1.58 | 1.4 | 0.1 | 0 | 25.6 | 26.9 | 26 | 1.53 | 1.1 | 0.2 | 24.3 | 24.3 | 25.1 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:50:00 | 2841.9 | 2086.7 | 841761.48 | 816212.3 | 49.2 | 3116.07 | 1356.756 | -908.206 | 32 | 188 | 25.9 | 58.2 | 26.3 | 57.7 | 0 | 0 | - | - | 27.2 | 54.7 | 0 | 0 | 0 | 0 | 25.6 | 27.6 | 26.1 | 1.59 | 1.4 | 0.2 | 0 | 25.7 | 26.9 | 26.1 | 1.53 | 1.1 | 0.2 | 24.4 | 24.3 | 25.3 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 18:55:00 | 2841.9 | 2163.88 | 841761.48 | 816289.62 | 49.34 | 3183.164 | 1289.662 | -977.622 | 31 | 188 | 25.8 | 58.3 | 26.3 | 57.6 | 0 | 0 | - | - | 27.3 | 54.6 | 0 | 0 | 0 | 0 | 25.8 | 27.7 | 26.3 | 1.59 | 1.5 | 0.3 | 0 | 25.8 | 27 | 26.2 | 1.54 | 1.2 | 0.3 | 24.4 | 24.4 | 25.2 | 1.56 | 1.59 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:00:00 | 2841.9 | 2222.2 | 841761.48 | 816348.76 | 49.5 | 3227.889 | 1244.937 | -638.333 | 29 | 188 | 25.8 | 58.4 | 26.4 | 57.5 | 0 | 0 | - | - | 27.3 | 54.6 | 0 | 0 | 0 | 0 | 25.9 | 27.7 | 26.4 | 1.59 | 1.5 | 0.4 | 0 | 25.9 | 27.1 | 26.3 | 1.54 | 1.2 | 0.4 | 24.5 | 24.5 | 25.4 | 1.57 | 1.6 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:05:00 | 2841.9 | 2274.7 | 841761.48 | 816400.12 | 49.66 | 3280.074 | 1192.752 | -584.688 | 28 | 188 | 25.8 | 58.4 | 26.4 | 57.5 | 0 | 0 | - | - | 27.4 | 54.5 | 0 | 0 | 0 | 0 | 26 | 27.8 | 26.7 | 1.59 | 1.5 | 0.5 | 0 | 26.1 | 27.1 | 26.3 | 1.54 | 1.2 | 0.4 | 24.6 | 24.6 | 25.2 | 1.57 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:10:00 | 2841.9 | 2320.92 | 841761.48 | 816445.68 | 49.81 | 3317.349 | 1155.478 | -562.676 | 27 | 188 | 25.9 | 58.3 | 26.4 | 57.5 | 0 | 0 | - | - | 27.4 | 54.5 | 0 | 0 | 0 | 0 | 26.1 | 27.8 | 26.6 | 1.6 | 1.4 | 0.4 | 0 | 26.1 | 27.1 | 26.3 | 1.54 | 1.1 | 0.4 | 24.7 | 24.7 | 25.3 | 1.57 | 1.6 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:15:00 | 2841.9 | 2367.3 | 841761.48 | 816492.76 | 49.96 | 3384.44 | 1088.388 | -630.776 | 26 | 188 | 25.9 | 58.2 | 26.5 | 57.4 | 0 | 0 | - | - | 27.4 | 54.4 | 0 | 0 | 0 | 0 | 26.2 | 27.8 | 26.7 | 1.6 | 1.4 | 0.5 | 0 | 26.1 | 27.2 | 26.5 | 1.54 | 1.1 | 0.4 | 24.8 | 24.8 | 25.4 | 1.57 | 1.6 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:20:00 | 2841.9 | 2417.04 | 841761.48 | 816542.08 | 50.11 | 3444.078 | 1028.748 | -528.665 | 25 | 188 | 26 | 58.2 | 26.5 | 57.4 | 0 | 0 | - | - | 27.4 | 54.4 | 0 | 0 | 0 | 0 | 26.3 | 27.9 | 26.9 | 1.6 | 1.4 | 0.6 | 0 | 26.2 | 27.2 | 26.5 | 1.55 | 1.2 | 0.5 | 25 | 25 | 25.3 | 1.57 | 1.61 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:25:00 | 2841.9 | 2463.98 | 841761.48 | 816589.42 | 50.26 | 3503.716 | 969.11 | -588.175 | 24 | 188 | 26 | 58.2 | 26.5 | 57.5 | 0 | 0 | - | - | 27.5 | 54.3 | 0 | 0 | 0 | 0 | 26.5 | 28 | 27 | 1.6 | 1.5 | 0.8 | 0 | 26.3 | 27.3 | 26.6 | 1.55 | 1.2 | 0.5 | 25.1 | 25.1 | 25.3 | 1.57 | 1.61 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:30:00 | 2841.9 | 2513.42 | 841761.48 | 816639.12 | 50.41 | 3548.442 | 924.384 | -561.422 | 22 | 188 | 26 | 58.2 | 26.5 | 57.5 | 0 | 0 | - | - | 27.5 | 54.3 | 0 | 0 | 0 | 0 | 26.6 | 28 | 27.2 | 1.6 | 1.5 | 0.9 | 0 | 26.4 | 27.4 | 26.7 | 1.55 | 1.2 | 0.6 | 25.3 | 25.3 | 25.3 | 1.57 | 1.61 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:35:00 | 2841.9 | 2545.56 | 841761.48 | 816669.8 | 50.56 | 3578.262 | 894.564 | -202.969 | 22 | 188 | 26.1 | 58.2 | 26.6 | 57.4 | 0 | 0 | - | - | 27.6 | 54.3 | 0 | 0 | 0 | 0 | 26.7 | 28.1 | 27.3 | 1.6 | 1.5 | 1 | 0 | 26.5 | 27.5 | 26.7 | 1.55 | 1.2 | 0.6 | 25.4 | 25.4 | 25.4 | 1.58 | 1.61 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:40:00 | 2841.9 | 2562.88 | 841761.48 | 816687.22 | 50.68 | 3593.172 | 879.654 | -189.935 | 21 | 188 | 26.1 | 58.2 | 26.7 | 57.4 | 0 | 0 | - | - | 27.6 | 54.2 | 0 | 0 | 0 | 0 | 26.9 | 28.1 | 27.3 | 1.61 | 1.4 | 1.1 | 0 | 26.6 | 27.6 | 26.9 | 1.56 | 1.2 | 0.6 | 25.5 | 25.5 | 25.7 | 1.58 | 1.62 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:45:00 | 2841.9 | 2577.54 | 841761.48 | 816702.16 | 50.81 | 3593.172 | 879.654 | -224.489 | 21 | 188 | 26.1 | 58.3 | 26.7 | 57.5 | 0 | 0 | - | - | 27.6 | 54.2 | 0 | 0 | 0 | 0 | 26.9 | 28.1 | 27.3 | 1.61 | 1.4 | 1 | 0 | 26.7 | 27.6 | 26.9 | 1.56 | 1.2 | 0.6 | 25.6 | 25.6 | 25.7 | 1.58 | 1.62 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:50:00 | 2841.9 | 2597.28 | 841761.48 | 816721.8 | 50.93 | 3637.902 | 834.924 | -151.698 | 20 | 188 | 26.1 | 58.3 | 26.4 | 57.9 | 0 | 0 | - | - | 27.6 | 54.2 | 0 | 0 | 0 | 0 | 26.9 | 28.1 | 27.2 | 1.61 | 1.2 | 1 | 0 | 26.7 | 27.6 | 26.9 | 1.56 | 1.1 | 0.5 | 25.7 | 25.7 | 26 | 1.58 | 1.62 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 19:55:00 | 2841.9 | 2620.28 | 841761.48 | 816744.62 | 51.06 | 3637.902 | 834.924 | -212.329 | 20 | 188 | 26.1 | 58.4 | 26.4 | 58 | 0 | 0 | - | - | 27.7 | 54.3 | 0 | 0 | 0 | 0 | 26.9 | 28.1 | 27.3 | 1.61 | 1.3 | 1 | 0 | 26.7 | 27.6 | 26.9 | 1.56 | 1.1 | 0.5 | 25.7 | 25.7 | 26.1 | 1.58 | 1.62 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:00:00 | 2841.9 | 2653.14 | 841761.48 | 816777.88 | 51.19 | 3682.63 | 790.196 | -335.081 | 19 | 188 | 26.1 | 58.5 | 26.5 | 57.9 | 0 | 0 | - | - | 27.7 | 54.3 | 0 | 0 | 0 | 0 | 27 | 28.2 | 27.4 | 1.6 | 1.4 | 1.2 | 0 | 26.7 | 27.6 | 26.8 | 1.56 | 1.1 | 0.6 | 25.8 | 25.8 | 26 | 1.58 | 1.62 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:05:00 | 2841.9 | 2670.72 | 841761.48 | 816795.12 | 51.31 | 3712.447 | 760.379 | -4.285 | 19 | 188 | 26.1 | 58.4 | 26.6 | 57.8 | 0 | 0 | - | - | 27.7 | 54.3 | 0 | 0 | 0 | 0 | 27.1 | 28.2 | 27.4 | 1.61 | 1.4 | 1.2 | 0 | 26.8 | 27.6 | 26.9 | 1.57 | 1 | 0.6 | 25.9 | 25.9 | 26.1 | 1.58 | 1.62 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:10:00 | 2842.44 | 2674.26 | 841762.02 | 816798.54 | 51.42 | 3712.447 | 760.379 | -51.395 | 19 | 188 | 26.2 | 58.5 | 26.7 | 57.7 | 0 | 0 | - | - | 27.7 | 54.3 | 0 | 0 | 0 | 0 | 27.2 | 28.2 | 27.5 | 1.61 | 1.4 | 1.2 | 0 | 26.9 | 27.7 | 26.9 | 1.57 | 1 | 0.6 | 25.9 | 25.9 | 26.1 | 1.58 | 1.62 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:15:00 | 2842.44 | 2681.6 | 841762.02 | 816806.14 | 51.54 | 3734.811 | 738.015 | -181.796 | 18 | 188 | 26.2 | 58.5 | 26.4 | 58.2 | 0 | 0 | - | - | 27.7 | 54.3 | 0 | 0 | 0 | 0 | 27.2 | 28.2 | 27.4 | 1.61 | 1.3 | 1.1 | 0 | 26.8 | 27.7 | 26.9 | 1.57 | 1 | 0.6 | 26 | 26 | 26.1 | 1.59 | 1.62 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:20:00 | 2842.44 | 2688.38 | 841762.02 | 816812.68 | 51.65 | 3734.811 | 738.015 | -7.135 | 18 | 188 | 26.2 | 58.5 | 26.3 | 58.5 | 0 | 0 | - | - | 27.7 | 54.3 | 0 | 0 | 0 | 0 | 27.2 | 28.2 | 27.4 | 1.62 | 1.3 | 1 | 0 | 26.8 | 27.7 | 27 | 1.57 | 1 | 0.5 | 26.1 | 26 | 26.1 | 1.59 | 1.62 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:25:00 | 2842.5 | 2691.74 | 841762.08 | 816816.04 | 51.76 | 3734.811 | 738.015 | -69.023 | 18 | 188 | 26.3 | 58.6 | 26.5 | 58.1 | 0 | 0 | - | - | 27.7 | 54.3 | 0 | 0 | 0 | 0 | 27.2 | 28.2 | 27.3 | 1.62 | 1.2 | 1 | 0 | 26.8 | 27.7 | 27 | 1.57 | 1 | 0.5 | 26.1 | 26.1 | 26.1 | 1.59 | 1.63 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:30:00 | 2842.54 | 2695.74 | 841762.12 | 816819.98 | 51.87 | 3742.266 | 730.56 | -38.704 | 18 | 188 | 26.2 | 58.6 | 26.7 | 58 | 0 | 0 | - | - | 27.7 | 54.4 | 0 | 0 | 0 | 0 | 27.2 | 28.2 | 27.4 | 1.62 | 1.3 | 1 | 0 | 26.8 | 27.7 | 27.1 | 1.57 | 1 | 0.5 | 26.1 | 26.1 | 26.2 | 1.59 | 1.63 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:35:00 | 2842.54 | 2699.26 | 841762.12 | 816823.54 | 51.98 | 3742.266 | 730.56 | -106.558 | 18 | 188 | 26.2 | 58.6 | 26.7 | 58 | 0 | 0 | - | - | 27.7 | 54.4 | 0 | 0 | 0 | 0 | 27.3 | 28.2 | 27.6 | 1.62 | 1.3 | 1.1 | 0 | 26.9 | 27.8 | 27.2 | 1.58 | 1 | 0.5 | 26.1 | 26.1 | 26.4 | 1.59 | 1.63 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:40:00 | 2842.54 | 2706.28 | 841762.12 | 816830.68 | 52.08 | 3742.266 | 730.56 | -65.859 | 18 | 188 | 26.2 | 58.7 | 26.7 | 58 | 0 | 0 | - | - | 27.6 | 54.5 | 0 | 0 | 0 | 0 | 27.4 | 28.4 | 27.7 | 1.62 | 1.4 | 1.1 | 0 | 27.1 | 27.8 | 27.3 | 1.58 | 1 | 0.6 | 26.1 | 26.1 | 26.7 | 1.6 | 1.63 | 1.61 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:45:00 | 2842.54 | 2712.34 | 841762.12 | 816836.7 | 52.19 | 3757.176 | 715.65 | -45.796 | 18 | 188 | 26.3 | 58.7 | 26.7 | 58 | 0 | 0 | - | - | 27.7 | 54.5 | 0 | 0 | 0 | 0 | 27.4 | 28.4 | 27.6 | 1.62 | 1.4 | 1.2 | 0 | 27.1 | 27.8 | 27.4 | 1.58 | 1 | 0.6 | 26.2 | 26.1 | 26.6 | 1.6 | 1.63 | 1.61 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:50:00 | 2842.54 | 2719.78 | 841762.12 | 816844.06 | 52.3 | 3757.176 | 715.65 | -97.452 | 18 | 188 | 26.3 | 58.7 | 26.8 | 58 | 0 | 0 | - | - | 27.7 | 54.5 | 0 | 0 | 0 | 0 | 27.2 | 28.3 | 27.4 | 1.62 | 1.3 | 1 | 0 | 26.9 | 27.8 | 27.3 | 1.58 | 1 | 0.5 | 26.2 | 26.1 | 26.3 | 1.59 | 1.63 | 1.61 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 20:55:00 | 2842.54 | 2732.88 | 841762.12 | 816857.5 | 52.41 | 3779.541 | 693.285 | -197.591 | 17 | 188 | 26.2 | 58.7 | 26.7 | 58 | 0 | 0 | - | - | 27.7 | 54.5 | 0 | 0 | 0 | 0 | 27.1 | 28.1 | 27.2 | 1.62 | 1.1 | 0.8 | 0 | 26.7 | 27.7 | 27.2 | 1.58 | 0.8 | 0.2 | 26.2 | 26.1 | 26.1 | 1.59 | 1.63 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:00:00 | 2842.54 | 2745.82 | 841762.12 | 816870.42 | 52.52 | 3786.995 | 685.831 | -117.821 | 17 | 188 | 26.3 | 58.7 | 26.7 | 58.1 | 0 | 0 | - | - | 27.7 | 54.5 | 0 | 0 | 0 | 0 | 26.9 | 27.9 | 26.9 | 1.61 | 1 | 0.8 | 0 | 26.1 | 27.5 | 27.1 | 1.57 | 0.8 | -0.4 | 26.2 | 26.2 | 25.9 | 1.59 | 1.63 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:05:00 | 2842.54 | 2754.94 | 841762.12 | 816879.34 | 52.63 | 3786.995 | 685.831 | -97.264 | 17 | 188 | 26.3 | 58.7 | 26.7 | 58.1 | 0 | 0 | - | - | 27.6 | 54.6 | 0 | 0 | 0 | 0 | 26.8 | 27.9 | 26.8 | 1.61 | 1 | 0.8 | 0 | 25.9 | 27.3 | 26.9 | 1.57 | 0.7 | -0.4 | 26.2 | 26.2 | 25.7 | 1.58 | 1.62 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:10:00 | 2842.54 | 2760.2 | 841762.12 | 816884.48 | 52.74 | 3801.905 | 670.921 | -83.449 | 17 | 188 | 26.3 | 58.8 | 26.8 | 58.1 | 0 | 0 | - | - | 27.6 | 54.7 | 0 | 0 | 0 | 0 | 26.8 | 27.8 | 26.7 | 1.61 | 1 | 0.8 | 0 | 25.9 | 27.3 | 26.8 | 1.57 | 0.6 | -0.4 | 26.3 | 26.3 | 25.7 | 1.58 | 1.62 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:15:00 | 2842.64 | 2762.84 | 841762.22 | 816887.1 | 52.84 | 3801.905 | 670.921 | -7.917 | 17 | 188 | 26.3 | 58.8 | 26.8 | 58.1 | 0 | 0 | - | - | 27.6 | 54.7 | 0 | 0 | 0 | 0 | 26.7 | 27.8 | 26.7 | 1.62 | 0.9 | 0.6 | 0 | 25.9 | 27.3 | 26.8 | 1.57 | 0.6 | -0.4 | 26.2 | 26.3 | 26.2 | 1.59 | 1.62 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:20:00 | 2842.64 | 2768.14 | 841762.22 | 816892.48 | 52.95 | 3801.905 | 670.921 | -51.576 | 16 | 188 | 26.3 | 58.8 | 26.8 | 58.2 | 0 | 0 | - | - | 27.6 | 54.8 | 0 | 0 | 0 | 0 | 26.9 | 28 | 27.1 | 1.62 | 1.1 | 0.8 | 0 | 26.1 | 27.4 | 27 | 1.57 | 0.7 | -0.4 | 26.3 | 26.3 | 26.4 | 1.59 | 1.62 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:25:00 | 2842.64 | 2773.06 | 841762.22 | 816897.4 | 53.05 | 3801.905 | 670.921 | -41.293 | 16 | 188 | 26.3 | 58.8 | 26.8 | 58.2 | 0 | 0 | - | - | 27.6 | 54.8 | 0 | 0 | 0 | 0 | 27.2 | 28.2 | 27.5 | 1.62 | 1.2 | 0.9 | 0 | 26.1 | 27.6 | 27.2 | 1.58 | 0.8 | -0.3 | 26.3 | 26.3 | 26.4 | 1.59 | 1.63 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:30:00 | 2842.64 | 2776.5 | 841762.22 | 816900.82 | 53.16 | 3824.268 | 648.558 | -22.379 | 16 | 188 | 26.3 | 58.9 | 26.8 | 58.2 | 0 | 0 | - | - | 27.6 | 54.8 | 0 | 0 | 0 | 0 | 27.3 | 28.2 | 27.5 | 1.62 | 1.2 | 1.1 | 0 | 26.1 | 27.7 | 27.3 | 1.58 | 0.9 | -0.3 | 26.4 | 26.3 | 26.4 | 1.6 | 1.63 | 1.61 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:35:00 | 2847.38 | 2777.32 | 841766.96 | 816901.56 | 53.26 | 3801.905 | 670.921 | 65.128 | 16 | 188 | 26.3 | 58.8 | 26.7 | 58.2 | 0 | 0 | - | - | 27.6 | 54.8 | 0 | 0 | 0 | 0 | 26.1 | 28.2 | 27.5 | 1.63 | 1.2 | -0.2 | 0 | 26.1 | 27.8 | 27.4 | 1.58 | 1 | -0.4 | 26.4 | 26.4 | 26.6 | 1.6 | 1.63 | 1.61 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:40:00 | 2848.64 | 2779.46 | 841768.22 | 816903.76 | 53.37 | 3809.359 | 663.467 | 10.728 | 16 | 188 | 26.3 | 58.9 | 26.7 | 58.3 | 0 | 0 | - | - | 27.7 | 54.8 | 0 | 0 | 0 | 0 | 26.1 | 28.3 | 27.4 | 1.63 | 1.2 | -0.3 | 0 | 26.2 | 27.8 | 27.4 | 1.58 | 1 | -0.3 | 26.4 | 26.4 | 26.6 | 1.6 | 1.64 | 1.61 | 1.62 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:45:00 | 2851.82 | 2780.04 | 841771.58 | 816904.28 | 53.47 | 3801.905 | 670.921 | 103.758 | 16 | 188 | 26.3 | 58.9 | 26.8 | 58.3 | 0 | 0 | - | - | 27.7 | 54.8 | 0 | 0 | 0 | 0 | 26.1 | 28.2 | 27.4 | 1.63 | 1 | -0.4 | 0 | 26.3 | 27.8 | 27.4 | 1.58 | 0.9 | -0.3 | 26.4 | 26.4 | 26.7 | 1.61 | 1.64 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:50:00 | 2860.24 | 2780.04 | 841780.04 | 816904.28 | 53.58 | 3801.905 | 670.921 | 146.755 | 17 | 188 | 26.4 | 58.9 | 26.7 | 58.4 | 0 | 0 | - | - | 27.7 | 54.8 | 0 | 0 | 0 | 0 | 26.2 | 28.4 | 27.7 | 1.63 | 1.2 | -0.2 | 0 | 26.3 | 27.9 | 27.4 | 1.59 | 0.9 | -0.3 | 26.4 | 26.4 | 26.6 | 1.6 | 1.64 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 21:55:00 | 2865.68 | 2780.24 | 841785.28 | 816904.54 | 53.68 | 3786.995 | 685.831 | -82.95 | 17 | 188 | 26.3 | 59 | 26.7 | 58.4 | 0 | 0 | - | - | 27.7 | 54.8 | 0 | 0 | 0 | 0 | 26.1 | 28.5 | 27.9 | 1.62 | 1.4 | -0.2 | 0 | 26.4 | 27.9 | 27.4 | 1.59 | 0.9 | -0.3 | 26.4 | 26.4 | 26.4 | 1.59 | 1.63 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:00:00 | 2865.7 | 2790.7 | 841785.28 | 816915.22 | 53.8 | 3801.905 | 670.921 | -109.456 | 16 | 188 | 26.3 | 59 | 26.7 | 58.4 | 0 | 0 | - | - | 27.7 | 54.8 | 0 | 0 | 0 | 0 | 26.1 | 28.5 | 27.8 | 1.62 | 1.4 | -0.2 | 0 | 26.4 | 27.9 | 27.4 | 1.58 | 1 | -0.2 | 26.5 | 26.4 | 26.3 | 1.6 | 1.63 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:05:00 | 2865.78 | 2796.9 | 841785.36 | 816921.2 | 53.9 | 3816.813 | 656.013 | -95.99 | 16 | 188 | 26.3 | 58.9 | 26.7 | 58.5 | 0 | 0 | - | - | 27.7 | 54.8 | 0 | 0 | 0 | 0 | 26.2 | 28.5 | 27.8 | 1.63 | 1.4 | -0.2 | 0 | 26.4 | 27.9 | 27.4 | 1.59 | 0.9 | -0.3 | 26.5 | 26.4 | 26.4 | 1.6 | 1.63 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:10:00 | 2868.58 | 2799.28 | 841788.36 | 816923.52 | 54 | 3801.905 | 670.921 | 121.624 | 16 | 188 | 26.3 | 59 | 26.7 | 58.5 | 0 | 0 | - | - | 27.7 | 54.8 | 0 | 0 | 0 | 0 | 26.2 | 28.6 | 27.9 | 1.63 | 1.4 | -0.2 | 0 | 26.4 | 28 | 27.6 | 1.59 | 1 | -0.2 | 26.5 | 26.5 | 26.6 | 1.6 | 1.64 | 1.62 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:15:00 | 2887.4 | 2799.28 | 841807.28 | 816923.52 | 54.12 | 3786.995 | 685.831 | 300.905 | 17 | 188 | 26.3 | 59 | 26.7 | 58.6 | 0 | 0 | - | - | 27.7 | 54.8 | 0 | 0 | 0 | 0 | 26.2 | 28.7 | 28 | 1.63 | 1.5 | -0.1 | 0 | 26.5 | 28.1 | 27.7 | 1.59 | 1 | -0.2 | 26.5 | 26.5 | 26.6 | 1.6 | 1.64 | 1.62 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:20:00 | 2913.22 | 2799.28 | 841833.18 | 816923.52 | 54.24 | 3764.631 | 708.195 | 394.132 | 17 | 188 | 26.4 | 59 | 26.7 | 58.6 | 0 | 0 | - | - | 27.7 | 54.9 | 0 | 0 | 0 | 0 | 26.2 | 28.7 | 28.1 | 1.63 | 1.5 | -0.1 | 0 | 26.5 | 28.1 | 27.6 | 1.59 | 1 | -0.2 | 26.5 | 26.5 | 26.4 | 1.6 | 1.64 | 1.62 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:25:00 | 2948.76 | 2799.28 | 841868.56 | 816923.52 | 54.36 | 3734.811 | 738.015 | 435.791 | 18 | 188 | 26.4 | 59.1 | 26.7 | 58.7 | 0 | 0 | - | - | 27.7 | 54.9 | 0 | 0 | 0 | 0 | 26.3 | 28.7 | 28.1 | 1.63 | 1.6 | -0.1 | 0 | 26.5 | 28.1 | 27.6 | 1.59 | 1 | -0.2 | 26.5 | 26.5 | 26.3 | 1.6 | 1.64 | 1.62 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:30:00 | 2990.76 | 2799.28 | 841910.78 | 816923.52 | 54.5 | 3682.63 | 790.196 | 377.236 | 19 | 188 | 26.3 | 59.2 | 26.7 | 58.7 | 0 | 0 | - | - | 27.7 | 54.9 | 0 | 0 | 0 | 0 | 26.3 | 28.7 | 28.1 | 1.63 | 1.5 | -0.1 | 0 | 26.5 | 28.1 | 27.6 | 1.59 | 1 | -0.2 | 26.5 | 26.5 | 26.3 | 1.6 | 1.64 | 1.62 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:35:00 | 3023.02 | 2799.28 | 841942.8 | 816923.52 | 54.63 | 3645.357 | 827.469 | 169.037 | 20 | 188 | 26.3 | 59.2 | 26.7 | 58.7 | 0 | 0 | - | - | 27.7 | 54.9 | 0 | 0 | 0 | 0 | 26.2 | 28.7 | 27.9 | 1.63 | 1.5 | -0.2 | 0 | 26.4 | 28.1 | 27.6 | 1.59 | 1 | -0.3 | 26.6 | 26.5 | 26.3 | 1.6 | 1.64 | 1.62 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:40:00 | 3024.6 | 2804.38 | 841944.18 | 816928.64 | 54.74 | 3660.267 | 812.559 | -11.701 | 20 | 188 | 26.4 | 59.1 | 26.8 | 58.5 | 0 | 0 | - | - | 27.7 | 54.9 | 0 | 0 | 0 | 0 | 26.2 | 28.4 | 27.6 | 1.63 | 1.2 | -0.3 | 0 | 26.3 | 27.9 | 27.6 | 1.59 | 0.9 | -0.3 | 26.6 | 26.6 | 26.2 | 1.6 | 1.64 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:45:00 | 3025.38 | 2813.7 | 841944.96 | 816938.34 | 54.86 | 3660.267 | 812.559 | -189.778 | 20 | 188 | 26.4 | 59.1 | 26.8 | 58.5 | 0 | 0 | - | - | 27.8 | 55 | 0 | 0 | 0 | 0 | 26.1 | 28.2 | 27.2 | 1.63 | 1 | -0.4 | 0 | 26.2 | 27.7 | 27.5 | 1.59 | 0.7 | -0.4 | 26.6 | 26.6 | 26.1 | 1.6 | 1.64 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:50:00 | 3025.38 | 2833.82 | 841944.96 | 816958.56 | 54.98 | 3682.63 | 790.196 | -141.449 | 19 | 188 | 26.4 | 59.1 | 26.8 | 58.6 | 0 | 0 | - | - | 27.7 | 55 | 0 | 0 | 0 | 0 | 26.1 | 28.2 | 27.2 | 1.63 | 0.9 | -0.3 | 0 | 26.2 | 27.7 | 27.3 | 1.59 | 0.6 | -0.4 | 26.7 | 26.6 | 26.3 | 1.6 | 1.64 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 22:55:00 | 3025.72 | 2840.78 | 841945.3 | 816965.1 | 55.09 | 3690.085 | 782.741 | 7.317 | 19 | 188 | 26.4 | 59.1 | 26.8 | 58.6 | 0 | 0 | - | - | 27.7 | 55.1 | 0 | 0 | 0 | 0 | 26.2 | 28.3 | 27.4 | 1.62 | 1.1 | -0.1 | 0 | 26.3 | 27.7 | 27.3 | 1.59 | 0.6 | -0.3 | 26.7 | 26.6 | 26.2 | 1.6 | 1.64 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:00:00 | 3028.38 | 2844.6 | 841947.96 | 816968.86 | 55.21 | 3690.085 | 782.741 | 36.972 | 19 | 188 | 26.4 | 59.2 | 26.8 | 58.6 | 0 | 0 | - | - | 27.7 | 55.1 | 0 | 0 | 0 | 0 | 26.2 | 28.4 | 27.6 | 1.63 | 1.2 | -0.1 | 0 | 26.4 | 27.8 | 27.3 | 1.59 | 0.7 | -0.3 | 26.7 | 26.7 | 26.2 | 1.6 | 1.64 | 1.61 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:05:00 | 3028.86 | 2855.88 | 841948.44 | 816980.5 | 55.32 | 3697.539 | 775.287 | -386.711 | 19 | 188 | 26.3 | 59.4 | 26.8 | 58.6 | 0 | 0 | - | - | 27.7 | 55.2 | 0 | 0 | 0 | 0 | 26.2 | 28.5 | 27.7 | 1.63 | 1.2 | 0 | 0 | 26.4 | 27.8 | 27.3 | 1.59 | 0.8 | -0.3 | 26.7 | 26.7 | 26.2 | 1.6 | 1.64 | 1.62 | 1.63 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:10:00 | 3028.86 | 2884.34 | 841948.44 | 817009.24 | 55.45 | 3734.811 | 738.015 | -246.206 | 18 | 188 | 26.2 | 59.6 | 26.8 | 58.7 | 0 | 0 | - | - | 27.6 | 55.2 | 0 | 0 | 0 | 0 | 26.3 | 28.5 | 27.7 | 1.63 | 1.2 | -0.1 | 0 | 26.4 | 27.9 | 27.4 | 1.59 | 0.8 | -0.2 | 26.7 | 26.7 | 26.4 | 1.6 | 1.64 | 1.62 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:15:00 | 3028.86 | 2903.56 | 841948.44 | 817027.96 | 55.58 | 3757.176 | 715.65 | -86.034 | 18 | 188 | 26.2 | 59.6 | 26.7 | 58.8 | 0 | 0 | - | - | 27.6 | 55.2 | 0 | 0 | 0 | 0 | 26.4 | 28.6 | 27.7 | 1.63 | 1.2 | 0 | 0 | 26.5 | 28 | 27.6 | 1.59 | 0.9 | -0.2 | 26.8 | 26.7 | 26.6 | 1.61 | 1.65 | 1.62 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:20:00 | 3030.96 | 2906.56 | 841950.54 | 817031.04 | 55.7 | 3757.176 | 715.65 | -157.315 | 18 | 188 | 26.3 | 59.5 | 26.8 | 58.8 | 0 | 0 | - | - | 27.7 | 55.3 | 0 | 0 | 0 | 0 | 26.4 | 28.6 | 27.7 | 1.63 | 1.2 | -0.1 | 0 | 26.5 | 28.1 | 27.6 | 1.59 | 0.9 | -0.2 | 26.8 | 26.8 | 26.6 | 1.61 | 1.65 | 1.62 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:25:00 | 3031.18 | 2914.3 | 841950.76 | 817038.62 | 55.81 | 3757.176 | 715.65 | -135.489 | 17 | 188 | 26.3 | 59.5 | 26.7 | 58.8 | 0 | 0 | - | - | 27.7 | 55.3 | 0 | 0 | 0 | 0 | 26.3 | 28.7 | 27.7 | 1.63 | 1.2 | -0.1 | 0 | 26.6 | 28.1 | 27.6 | 1.59 | 0.9 | -0.2 | 26.8 | 26.8 | 26.4 | 1.6 | 1.65 | 1.62 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:30:00 | 3032.66 | 2918.88 | 841952.34 | 817043.12 | 55.94 | 3779.541 | 693.285 | -44.924 | 17 | 188 | 26.3 | 59.5 | 26.7 | 58.9 | 0 | 0 | - | - | 27.6 | 55.3 | 0 | 0 | 0 | 0 | 26.3 | 28.6 | 27.6 | 1.63 | 1.1 | -0.2 | 0 | 26.4 | 28.1 | 27.6 | 1.59 | 0.8 | -0.3 | 26.8 | 26.8 | 26.4 | 1.61 | 1.65 | 1.62 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:35:00 | 3032.92 | 2924.84 | 841952.5 | 817049.08 | 56.05 | 3779.541 | 693.285 | 20.719 | 17 | 188 | 26.3 | 59.5 | 26.7 | 58.9 | 0 | 0 | - | - | 27.7 | 55.3 | 0 | 0 | 0 | 0 | 26.3 | 28.5 | 27.6 | 1.63 | 1 | -0.1 | 0 | 26.5 | 27.9 | 27.4 | 1.59 | 0.7 | -0.3 | 26.9 | 26.8 | 26.3 | 1.61 | 1.65 | 1.62 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:40:00 | 3040.24 | 2924.84 | 841959.86 | 817049.08 | 56.16 | 3772.086 | 700.74 | 78.171 | 17 | 188 | 26.4 | 59.5 | 26.7 | 58.9 | 0 | 0 | - | - | 27.7 | 55.4 | 0 | 0 | 0 | 0 | 26.3 | 28.6 | 27.8 | 1.63 | 1.1 | -0.1 | 0 | 26.5 | 27.9 | 27.4 | 1.59 | 0.7 | -0.2 | 26.9 | 26.9 | 26.2 | 1.6 | 1.65 | 1.62 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:45:00 | 3046.96 | 2925.58 | 841966.54 | 817049.82 | 56.28 | 3757.176 | 715.65 | -37.943 | 17 | 188 | 26.4 | 59.5 | 26.7 | 59 | 0 | 0 | - | - | 27.6 | 55.4 | 0 | 0 | 0 | 0 | 26.3 | 28.6 | 27.9 | 1.63 | 1.1 | -0.1 | 0 | 26.5 | 28 | 27.3 | 1.59 | 0.8 | -0.2 | 26.9 | 26.9 | 26.2 | 1.61 | 1.65 | 1.62 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:50:00 | 3048.54 | 2926.52 | 841968.12 | 817050.86 | 56.4 | 3757.176 | 715.65 | -90.932 | 17 | 188 | 26.4 | 59.5 | 26.8 | 58.9 | 0 | 0 | - | - | 27.6 | 55.4 | 0 | 0 | 0 | 0 | 26.4 | 28.7 | 27.9 | 1.63 | 1.1 | -0.1 | 0 | 26.6 | 28 | 27.4 | 1.59 | 0.8 | -0.2 | 26.9 | 26.9 | 26.3 | 1.61 | 1.65 | 1.62 | 1.64 | 0 | 0 | 0 | 0
Amleang 136MW-01 | / | SACU-07/B07-ESS04 | 2026-06-02 23:55:00 | 3048.54 | 2949.7 | 841968.12 | 817074.08 | 56.52 | 3779.541 | 693.285 | -299.695 | 17 | 188 | 26.3 | 59.6 | 26.7 | 59 | 0 | 0 | - | - | 27.6 | 55.5 | 0 | 0 | 0 | 0 | 26.3 | 28.4 | 27.6 | 1.64 | 0.9 | -0.3 | 0 | 26.4 | 27.9 | 27.4 | 1.59 | 0.7 | -0.3 | 26.9 | 26.9 | 26.2 | 1.61 | 1.65 | 1.62 | 1.64 | 0 | 0 | 0 | 0