## 5 minutes
Time range: | 2026-06-02 00:00:00 - 2026-06-02 23:59:59
Export time: | 2026-06-03 01:05:02
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge energy(kWh) | Total discharge energy(kWh) | Daily auxiliary power consumption(kWh) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge power(kW) | SOC(%) | Equivalent number of cycles | Battery cabin temperature 1(℃) | Battery cabin humidity 1(%) | Battery cabin temperature 2(℃) | Battery cabin humidity 2(%) | CO concentration 1(ppm) | CO concentration 2(ppm) | H2 concentration 1(ppm) | H2 concentration 2(ppm) | Control unit cabin temperature 1(℃) | Control unit cabin humidity 1(%) | Control status of EEV 1(step) | Control status of EEV 2(step) | Running status of outdoor fan 1(%) | Running status of outdoor fan 2(%) | Discharge temperature of compressor 1(℃) | Suction temperature of refrigerant system 1(℃) | Condenser outlet temperature of refrigerant system 1(℃) | Condenser outlet pressure of refrigerant system 1(Mpa) | Suction superheat degree of refrigerant system 1(℃) | Discharge superheat degree of compressor 1(℃) | Running status of outdoor fan 3(%) | Discharge temperature of compressor 2(℃) | Suction temperature of refrigerant system 2(℃) | Condenser outlet temperature of refrigerant system 2(℃) | Condenser outlet pressure of refrigerant system 2(Mpa) | Suction superheat degree of refrigerant system 2(℃) | Discharge superheat degree of compressor 2(℃) | Battery-side supply water temperature(℃) | Battery-side return water temperature(℃) | Air intake temperature(℃) | Discharge pressure of refrigerant system 1(Mpa) | Suction pressure of refrigerant system 1(Mpa) | Discharge pressure of refrigerant system 2(Mpa) | Suction pressure of refrigerant system 2(Mpa) | Running status of EEV 1(step) | Running status of EEV 2(step) | Compressor 1 running status(rpm) | Compressor 2 running status(rpm)
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:00:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.6 | 56.7 | 25.7 | 56.8 | 0 | 0 | - | - | 28.6 | 51.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:05:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.6 | 56.6 | 25.7 | 56.8 | 0 | 0 | - | - | 28.5 | 51.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:10:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.6 | 56.7 | 25.7 | 56.8 | 0 | 0 | - | - | 28.5 | 51.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:15:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.6 | 56.8 | 25.7 | 56.8 | 0 | 0 | - | - | 28.4 | 51.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:20:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.6 | 56.8 | 25.7 | 56.8 | 0 | 0 | - | - | 28.4 | 51.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:25:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.5 | 56.8 | 25.7 | 56.9 | 0 | 0 | - | - | 28.3 | 51.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:30:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.6 | 56.8 | 25.7 | 56.8 | 0 | 0 | - | - | 28.3 | 51.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:35:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.5 | 56.8 | 25.7 | 56.9 | 0 | 0 | - | - | 28.2 | 51.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:40:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.5 | 56.9 | 25.6 | 56.9 | 0 | 0 | - | - | 28.1 | 51.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:45:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.5 | 56.9 | 25.6 | 56.9 | 0 | 0 | - | - | 28.1 | 51.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:50:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.5 | 56.9 | 25.6 | 56.9 | 0 | 0 | - | - | 28.1 | 51.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 00:55:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.5 | 56.9 | 25.6 | 56.9 | 0 | 0 | - | - | 28 | 51.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:00:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.5 | 56.9 | 25.6 | 56.9 | 0 | 0 | - | - | 28 | 51.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:05:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.5 | 56.9 | 25.7 | 56.9 | 0 | 0 | - | - | 27.9 | 51.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:10:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.5 | 56.9 | 25.7 | 56.8 | 0 | 0 | - | - | 27.9 | 51.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:15:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.5 | 56.9 | 25.7 | 56.8 | 0 | 0 | - | - | 27.9 | 51.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:20:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 3778.644 | 649.452 | -0.023 | 15 | 183 | 25.6 | 56.8 | 25.7 | 56.8 | 0 | 0 | - | - | 27.8 | 51.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:25:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.8 | 25.7 | 56.8 | 0 | 0 | - | - | 27.8 | 51.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:30:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.8 | 25.7 | 56.8 | 0 | 0 | - | - | 27.8 | 52 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:35:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.8 | 25.7 | 56.8 | 0 | 0 | - | - | 27.7 | 52 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:40:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.8 | 25.7 | 56.9 | 0 | 0 | - | - | 27.7 | 51.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:45:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.7 | 25.7 | 56.8 | 0 | 0 | - | - | 27.7 | 52 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:50:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.8 | 25.7 | 56.9 | 0 | 0 | - | - | 27.7 | 52 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 01:55:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.7 | 25.7 | 56.9 | 0 | 0 | - | - | 27.6 | 52 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:00:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.7 | 25.6 | 56.9 | 0 | 0 | - | - | 27.6 | 52.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:05:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.6 | 25.6 | 56.9 | 0 | 0 | - | - | 27.6 | 52.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:10:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.7 | 56.6 | 25.6 | 56.9 | 0 | 0 | - | - | 27.6 | 52.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:15:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.6 | 25.6 | 56.9 | 0 | 0 | - | - | 27.6 | 52.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:20:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.7 | 56.6 | 25.6 | 57 | 0 | 0 | - | - | 27.6 | 52.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:25:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.7 | 56.6 | 25.6 | 56.9 | 0 | 0 | - | - | 27.6 | 52.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:30:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.7 | 56.6 | 25.6 | 56.9 | 0 | 0 | - | - | 27.5 | 52.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:35:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.7 | 56.6 | 25.6 | 57 | 0 | 0 | - | - | 27.5 | 52.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:40:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.7 | 56.6 | 25.6 | 57 | 0 | 0 | - | - | 27.5 | 52.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:45:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.6 | 25.6 | 57 | 0 | 0 | - | - | 27.5 | 52.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:50:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.6 | 25.5 | 57.1 | 0 | 0 | - | - | 27.4 | 52.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 02:55:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.6 | 25.5 | 57 | 0 | 0 | - | - | 27.4 | 52.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:00:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.6 | 25.5 | 57.1 | 0 | 0 | - | - | 27.4 | 52.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:05:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.6 | 25.5 | 57.1 | 0 | 0 | - | - | 27.4 | 52.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:10:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.6 | 25.5 | 57.1 | 0 | 0 | - | - | 27.4 | 52.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:15:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.6 | 25.5 | 57.1 | 0 | 0 | - | - | 27.3 | 52.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:20:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.6 | 25.5 | 57.1 | 0 | 0 | - | - | 27.3 | 52.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:25:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.7 | 25.5 | 57.1 | 0 | 0 | - | - | 27.3 | 52.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:30:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.6 | 25.5 | 57.2 | 0 | 0 | - | - | 27.3 | 52.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:35:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.6 | 56.7 | 25.4 | 57.2 | 0 | 0 | - | - | 27.2 | 52.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:40:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.5 | 56.7 | 25.4 | 57.2 | 0 | 0 | - | - | 27.2 | 52.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:45:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.5 | 56.7 | 25.4 | 57.3 | 0 | 0 | - | - | 27.2 | 52.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:50:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.5 | 56.8 | 25.3 | 57.3 | 0 | 0 | - | - | 27.2 | 52.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 03:55:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.5 | 56.8 | 25.3 | 57.3 | 0 | 0 | - | - | 27.1 | 52.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:00:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.4 | 56.9 | 25.3 | 57.4 | 0 | 0 | - | - | 27.1 | 52.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:05:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.4 | 56.9 | 25.3 | 57.4 | 0 | 0 | - | - | 27.1 | 52.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:10:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.3 | 57 | 25.2 | 57.5 | 0 | 0 | - | - | 27 | 52.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:15:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.3 | 57 | 25.2 | 57.5 | 0 | 0 | - | - | 27 | 52.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:20:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.3 | 57.1 | 25.2 | 57.6 | 0 | 0 | - | - | 27 | 52.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:25:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.3 | 57.1 | 25.2 | 57.6 | 0 | 0 | - | - | 26.9 | 52.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:30:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.2 | 57.1 | 25.2 | 57.7 | 0 | 0 | - | - | 26.9 | 52.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:35:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.2 | 57.2 | 25.1 | 57.7 | 0 | 0 | - | - | 26.9 | 52.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:40:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.2 | 57.2 | 25.2 | 57.7 | 0 | 0 | - | - | 26.9 | 52.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:45:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.2 | 57.2 | 25.1 | 57.7 | 0 | 0 | - | - | 26.9 | 52.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:50:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.2 | 57.2 | 25.1 | 57.7 | 0 | 0 | - | - | 26.8 | 53 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 04:55:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.2 | 57.3 | 25 | 57.8 | 0 | 0 | - | - | 26.8 | 53 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:00:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.3 | 25.1 | 57.8 | 0 | 0 | - | - | 26.8 | 53 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:05:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.3 | 25.1 | 57.8 | 0 | 0 | - | - | 26.8 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:10:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.4 | 25.1 | 57.8 | 0 | 0 | - | - | 26.8 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:15:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.3 | 25.1 | 57.8 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:20:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.4 | 25 | 57.8 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:25:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.4 | 25 | 57.8 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:30:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.4 | 25 | 57.9 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:35:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.4 | 25 | 57.9 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:40:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.4 | 25 | 57.8 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:45:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.4 | 25 | 57.8 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:50:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.4 | 25 | 57.8 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 05:55:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.1 | 57.4 | 25 | 57.8 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:00:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.2 | 57.3 | 25.1 | 57.8 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:05:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.2 | 57.3 | 25.1 | 57.8 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:10:00 | 0 | 0 | 822854.18 | 800472.1 | 0 | 0 | 0 | 0 | - | 183 | 25.2 | 57.3 | 25.1 | 57.7 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:15:00 | 0 | 0 | 822854.18 | 800472.1 | 0.04 | 3808.166 | 619.932 | -0.003 | 15 | 183 | 25.3 | 57.2 | 25.2 | 57.6 | 0 | 0 | - | - | 26.7 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24 | 24.2 | 28.7 | 1.51 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:20:00 | 0 | 0 | 822854.18 | 800472.1 | 0.16 | 3786.024 | 642.072 | -0.003 | 15 | 183 | 25.3 | 57 | 25.2 | 57.5 | 0 | 0 | - | - | 26.8 | 53 | 0 | 0 | 0 | 0 | 26.2 | 26.5 | 26.4 | 1.49 | 2.4 | 2 | 0 | 25.9 | 26.5 | 26.5 | 1.51 | 2.1 | 2 | 23.9 | 24.1 | 28.2 | 1.5 | 1.5 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:25:00 | 0 | 0 | 822854.18 | 800472.1 | 0.28 | 3778.644 | 649.452 | -2.521 | 15 | 183 | 25.4 | 56.9 | 25.3 | 57.4 | 0 | 0 | - | - | 26.9 | 53 | 0 | 0 | 0 | 0 | 26.2 | 26.6 | 26.6 | 1.49 | 2.5 | 2.1 | 0 | 26 | 26.6 | 26.7 | 1.51 | 2.2 | 2.1 | 23.9 | 24.1 | 27.8 | 1.51 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:30:00 | 3.2 | 0.2 | 822857.62 | 800472.3 | 0.41 | 3778.644 | 649.452 | 109.86 | 15 | 183 | 25.5 | 56.8 | 25.4 | 57.3 | 0 | 0 | - | - | 27 | 52.9 | 0 | 0 | 0 | 0 | 26.4 | 26.7 | 26.7 | 1.49 | 2.7 | 2.2 | 0 | 26.1 | 26.6 | 26.8 | 1.51 | 2.2 | 2.2 | 23.9 | 24.1 | 27.5 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:35:00 | 16.34 | 0.2 | 822870.78 | 800472.3 | 0.53 | 3778.644 | 649.452 | 215.974 | 15 | 183 | 25.5 | 56.8 | 25.4 | 57.2 | 0 | 0 | - | - | 27.1 | 52.8 | 0 | 0 | 0 | 0 | 26.5 | 26.8 | 26.7 | 1.49 | 2.7 | 2.3 | 0 | 26.2 | 26.7 | 26.9 | 1.51 | 2.3 | 2.2 | 23.9 | 24.1 | 27.4 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:40:00 | 36.92 | 0.2 | 822891.52 | 800472.3 | 0.65 | 3778.644 | 649.452 | 267.125 | 16 | 183 | 25.6 | 56.7 | 25.5 | 57.1 | 0 | 0 | - | - | 27.2 | 52.6 | 0 | 0 | 0 | 0 | 26.6 | 26.9 | 26.8 | 1.49 | 2.9 | 2.5 | 0 | 26.2 | 26.7 | 27 | 1.51 | 2.3 | 2.3 | 24 | 24.1 | 27.5 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:45:00 | 70.7 | 0.2 | 822925.5 | 800472.3 | 0.79 | 3741.744 | 686.352 | 421.801 | 17 | 183 | 25.7 | 56.7 | 25.6 | 57 | 0 | 0 | - | - | 27.3 | 52.6 | 0 | 0 | 0 | 0 | 26.7 | 27.1 | 26.8 | 1.49 | 3 | 2.5 | 0 | 26.3 | 26.9 | 27 | 1.51 | 2.4 | 2.3 | 24 | 24.1 | 30.5 | 1.5 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:50:00 | 107.48 | 0.2 | 822961.84 | 800472.3 | 0.91 | 3697.464 | 730.633 | 358.714 | 17 | 183 | 25.9 | 56.5 | 25.8 | 56.8 | 0 | 0 | - | - | 27.5 | 52.4 | 0 | 0 | 0 | 0 | 26.9 | 27.3 | 27.1 | 1.49 | 3.2 | 2.7 | 0 | 26.5 | 27 | 27.2 | 1.51 | 2.6 | 2.5 | 23.9 | 24.1 | 33.3 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 06:55:00 | 136.48 | 0.2 | 822991.12 | 800472.3 | 1.03 | 3682.704 | 745.393 | 244.935 | 18 | 183 | 26.1 | 56.1 | 26.1 | 56.4 | 0 | 0 | - | - | 27.9 | 52 | 0 | 0 | 0 | 0 | 27.3 | 27.7 | 27.6 | 1.49 | 3.6 | 3.1 | 0 | 26.7 | 27.4 | 27.9 | 1.51 | 2.9 | 2.7 | 24 | 24.2 | 34.7 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:00:00 | 144.8 | 0.68 | 822998.98 | 800472.98 | 1.14 | 3682.704 | 745.393 | -78.098 | 18 | 184 | 26.4 | 55.7 | 26.4 | 55.9 | 0 | 0 | - | - | 28.4 | 51.4 | 0 | 0 | 0 | 0 | 27.6 | 28 | 28 | 1.49 | 4 | 3.4 | 0 | 27 | 27.6 | 28.4 | 1.51 | 3.1 | 2.9 | 24 | 24.2 | 34.6 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:05:00 | 144.8 | 24.64 | 822998.98 | 800497.42 | 1.26 | 3697.464 | 730.633 | -461.564 | 18 | 184 | 26.6 | 55.3 | 26.6 | 55.5 | 0 | 0 | - | - | 29 | 50.8 | 0 | 0 | 0 | 0 | 27.9 | 28.3 | 28.3 | 1.5 | 4.2 | 3.6 | 0 | 27.2 | 27.9 | 29.1 | 1.51 | 3.4 | 3.2 | 24.1 | 24.2 | 34.2 | 1.51 | 1.5 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:10:00 | 144.8 | 85.62 | 822998.98 | 800558.8 | 1.37 | 3741.744 | 686.352 | -996.437 | 17 | 184 | 26.8 | 55 | 26.8 | 55.2 | 0 | 0 | - | - | 29.5 | 50.2 | 0 | 0 | 0 | 0 | 28.2 | 28.6 | 28.6 | 1.5 | 4.5 | 3.9 | 0 | 27.5 | 28.1 | 29.5 | 1.51 | 3.5 | 3.4 | 24.1 | 24.3 | 32.6 | 1.51 | 1.51 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:15:00 | 144.8 | 147.76 | 822998.98 | 800621.08 | 1.49 | 3822.927 | 605.172 | -650.006 | 14 | 184 | 27 | 54.8 | 27 | 55 | 0 | 0 | - | - | 29.9 | 49.7 | 0 | 0 | 0 | 0 | 28.5 | 28.9 | 28.9 | 1.5 | 4.7 | 4.1 | 0 | 27.7 | 28.3 | 29.9 | 1.52 | 3.7 | 3.6 | 24.2 | 24.4 | 31.3 | 1.52 | 1.51 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:20:00 | 146.56 | 167.82 | 823000.82 | 800639.92 | 1.6 | 3859.829 | 568.272 | -5.041 | 14 | 184 | 27.2 | 54.6 | 27.2 | 54.8 | 0 | 0 | - | - | 30.1 | 49.3 | 0 | 0 | 0 | 0 | 28.6 | 29 | 29 | 1.51 | 4.6 | 4.1 | 0 | 27.9 | 28.4 | 30.1 | 1.52 | 3.7 | 3.6 | 24.4 | 24.5 | 32.9 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:25:00 | 146.82 | 178.94 | 823001 | 800651.44 | 1.7 | 3859.829 | 568.272 | -494.473 | 14 | 184 | 27.4 | 54.3 | 27.3 | 54.7 | 0 | 0 | - | - | 30.4 | 49 | 0 | 0 | 0 | 0 | 28.9 | 29.2 | 29.3 | 1.51 | 4.7 | 4.3 | 0 | 28.1 | 28.6 | 30.2 | 1.53 | 3.8 | 3.7 | 24.4 | 24.6 | 32.4 | 1.53 | 1.52 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:30:00 | 146.82 | 209.42 | 823001 | 800681.94 | 1.8 | 3904.11 | 523.99 | -176.32 | 13 | 184 | 27.4 | 54.3 | 27.4 | 54.5 | 0 | 0 | - | - | 30.7 | 48.7 | 0 | 0 | 0 | 0 | 29.1 | 29.4 | 29.4 | 1.51 | 4.8 | 4.4 | 0 | 28.3 | 28.8 | 30.5 | 1.53 | 3.9 | 3.8 | 24.5 | 24.7 | 32.4 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:35:00 | 156.7 | 211.68 | 823011.12 | 800683.78 | 1.89 | 3896.73 | 531.371 | 241.722 | 13 | 184 | 27.6 | 54.1 | 27.5 | 54.5 | 0 | 0 | - | - | 30.9 | 48.5 | 0 | 0 | 0 | 0 | 29.2 | 29.6 | 29.6 | 1.52 | 4.9 | 4.4 | 0 | 28.5 | 29 | 30.7 | 1.54 | 3.9 | 3.9 | 24.6 | 24.7 | 33.7 | 1.53 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:40:00 | 172.76 | 211.68 | 823027.06 | 800683.78 | 1.99 | 3881.969 | 546.132 | 81.033 | 13 | 184 | 27.7 | 54 | 27.6 | 54.4 | 0 | 0 | - | - | 31.2 | 48.3 | 0 | 0 | 0 | 0 | 29.4 | 29.7 | 29.7 | 1.52 | 5 | 4.5 | 0 | 28.6 | 29.2 | 30.9 | 1.54 | 4 | 3.9 | 24.6 | 24.8 | 36.1 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:45:00 | 177.46 | 211.68 | 823032.06 | 800683.78 | 2.08 | 3867.209 | 560.892 | 188.499 | 14 | 184 | 27.8 | 53.8 | 27.7 | 54.3 | 0 | 0 | - | - | 31.5 | 48 | 0 | 0 | 0 | 0 | 29.6 | 30 | 30 | 1.52 | 5.3 | 4.7 | 0 | 28.8 | 29.4 | 31.2 | 1.54 | 4.3 | 4.2 | 24.7 | 24.8 | 37.5 | 1.54 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:50:00 | 205.12 | 211.68 | 823059.5 | 800683.78 | 2.17 | 3845.069 | 583.032 | 195.1 | 14 | 184 | 28 | 53.6 | 27.9 | 54 | 0 | 0 | - | - | 32 | 47.7 | 0 | 0 | 0 | 0 | 29.9 | 30.4 | 30.4 | 1.52 | 5.6 | 5 | 0 | 29.1 | 29.7 | 31.8 | 1.54 | 4.5 | 4.3 | 24.7 | 24.8 | 38.3 | 1.54 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 07:55:00 | 243.5 | 211.68 | 823098.38 | 800683.78 | 2.27 | 3800.784 | 627.312 | 308.469 | 15 | 184 | 28.2 | 53.5 | 28.1 | 53.8 | 0 | 0 | - | - | 32.4 | 47.2 | 0 | 0 | 0 | 0 | 30.3 | 30.7 | 30.8 | 1.52 | 6 | 5.4 | 0 | 29.4 | 30 | 32.3 | 1.54 | 4.9 | 4.7 | 24.7 | 24.8 | 38.8 | 1.54 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:00:00 | 257.28 | 214.5 | 823111.46 | 800687.48 | 2.37 | 3800.784 | 627.312 | -272.407 | 15 | 184 | 28.4 | 53.1 | 28.3 | 53.6 | 0 | 0 | - | - | 33 | 46.8 | 0 | 0 | 0 | 0 | 30.6 | 31 | 31.2 | 1.52 | 6.3 | 5.7 | 0 | 29.7 | 30.3 | 32.8 | 1.54 | 5.2 | 5 | 24.7 | 24.8 | 39.5 | 1.54 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:05:00 | 257.28 | 238.54 | 823111.46 | 800711.12 | 2.46 | 3815.546 | 612.552 | -213.496 | 15 | 184 | 28.6 | 52.8 | 28.5 | 53.3 | 0 | 0 | - | - | 33.5 | 46.3 | 0 | 0 | 0 | 0 | 31 | 31.5 | 31.7 | 1.53 | 6.7 | 6.1 | 0 | 30 | 30.7 | 33.4 | 1.54 | 5.5 | 5.2 | 24.7 | 24.9 | 39.8 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:10:00 | 257.28 | 255.2 | 823111.46 | 800727.32 | 2.55 | 3845.069 | 583.032 | -4.587 | 14 | 184 | 28.9 | 52.5 | 28.7 | 53.1 | 0 | 0 | - | - | 34.1 | 45.7 | 0 | 0 | 0 | 0 | 31.3 | 31.8 | 32 | 1.53 | 6.9 | 6.3 | 0 | 30.3 | 31 | 33.8 | 1.54 | 5.7 | 5.5 | 24.8 | 24.9 | 39.6 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:15:00 | 257.28 | 256.54 | 823111.46 | 800728.64 | 2.64 | 3845.069 | 583.032 | 0.905 | 14 | 184 | 29.2 | 52 | 28.8 | 52.9 | 0 | 0 | - | - | 34.6 | 45.2 | 0 | 0 | 0 | 0 | 31.7 | 31.9 | 32.4 | 1.53 | 7 | 6.6 | 0 | 30.6 | 31.2 | 34.2 | 1.55 | 5.9 | 5.7 | 24.8 | 25 | 39.2 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:20:00 | 257.28 | 263.64 | 823111.46 | 800735.92 | 2.72 | 3852.449 | 575.652 | -232.565 | 14 | 184 | 29.4 | 51.7 | 29 | 52.6 | 0 | 0 | - | - | 35 | 44.7 | 0 | 0 | 0 | 0 | 31.9 | 31.8 | 32.6 | 1.53 | 6.9 | 6.9 | 0 | 30.9 | 31.4 | 34.5 | 1.54 | 6.1 | 6 | 24.8 | 25 | 39.2 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:25:00 | 257.28 | 282.6 | 823111.46 | 800754.9 | 2.8 | 3859.829 | 568.272 | -100.703 | 14 | 184 | 29.6 | 51.5 | 29.2 | 52.3 | 0 | 0 | - | - | 35.3 | 44.4 | 0 | 0 | 0 | 0 | 32.1 | 31.9 | 32.9 | 1.53 | 6.9 | 7.1 | 0 | 31.1 | 31.6 | 34.8 | 1.54 | 6.3 | 6.3 | 24.9 | 25.1 | 37.9 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:30:00 | 259.08 | 287.94 | 823113.26 | 800760.26 | 2.88 | 3859.829 | 568.272 | -204.682 | 13 | 184 | 29.9 | 51.1 | 29.4 | 52.1 | 0 | 0 | - | - | 35.6 | 44.1 | 0 | 0 | 0 | 0 | 32.2 | 31.7 | 32.9 | 1.53 | 6.8 | 7.2 | 0 | 31.2 | 31.6 | 34.9 | 1.54 | 6.3 | 6.4 | 24.9 | 25.1 | 37.1 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:35:00 | 259.08 | 314.26 | 823113.26 | 800786.46 | 2.97 | 3918.87 | 509.229 | -203.183 | 12 | 184 | 30.1 | 50.9 | 29.7 | 51.8 | 0 | 0 | - | - | 35.7 | 44 | 0 | 0 | 0 | 0 | 32.3 | 31.7 | 33 | 1.53 | 6.8 | 7.2 | 0 | 31.4 | 31.6 | 34.9 | 1.55 | 6.3 | 6.6 | 25 | 25.1 | 35.9 | 1.54 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:40:00 | 259.08 | 324.76 | 823113.26 | 800797.02 | 3.05 | 3926.25 | 501.848 | -16.038 | 12 | 184 | 30.4 | 50.6 | 29.9 | 51.6 | 0 | 0 | - | - | 35.8 | 43.9 | 0 | 0 | 0 | 0 | 32.4 | 31.6 | 33 | 1.53 | 6.7 | 7.3 | 0 | 31.5 | 31.6 | 34.9 | 1.55 | 6.3 | 6.7 | 25 | 25.2 | 35.6 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:45:00 | 264.5 | 325.58 | 823118.68 | 800797.68 | 3.13 | 3926.25 | 501.848 | 258.378 | 12 | 184 | 30.6 | 50.3 | 30 | 51.4 | 0 | 0 | - | - | 35.8 | 43.9 | 0 | 0 | 0 | 0 | 32.4 | 31.5 | 33 | 1.53 | 6.7 | 7.4 | 0 | 31.6 | 31.6 | 34.7 | 1.54 | 6.3 | 6.8 | 25.1 | 25.2 | 36.1 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:50:00 | 289.58 | 325.58 | 823144.16 | 800797.68 | 3.21 | 3881.97 | 546.132 | 398.087 | 13 | 184 | 30.8 | 50 | 30.3 | 51.1 | 0 | 0 | - | - | 35.8 | 44 | 0 | 0 | 0 | 0 | 32.5 | 31.4 | 33.1 | 1.53 | 6.5 | 7.5 | 0 | 31.7 | 31.6 | 34.6 | 1.55 | 6.2 | 6.8 | 25.1 | 25.2 | 36.9 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 08:55:00 | 331.98 | 325.58 | 823187.54 | 800797.68 | 3.3 | 3837.688 | 590.412 | 606.719 | 14 | 184 | 31.2 | 49.6 | 30.6 | 50.7 | 0 | 0 | - | - | 35.9 | 43.9 | 0 | 0 | 0 | 0 | 32.6 | 31.4 | 33.3 | 1.53 | 6.5 | 7.6 | 0 | 31.9 | 31.6 | 34.6 | 1.55 | 6.3 | 7 | 25.1 | 25.2 | 37.9 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:00:00 | 382.66 | 325.58 | 823238.06 | 800797.68 | 3.39 | 3793.404 | 634.692 | 344.17 | 15 | 184 | 31.5 | 49.2 | 30.9 | 50.5 | 0 | 0 | - | - | 36.1 | 43.9 | 0 | 0 | 0 | 0 | 32.8 | 31.5 | 33.5 | 1.53 | 6.6 | 7.7 | 0 | 32 | 31.7 | 34.8 | 1.55 | 6.4 | 7.1 | 25.1 | 25.2 | 38.4 | 1.54 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:05:00 | 401.3 | 325.58 | 823255.5 | 800797.68 | 3.47 | 3778.644 | 649.452 | 27.006 | 16 | 184 | 31.7 | 48.9 | 31 | 50.2 | 0 | 0 | - | - | 36.3 | 43.8 | 0 | 0 | 0 | 0 | 32.9 | 31.6 | 33.6 | 1.53 | 6.7 | 7.9 | 0 | 32.2 | 31.8 | 35 | 1.55 | 6.5 | 7.3 | 25.1 | 25.3 | 38.7 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:10:00 | 402.64 | 330 | 823257 | 800802.1 | 3.55 | 3793.404 | 634.692 | 144.01 | 16 | 184 | 32.1 | 48.6 | 31.1 | 50.2 | 0 | 0 | - | - | 36.5 | 43.5 | 0 | 0 | 0 | 0 | 33.1 | 31.7 | 33.8 | 1.53 | 6.7 | 8 | 0 | 32.4 | 31.9 | 35.2 | 1.55 | 6.6 | 7.4 | 25.2 | 25.3 | 38.1 | 1.55 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:15:00 | 431.76 | 330 | 823287.26 | 800802.1 | 3.64 | 3749.124 | 678.972 | 660.462 | 16 | 184 | 32.3 | 48.3 | 31.4 | 49.9 | 0 | 0 | - | - | 36.7 | 43.4 | 0 | 0 | 0 | 0 | 33.1 | 31.7 | 33.9 | 1.53 | 6.7 | 8 | 0 | 32.4 | 31.9 | 35.3 | 1.55 | 6.5 | 7.5 | 25.2 | 25.3 | 39.3 | 1.55 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:20:00 | 489.06 | 330 | 823343.58 | 800802.1 | 3.73 | 3704.844 | 723.252 | 668.424 | 18 | 184 | 32.5 | 48.1 | 31.6 | 49.7 | 0 | 0 | - | - | 36.9 | 43.3 | 0 | 0 | 0 | 0 | 33.3 | 31.8 | 34.1 | 1.53 | 6.7 | 8.2 | 0 | 32.6 | 31.9 | 35.5 | 1.55 | 6.5 | 7.6 | 25.3 | 25.4 | 38.2 | 1.55 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:25:00 | 546.32 | 330 | 823401.56 | 800802.1 | 3.82 | 3638.424 | 789.677 | 509.879 | 19 | 184 | 32.8 | 47.8 | 31.8 | 49.5 | 0 | 0 | - | - | 37.1 | 43.1 | 0 | 0 | 0 | 0 | 33.4 | 31.8 | 34.3 | 1.53 | 6.8 | 8.2 | 0 | 32.8 | 32 | 35.6 | 1.55 | 6.5 | 7.7 | 25.3 | 25.4 | 37.7 | 1.55 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:30:00 | 581.34 | 330 | 823435.88 | 800802.1 | 3.91 | 3601.52 | 826.578 | 233.121 | 20 | 184 | 32.9 | 47.7 | 31.9 | 49.4 | 0 | 0 | - | - | 37.2 | 43 | 0 | 0 | 0 | 0 | 33.5 | 31.9 | 34.3 | 1.53 | 6.9 | 8.3 | 0 | 32.9 | 32 | 35.7 | 1.55 | 6.6 | 7.8 | 25.3 | 25.5 | 37.5 | 1.55 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:35:00 | 594.68 | 330.28 | 823448.9 | 800802.4 | 4 | 3586.759 | 841.338 | 13.459 | 20 | 184 | 33.1 | 47.5 | 31.9 | 49.4 | 0 | 0 | - | - | 37.3 | 42.9 | 0 | 0 | 0 | 0 | 33.6 | 31.9 | 34.4 | 1.54 | 6.9 | 8.4 | 0 | 33 | 32.1 | 35.8 | 1.55 | 6.5 | 7.9 | 25.4 | 25.5 | 38 | 1.55 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:40:00 | 594.9 | 343.58 | 823449.08 | 800815.8 | 4.08 | 3601.52 | 826.578 | -82.643 | 20 | 184 | 33.3 | 47.4 | 32.1 | 49.3 | 0 | 0 | - | - | 37.4 | 42.7 | 0 | 0 | 0 | 0 | 33.7 | 32 | 34.5 | 1.54 | 6.8 | 8.4 | 0 | 33.1 | 32.1 | 35.8 | 1.55 | 6.6 | 8 | 25.4 | 25.6 | 37.5 | 1.55 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:45:00 | 595.3 | 351.4 | 823449.48 | 800823.62 | 4.16 | 3608.901 | 819.198 | -71.324 | 20 | 184 | 33.4 | 47.2 | 32.2 | 49.1 | 0 | 0 | - | - | 37.5 | 42.7 | 0 | 0 | 0 | 0 | 33.8 | 32 | 34.6 | 1.54 | 6.8 | 8.5 | 0 | 33.1 | 32.1 | 35.9 | 1.56 | 6.6 | 8 | 25.5 | 25.6 | 36.1 | 1.55 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:50:00 | 595.3 | 367.88 | 823449.48 | 800839.98 | 4.24 | 3631.043 | 797.057 | -208.348 | 19 | 184 | 33.5 | 47.1 | 32.4 | 49 | 0 | 0 | - | - | 37.5 | 42.7 | 0 | 0 | 0 | 0 | 33.7 | 31.9 | 34.6 | 1.54 | 6.7 | 8.4 | 0 | 33.2 | 32.1 | 35.9 | 1.56 | 6.4 | 8 | 25.5 | 25.7 | 35.7 | 1.55 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 09:55:00 | 611.32 | 370.28 | 823466.48 | 800842.38 | 4.32 | 3616.282 | 811.818 | 551.272 | 20 | 184 | 33.6 | 47.1 | 32.5 | 48.9 | 0 | 0 | - | - | 37.5 | 42.7 | 0 | 0 | 0 | 0 | 33.8 | 31.9 | 34.5 | 1.54 | 6.7 | 8.5 | 0 | 33.2 | 32.1 | 35.6 | 1.56 | 6.4 | 8.1 | 25.5 | 25.7 | 34.9 | 1.55 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:00:00 | 641.34 | 370.3 | 823495.68 | 800842.4 | 4.41 | 3586.759 | 841.338 | 7.08 | 20 | 184 | 33.7 | 47 | 32.5 | 48.9 | 0 | 0 | - | - | 37.5 | 42.8 | 0 | 0 | 0 | 0 | 33.7 | 31.8 | 34.4 | 1.54 | 6.5 | 8.4 | 0 | 33.2 | 31.9 | 35.6 | 1.56 | 6.3 | 8 | 25.6 | 25.7 | 34.7 | 1.56 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:05:00 | 650.74 | 370.3 | 823505.28 | 800842.4 | 4.49 | 3579.379 | 848.718 | 381.384 | 20 | 184 | 33.7 | 47 | 32.5 | 49 | 0 | 0 | - | - | 37.4 | 43 | 0 | 0 | 0 | 0 | 33.7 | 31.7 | 34.4 | 1.54 | 6.5 | 8.3 | 0 | 33.2 | 31.9 | 35.4 | 1.56 | 6.3 | 8 | 25.6 | 25.7 | 34.7 | 1.56 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:10:00 | 682.12 | 370.3 | 823536.82 | 800842.4 | 4.57 | 3542.478 | 885.618 | 318.726 | 21 | 184 | 33.7 | 47 | 32.6 | 48.9 | 0 | 0 | - | - | 37.2 | 43.1 | 0 | 0 | 0 | 0 | 33.7 | 31.7 | 34.4 | 1.54 | 6.4 | 8.4 | 0 | 33.3 | 31.8 | 35.3 | 1.56 | 6.2 | 8 | 25.6 | 25.8 | 34.7 | 1.56 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:15:00 | 716.4 | 370.3 | 823570.82 | 800842.4 | 4.66 | 3505.578 | 922.518 | 454.67 | 22 | 184 | 34 | 46.8 | 32.3 | 49.3 | 0 | 0 | - | - | 37.1 | 43.2 | 0 | 0 | 0 | 0 | 33.7 | 31.7 | 34.2 | 1.54 | 6.3 | 8.3 | 0 | 33.2 | 31.8 | 35.1 | 1.56 | 6.1 | 8 | 25.6 | 25.8 | 35 | 1.56 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:20:00 | 764.66 | 370.3 | 823619.84 | 800842.4 | 4.76 | 3446.538 | 981.558 | 545.012 | 23 | 184 | 34.6 | 46.3 | 31.9 | 50.1 | 0 | 0 | - | - | 37.1 | 43.3 | 0 | 0 | 0 | 0 | 33.7 | 31.6 | 34.2 | 1.55 | 6.3 | 8.3 | 0 | 33.3 | 31.8 | 35.1 | 1.56 | 6.1 | 8 | 25.7 | 25.8 | 35.6 | 1.56 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:25:00 | 802.18 | 370.3 | 823656.56 | 800842.4 | 4.85 | 3417.018 | 1011.078 | 382.696 | 24 | 184 | 34.6 | 46.1 | 32.1 | 49.9 | 0 | 0 | - | - | 37 | 43.4 | 0 | 0 | 0 | 0 | 33.8 | 31.6 | 34.3 | 1.54 | 6.3 | 8.4 | 0 | 33.3 | 31.8 | 35 | 1.56 | 6.1 | 8 | 25.7 | 25.8 | 35.9 | 1.56 | 1.56 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:30:00 | 819.82 | 370.3 | 823674.08 | 800842.4 | 4.93 | 3394.878 | 1033.22 | 28.28 | 25 | 184 | 34.2 | 46.7 | 32.4 | 49.4 | 0 | 0 | - | - | 37 | 43.5 | 0 | 0 | 0 | 0 | 33.9 | 31.7 | 34.4 | 1.55 | 6.3 | 8.4 | 0 | 33.4 | 31.9 | 35.1 | 1.57 | 6.1 | 8.1 | 25.7 | 25.9 | 35.8 | 1.56 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:35:00 | 830.34 | 370.3 | 823684.56 | 800842.4 | 5.02 | 3394.878 | 1033.22 | 82.162 | 25 | 184 | 34.2 | 46.8 | 32.6 | 49.2 | 0 | 0 | - | - | 37.1 | 43.4 | 0 | 0 | 0 | 0 | 33.9 | 31.8 | 34.4 | 1.55 | 6.3 | 8.4 | 0 | 33.4 | 31.9 | 35.2 | 1.57 | 6.1 | 8.1 | 25.8 | 25.9 | 36.1 | 1.56 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:40:00 | 844.16 | 370.3 | 823698.54 | 800842.4 | 5.1 | 3380.117 | 1047.981 | 114.135 | 25 | 184 | 34.4 | 46.6 | 32.8 | 49 | 0 | 0 | - | - | 37.1 | 43.4 | 0 | 0 | 0 | 0 | 33.9 | 31.8 | 34.4 | 1.55 | 6.3 | 8.4 | 0 | 33.5 | 32 | 35.2 | 1.57 | 6.2 | 8.1 | 25.8 | 26 | 35.7 | 1.57 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:45:00 | 846.92 | 376.82 | 823701.1 | 800849.22 | 5.18 | 3380.117 | 1047.981 | -181.437 | 25 | 184 | 34.5 | 46.5 | 33 | 48.8 | 0 | 0 | - | - | 37.2 | 43.3 | 0 | 0 | 0 | 0 | 34 | 31.8 | 34.5 | 1.55 | 6.4 | 8.4 | 0 | 33.6 | 32 | 35.3 | 1.57 | 6.2 | 8.1 | 25.8 | 26 | 35.6 | 1.56 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:50:00 | 858.16 | 379.62 | 823712.56 | 800851.72 | 5.26 | 3365.357 | 1062.743 | 417.287 | 26 | 184 | 34.7 | 46.4 | 33.2 | 48.6 | 0 | 0 | - | - | 37.2 | 43.3 | 0 | 0 | 0 | 0 | 34.1 | 31.9 | 34.6 | 1.55 | 6.4 | 8.5 | 0 | 33.6 | 32.1 | 35.3 | 1.57 | 6.1 | 8.1 | 25.9 | 26 | 35.2 | 1.57 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 10:55:00 | 893.98 | 379.62 | 823748.58 | 800851.72 | 5.36 | 3328.455 | 1099.644 | 274.484 | 27 | 184 | 34.8 | 46.2 | 33.4 | 48.5 | 0 | 0 | - | - | 37.2 | 43.2 | 0 | 0 | 0 | 0 | 34.1 | 31.9 | 34.6 | 1.55 | 6.4 | 8.5 | 0 | 33.7 | 32.1 | 35.4 | 1.57 | 6.2 | 8.2 | 25.9 | 26.1 | 35.1 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:00:00 | 917.9 | 379.62 | 823773.38 | 800851.72 | 5.45 | 3276.792 | 1151.304 | 446.638 | 27 | 184 | 34.8 | 46.2 | 33.4 | 48.4 | 0 | 0 | - | - | 37.3 | 43.3 | 0 | 0 | 0 | 0 | 34.2 | 31.9 | 34.7 | 1.56 | 6.3 | 8.5 | 0 | 33.7 | 32.2 | 35.4 | 1.57 | 6.2 | 8.2 | 25.9 | 26.1 | 35.1 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:05:00 | 983.82 | 379.62 | 823838.46 | 800851.72 | 5.56 | 3232.512 | 1195.584 | 857.332 | 29 | 184 | 34.8 | 46.2 | 33.4 | 48.4 | 0 | 0 | - | - | 37.3 | 43.3 | 0 | 0 | 0 | 0 | 34.3 | 32 | 34.8 | 1.56 | 6.4 | 8.6 | 0 | 33.8 | 32.2 | 35.4 | 1.57 | 6.2 | 8.3 | 26 | 26.1 | 34.9 | 1.57 | 1.57 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:10:00 | 1047.08 | 379.62 | 823901.3 | 800851.74 | 5.67 | 3158.712 | 1269.387 | -52.464 | 30 | 184 | 34.9 | 46.2 | 33.4 | 48.5 | 0 | 0 | - | - | 37.2 | 43.3 | 0 | 0 | 0 | 0 | 34.2 | 32 | 34.7 | 1.56 | 6.4 | 8.5 | 0 | 33.9 | 32.3 | 35.4 | 1.58 | 6.2 | 8.3 | 26.1 | 26.2 | 35.1 | 1.57 | 1.57 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:15:00 | 1057.68 | 380.62 | 823912.28 | 800852.72 | 5.77 | 3143.952 | 1284.148 | 230.894 | 30 | 184 | 35 | 46.2 | 33.4 | 48.7 | 0 | 0 | - | - | 37.2 | 43.3 | 0 | 0 | 0 | 0 | 34.3 | 32 | 34.8 | 1.56 | 6.3 | 8.5 | 0 | 33.9 | 32.3 | 35.4 | 1.58 | 6.2 | 8.2 | 26.1 | 26.3 | 34.9 | 1.58 | 1.57 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:20:00 | 1078.34 | 380.62 | 823932.66 | 800852.72 | 5.87 | 3136.571 | 1291.528 | 68.437 | 31 | 184 | 35 | 46.2 | 33.5 | 48.6 | 0 | 0 | - | - | 37.3 | 43.3 | 0 | 0 | 0 | 0 | 34.4 | 32.1 | 34.9 | 1.56 | 6.3 | 8.6 | 0 | 34 | 32.4 | 35.4 | 1.58 | 6.2 | 8.3 | 26.2 | 26.4 | 34.8 | 1.58 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:25:00 | 1082.8 | 381.6 | 823937.22 | 800853.7 | 5.97 | 3129.191 | 1298.909 | 137.075 | 31 | 184 | 35.2 | 45.9 | 33.5 | 48.5 | 0 | 0 | - | - | 37.3 | 43.4 | 0 | 0 | 0 | 0 | 34.4 | 32.1 | 34.9 | 1.56 | 6.3 | 8.6 | 0 | 33.9 | 32.4 | 35.4 | 1.58 | 6.2 | 8.3 | 26.3 | 26.4 | 35.3 | 1.58 | 1.58 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:30:00 | 1120.2 | 381.6 | 823975.66 | 800853.7 | 6.09 | 3084.909 | 1343.19 | 888.186 | 32 | 184 | 35.4 | 45.8 | 33.7 | 48.4 | 0 | 0 | - | - | 37.4 | 43.3 | 0 | 0 | 0 | 0 | 34.4 | 32.1 | 34.9 | 1.56 | 6.3 | 8.5 | 0 | 34 | 32.4 | 35.4 | 1.58 | 6.2 | 8.2 | 26.3 | 26.4 | 35.5 | 1.58 | 1.58 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:35:00 | 1201.82 | 381.6 | 824056.98 | 800853.7 | 6.2 | 2988.966 | 1439.13 | 949.098 | 34 | 184 | 35.5 | 45.7 | 34 | 48.2 | 0 | 0 | - | - | 37.5 | 43.2 | 0 | 0 | 0 | 0 | 34.6 | 32.2 | 35 | 1.57 | 6.3 | 8.6 | 0 | 34.1 | 32.5 | 35.5 | 1.59 | 6.2 | 8.3 | 26.4 | 26.6 | 35.6 | 1.58 | 1.58 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:40:00 | 1290.78 | 381.6 | 824147.02 | 800853.7 | 6.32 | 2885.645 | 1542.453 | 1384.79 | 36 | 184 | 35.8 | 45.5 | 34.1 | 48 | 0 | 0 | - | - | 37.5 | 43.2 | 0 | 0 | 0 | 0 | 34.7 | 32.3 | 35.2 | 1.57 | 6.4 | 8.7 | 0 | 34.2 | 32.6 | 35.6 | 1.59 | 6.3 | 8.4 | 26.6 | 26.8 | 35.2 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:45:00 | 1408.82 | 381.6 | 824265.2 | 800853.7 | 6.48 | 2767.561 | 1660.536 | 1427.922 | 39 | 184 | 36 | 45.3 | 34.4 | 47.8 | 0 | 0 | - | - | 37.6 | 43.1 | 0 | 0 | 0 | 0 | 34.7 | 32.4 | 35.2 | 1.58 | 6.3 | 8.6 | 0 | 34.3 | 32.6 | 35.7 | 1.6 | 6.2 | 8.3 | 25.3 | 27.1 | 35.7 | 2.6 | 0.79 | 2.64 | 0.95 | 170 | 169 | 2400 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:50:00 | 1535.88 | 381.6 | 824392.48 | 800853.7 | 7.45 | 2642.099 | 1785.998 | 1448.936 | 42 | 184 | 36.3 | 45 | 34.6 | 47.6 | 0 | 0 | - | - | 37.7 | 43 | 204 | 190 | 70.7 | 70.9 | 51.8 | 26.9 | 44.9 | 2.73 | 15.8 | 3.9 | 70.1 | 53.7 | 27.2 | 47.2 | 2.95 | 12.8 | 3.1 | 22.3 | 24.3 | 38.3 | 3.08 | 1.11 | 3.32 | 1.18 | 238 | 196 | 2907 | 2907
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 11:55:00 | 1657.58 | 381.6 | 824512.34 | 800853.7 | 8.53 | 2501.875 | 1926.222 | 1038.792 | 45 | 184 | 36.6 | 44.6 | 34.7 | 47.4 | 0 | 0 | - | - | 37.8 | 43 | 238 | 196 | 84 | 84 | 77.3 | 24.2 | 50.2 | 2.98 | 10.3 | 25.7 | 84.6 | 79.2 | 24.4 | 53.6 | 3.28 | 8.8 | 24 | 21.6 | 23.6 | 39.2 | 2.97 | 1.11 | 3.27 | 1.15 | 238 | 196 | 2722 | 2722
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:00:00 | 1711.48 | 381.6 | 824567.72 | 800853.7 | 9.47 | 2450.214 | 1977.883 | 434.29 | 46 | 184 | 36.7 | 44.4 | 34.9 | 47.2 | 0 | 0 | - | - | 38 | 42.8 | 238 | 196 | 81 | 81.4 | 77.5 | 23.6 | 49.1 | 2.87 | 9.7 | 27.4 | 79 | 81.4 | 23.8 | 53.2 | 3.22 | 8.8 | 27 | 21.6 | 23.6 | 38.6 | 2.82 | 1.11 | 3.15 | 1.15 | 238 | 196 | 2493 | 2485
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:05:00 | 1737.78 | 381.6 | 824592.2 | 800853.7 | 10.35 | 2428.074 | 2000.023 | 180.633 | 47 | 184 | 37.1 | 44 | 34.9 | 47.1 | 0 | 0 | - | - | 38.1 | 42.7 | 238 | 196 | 77.2 | 77.6 | 74.9 | 23.6 | 47.3 | 2.79 | 10 | 26.1 | 76 | 80 | 23.8 | 51.9 | 3.14 | 8.8 | 26.9 | 21.7 | 23.6 | 38.6 | 2.86 | 1.11 | 3.17 | 1.15 | 238 | 196 | 2454 | 2454
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:10:00 | 1743.82 | 382.64 | 824598 | 800854.98 | 11.18 | 2420.694 | 2007.403 | -173.473 | 47 | 184 | 37.2 | 43.8 | 34.8 | 47.2 | 0 | 0 | - | - | 38.3 | 42.5 | 238 | 196 | 76.7 | 77.1 | 74.8 | 23.6 | 47.4 | 2.76 | 9.9 | 26.5 | 77.1 | 79.8 | 23.9 | 51.9 | 3.13 | 8.7 | 26.8 | 21.7 | 23.6 | 35.4 | 2.8 | 1.11 | 3.09 | 1.15 | 238 | 196 | 2352 | 2352
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:15:00 | 1743.82 | 394.48 | 824598 | 800866.64 | 11.98 | 2428.074 | 2000.023 | -47.282 | 47 | 184 | 37.1 | 43.8 | 34.7 | 47.3 | 0 | 0 | - | - | 38.3 | 42.5 | 238 | 196 | 75.1 | 75 | 73.2 | 23.5 | 46.8 | 2.75 | 9.6 | 25 | 75.4 | 78.4 | 23.8 | 51.3 | 3.1 | 8.8 | 25.7 | 21.7 | 23.6 | 35 | 2.72 | 1.11 | 3.06 | 1.16 | 238 | 195 | 2275 | 2275
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:20:00 | 1751.14 | 396.04 | 824605.54 | 800868.14 | 12.75 | 2428.074 | 2000.023 | 138.526 | 47 | 184 | 37 | 43.9 | 34.6 | 47.4 | 0 | 0 | - | - | 38.4 | 42.5 | 238 | 195 | 72.6 | 72.4 | 72 | 23.4 | 45.6 | 2.66 | 9.7 | 25 | 72.4 | 77.4 | 23.7 | 50.6 | 3.03 | 8.6 | 25.8 | 21.7 | 23.5 | 37.4 | 2.74 | 1.11 | 3.06 | 1.15 | 238 | 194 | 2241 | 2241
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:25:00 | 1761.42 | 396.04 | 824615.86 | 800868.14 | 13.49 | 2413.314 | 2014.784 | 82.885 | 47 | 184 | 36.8 | 44.1 | 34.5 | 47.4 | 0 | 0 | - | - | 38.4 | 42.4 | 238 | 194 | 72.8 | 72.6 | 72 | 23.5 | 45.9 | 2.67 | 9.6 | 25 | 72 | 77.3 | 23.7 | 50.6 | 3.03 | 8.6 | 25.6 | 21.7 | 23.4 | 38.1 | 2.77 | 1.12 | 3.07 | 1.15 | 238 | 194 | 2185 | 2185
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:30:00 | 1763.6 | 402.28 | 824617.78 | 800875.02 | 14.22 | 2413.314 | 2014.784 | -351.253 | 47 | 184 | 36.7 | 44.2 | 34.5 | 47.4 | 0 | 0 | - | - | 38.4 | 42.5 | 238 | 194 | 72.9 | 72.7 | 72.1 | 23.5 | 46.3 | 2.7 | 9.3 | 24.6 | 71.8 | 77.3 | 23.7 | 50.7 | 3.04 | 8.5 | 25.5 | 21.7 | 23.4 | 37.9 | 2.69 | 1.12 | 3.02 | 1.16 | 238 | 193 | 2122 | 2122
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:35:00 | 1763.6 | 432.82 | 824617.78 | 800905.56 | 14.93 | 2435.454 | 1992.643 | -338.206 | 46 | 184 | 36.4 | 44.4 | 34.4 | 47.5 | 0 | 0 | - | - | 38.4 | 42.4 | 238 | 192 | 71.3 | 71.2 | 71 | 23.4 | 45.4 | 2.65 | 9.1 | 24.2 | 69.9 | 76.5 | 23.7 | 50.1 | 3 | 8.4 | 25.3 | 21.7 | 23.4 | 37.9 | 2.73 | 1.13 | 3.02 | 1.15 | 238 | 191 | 2053 | 2053
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:40:00 | 1763.6 | 473.22 | 824617.78 | 800946.2 | 15.6 | 2472.354 | 1955.742 | -402.05 | 45 | 184 | 36.2 | 44.6 | 34.3 | 47.6 | 0 | 0 | - | - | 38.4 | 42.4 | 238 | 190 | 71.1 | 71 | 70.9 | 23.4 | 45.8 | 2.68 | 8.9 | 23.7 | 72.4 | 76.4 | 23.7 | 50.1 | 3.01 | 8.5 | 25.1 | 21.8 | 23.4 | 38.4 | 2.69 | 1.14 | 2.97 | 1.16 | 233 | 181 | 1900 | 1902
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:45:00 | 1769.92 | 484.08 | 824624.26 | 800956.18 | 16.25 | 2501.875 | 1926.222 | 354.674 | 45 | 184 | 36.1 | 44.8 | 34 | 47.8 | 0 | 0 | - | - | 38.4 | 42.5 | 233 | 181 | 68.7 | 68.9 | 69.4 | 23.4 | 45.1 | 2.61 | 8.6 | 23.4 | 68 | 75.6 | 23.8 | 49.6 | 2.96 | 8.5 | 25 | 21.7 | 23.3 | 37.6 | 2.66 | 1.13 | 2.96 | 1.15 | 233 | 181 | 1944 | 1944
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:50:00 | 1780.54 | 495.94 | 824634.72 | 800968.92 | 16.88 | 2479.734 | 1948.362 | -438.181 | 45 | 184 | 35.9 | 44.9 | 33.9 | 47.9 | 0 | 0 | - | - | 38.4 | 42.5 | 233 | 181 | 68.7 | 68.7 | 69.1 | 23.3 | 44.6 | 2.6 | 9 | 23.2 | 67.6 | 75.5 | 23.7 | 49.2 | 2.95 | 8.8 | 25 | 21.7 | 23.2 | 38.1 | 2.69 | 1.13 | 2.97 | 1.15 | 233 | 181 | 1914 | 1914
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 12:55:00 | 1781.82 | 517.96 | 824636.14 | 800990.06 | 17.52 | 2516.636 | 1911.462 | 179.316 | 45 | 184 | 35.7 | 45.1 | 33.8 | 48 | 0 | 0 | - | - | 38.4 | 42.4 | 233 | 181 | 68.3 | 68.8 | 69.3 | 23.3 | 45.1 | 2.62 | 8.7 | 23.1 | 68.5 | 75.6 | 23.6 | 49.5 | 2.95 | 8.6 | 25 | 21.6 | 23.2 | 38.1 | 2.68 | 1.13 | 2.97 | 1.14 | 233 | 181 | 1911 | 1911
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:00:00 | 1784.96 | 527.6 | 824639.14 | 801000.66 | 18.15 | 2516.636 | 1911.462 | -344.705 | 45 | 184 | 35.6 | 45.2 | 33.6 | 48.2 | 0 | 0 | - | - | 38.4 | 42.5 | 233 | 181 | 68.6 | 68.5 | 69.2 | 23.2 | 45.2 | 2.63 | 8.6 | 22.9 | 69.6 | 75.5 | 23.4 | 49.3 | 2.95 | 8.5 | 24.9 | 21.5 | 23.1 | 38.3 | 2.7 | 1.13 | 2.98 | 1.14 | 233 | 181 | 1900 | 1900
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:05:00 | 1786.98 | 539.22 | 824641.44 | 801011.32 | 18.79 | 2546.158 | 1881.942 | 291.365 | 44 | 184 | 35.5 | 45.3 | 33.5 | 48.3 | 0 | 0 | - | - | 38.3 | 42.4 | 233 | 181 | 68.8 | 69 | 69.4 | 23.2 | 45.2 | 2.64 | 8.6 | 22.9 | 67.9 | 75.5 | 23.3 | 49.5 | 2.95 | 8.5 | 24.9 | 21.3 | 22.9 | 38.5 | 2.67 | 1.13 | 2.96 | 1.14 | 233 | 180 | 1885 | 1885
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:10:00 | 1821.34 | 539.22 | 824676.04 | 801011.32 | 19.43 | 2501.875 | 1926.222 | 331.865 | 45 | 184 | 35.4 | 45.3 | 33.4 | 48.3 | 0 | 0 | - | - | 38.3 | 42.5 | 233 | 179 | 68 | 67.9 | 69 | 22.9 | 44.7 | 2.6 | 8.5 | 23.1 | 67 | 75.2 | 23.2 | 49.1 | 2.94 | 8.5 | 24.9 | 21.2 | 22.7 | 37.9 | 2.63 | 1.12 | 2.94 | 1.13 | 233 | 179 | 1929 | 1926
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:15:00 | 1855.24 | 539.22 | 824709.64 | 801011.32 | 20.12 | 2472.354 | 1955.742 | 92.988 | 46 | 184 | 35.2 | 45.4 | 33.3 | 48.4 | 0 | 0 | - | - | 38.3 | 42.5 | 233 | 179 | 68 | 68.1 | 68.7 | 22.8 | 44.3 | 2.55 | 8.9 | 23.6 | 68.2 | 75.1 | 23.1 | 49.1 | 2.91 | 8.5 | 25.1 | 20.7 | 22.6 | 36.9 | 2.76 | 1.05 | 3.07 | 1.08 | 233 | 179 | 2400 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:20:00 | 1855.84 | 550.46 | 824710.02 | 801022.98 | 20.91 | 2472.354 | 1955.742 | -523.934 | 46 | 184 | 35.1 | 45.5 | 33.1 | 48.6 | 0 | 0 | - | - | 38.2 | 42.5 | 233 | 179 | 74.1 | 74.2 | 71.9 | 22.3 | 46.1 | 2.7 | 10.1 | 24.4 | 74.9 | 77.7 | 22.7 | 50.6 | 3.05 | 9.6 | 25.7 | 20.4 | 22 | 37.3 | 2.67 | 1.1 | 2.98 | 1.11 | 228 | 175 | 1966 | 1966
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:25:00 | 1855.84 | 606.9 | 824710.02 | 801079.46 | 21.58 | 2531.397 | 1896.702 | -141.29 | 44 | 184 | 35 | 45.5 | 33 | 48.6 | 0 | 0 | - | - | 38.2 | 42.5 | 228 | 175 | 69.6 | 69.3 | 71.1 | 22.1 | 45.1 | 2.63 | 8.6 | 24.8 | 68.8 | 77.2 | 22.3 | 49.6 | 2.95 | 8.5 | 26.7 | 20.5 | 22.1 | 37.1 | 2.68 | 1.1 | 2.97 | 1.11 | 228 | 175 | 1966 | 1966
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:30:00 | 1858.3 | 608.9 | 824712.48 | 801081 | 22.24 | 2546.158 | 1881.942 | -26.924 | 44 | 184 | 34.8 | 45.7 | 32.8 | 48.8 | 0 | 0 | - | - | 38.1 | 42.5 | 228 | 175 | 69.1 | 68.9 | 70.1 | 22.2 | 44.9 | 2.6 | 8.7 | 24.1 | 69.1 | 76.5 | 22.5 | 49.1 | 2.94 | 8.7 | 26.1 | 20.4 | 22.1 | 36.6 | 2.68 | 1.09 | 2.95 | 1.1 | 228 | 175 | 2005 | 2005
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:35:00 | 1862.46 | 610.52 | 824716.64 | 801082.62 | 22.92 | 2546.158 | 1881.942 | -108.231 | 44 | 184 | 34.7 | 45.7 | 32.6 | 48.9 | 0 | 0 | - | - | 38.1 | 42.6 | 228 | 175 | 68.7 | 68.3 | 70.1 | 22.1 | 44.7 | 2.59 | 8.9 | 24.4 | 67.9 | 76.1 | 22.4 | 49.1 | 2.91 | 8.8 | 26.2 | 20.1 | 21.7 | 34.2 | 2.68 | 1.06 | 2.95 | 1.08 | 228 | 175 | 2149 | 2149
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:40:00 | 1862.46 | 635.04 | 824716.64 | 801108.1 | 23.63 | 2560.918 | 1867.182 | -659.672 | 44 | 184 | 34.5 | 45.8 | 32.4 | 49 | 0 | 0 | - | - | 38 | 42.6 | 228 | 175 | 69.1 | 69.4 | 70.5 | 21.7 | 45 | 2.61 | 9.2 | 24.5 | 68.2 | 76.5 | 22.1 | 49.1 | 2.93 | 9.1 | 26.2 | 19.7 | 21.5 | 34.1 | 2.68 | 1.06 | 2.95 | 1.07 | 228 | 175 | 2152 | 2152
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:45:00 | 1862.46 | 699.18 | 824716.64 | 801172.26 | 24.35 | 2649.48 | 1778.618 | -909.936 | 42 | 184 | 34.3 | 45.9 | 32.3 | 49.1 | 0 | 0 | - | - | 37.9 | 42.7 | 228 | 175 | 69.7 | 69.5 | 70.9 | 21.4 | 45 | 2.62 | 9.1 | 24.6 | 70.5 | 76.6 | 21.8 | 49.1 | 2.94 | 9.1 | 26.2 | 19.4 | 21.3 | 33.4 | 2.64 | 1.05 | 2.92 | 1.06 | 228 | 175 | 2197 | 2197
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:50:00 | 1862.46 | 769.2 | 824716.64 | 801242.1 | 25.08 | 2701.14 | 1726.956 | -531.322 | 40 | 184 | 34.1 | 46.1 | 32 | 49.4 | 0 | 0 | - | - | 37.8 | 42.7 | 228 | 175 | 68.4 | 68.1 | 70.4 | 21.2 | 44.3 | 2.56 | 9.3 | 25 | 69.2 | 76.4 | 21.6 | 48.6 | 2.89 | 9 | 26.7 | 19.2 | 20.9 | 32.1 | 2.62 | 1.03 | 2.91 | 1.05 | 228 | 175 | 2272 | 2272
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 13:55:00 | 1862.46 | 788.3 | 824716.64 | 801260.54 | 25.63 | 2738.04 | 1690.056 | -150.948 | 40 | 184 | 33.8 | 46.3 | 31.7 | 49.6 | 0 | 0 | - | - | 37.6 | 42.9 | 228 | 175 | 68.1 | 68 | 70.4 | 20.8 | 44 | 2.55 | 9.4 | 25.1 | 67.2 | 76 | 21.2 | 48.4 | 2.89 | 9 | 26.4 | 20.2 | 21.3 | 32.1 | 2.7 | 1.06 | 1.96 | 1.4 | 228 | 0 | 2280 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:00:00 | 1862.46 | 817.9 | 824716.64 | 801292 | 26.04 | 2745.42 | 1682.676 | -447.539 | 39 | 184 | 33.5 | 46.6 | 31.4 | 50 | 0 | 0 | - | - | 37.4 | 43 | 228 | 0 | 59.1 | 58.9 | 71.1 | 21.6 | 45.2 | 2.64 | 9 | 24.5 | 57.7 | 40.4 | 46.5 | 36.7 | 1.85 | 24.2 | 9.1 | 20.7 | 21.9 | 31.7 | 2.71 | 1.07 | 1.42 | 1.42 | 228 | 0 | 2299 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:05:00 | 1862.46 | 844.08 | 824716.64 | 801317.6 | 26.37 | 2789.702 | 1638.396 | -450.527 | 39 | 184 | 33.2 | 46.9 | 31 | 50.4 | 0 | 0 | - | - | 37.2 | 43.2 | 228 | 0 | 58.8 | 58.7 | 71.2 | 21.8 | 45.4 | 2.65 | 9 | 24.6 | 59.8 | 38.6 | 51.4 | 33.1 | 1.43 | 29.2 | 16.4 | 21.9 | 22.1 | 31.7 | 1.93 | 1.1 | 1.42 | 1.43 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:10:00 | 1862.46 | 874.72 | 824716.64 | 801347.52 | 26.51 | 2833.984 | 1594.116 | -363.742 | 38 | 184 | 32.8 | 47.4 | 30.6 | 51 | 0 | 0 | - | - | 36.9 | 43.5 | 0 | 0 | 0 | 0 | 51.6 | 29.9 | 36.6 | 1.79 | 7.9 | 21 | 0 | 38.4 | 48.9 | 32.4 | 1.44 | 26.2 | 16 | 23.1 | 23.2 | 28.7 | 1.59 | 1.46 | 1.44 | 1.46 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:15:00 | 1872.28 | 883.2 | 824726.84 | 801355.3 | 26.65 | 2833.984 | 1594.116 | 269.635 | 38 | 184 | 32.3 | 48 | 30.2 | 51.6 | 0 | 0 | - | - | 36.5 | 43.9 | 0 | 0 | 0 | 0 | 31.1 | 43.6 | 33.4 | 1.54 | 20.3 | 5.7 | 0 | 37.2 | 42.8 | 31.6 | 1.45 | 19.7 | 14.4 | 23.4 | 23.6 | 26.7 | 1.5 | 1.48 | 1.45 | 1.47 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:20:00 | 1891.64 | 883.2 | 824745.9 | 801355.3 | 26.79 | 2789.702 | 1638.396 | 79.813 | 38 | 184 | 31.7 | 48.8 | 29.8 | 52.2 | 0 | 0 | - | - | 35.8 | 44.6 | 0 | 0 | 0 | 0 | 28.4 | 44.1 | 31.8 | 1.48 | 20.5 | 4.5 | 0 | 35.6 | 37.7 | 30.2 | 1.46 | 14.4 | 12.6 | 23.6 | 23.8 | 26.7 | 1.5 | 1.49 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:25:00 | 1899.56 | 883.42 | 824753.98 | 801355.52 | 26.93 | 2789.702 | 1638.396 | 224.284 | 39 | 184 | 31.1 | 49.6 | 29.3 | 53.1 | 0 | 0 | - | - | 34.9 | 45.5 | 0 | 0 | 0 | 0 | 28.2 | 41.6 | 30.9 | 1.48 | 17.8 | 4.1 | 0 | 33.9 | 34.7 | 29.2 | 1.47 | 11.2 | 10.7 | 23.8 | 23.9 | 25.9 | 1.5 | 1.49 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:30:00 | 1945.6 | 883.42 | 824800.74 | 801355.52 | 27.07 | 2738.04 | 1690.056 | 957.227 | 40 | 184 | 30.7 | 50.2 | 28.5 | 54.4 | 0 | 0 | - | - | 34.1 | 46.5 | 0 | 0 | 0 | 0 | 27.9 | 39.9 | 30.1 | 1.49 | 15.9 | 3.9 | 0 | 32.4 | 32.9 | 28.6 | 1.47 | 9.3 | 9.3 | 23.8 | 24 | 26.3 | 1.51 | 1.5 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:35:00 | 2026.86 | 883.42 | 824882.98 | 801355.52 | 27.21 | 2656.86 | 1771.238 | 905.239 | 42 | 184 | 30.3 | 50.8 | 28.1 | 55.1 | 0 | 0 | - | - | 33.3 | 47.4 | 0 | 0 | 0 | 0 | 27.7 | 38.7 | 29.2 | 1.49 | 14.7 | 3.6 | 0 | 31.2 | 31.4 | 28 | 1.47 | 7.8 | 8.1 | 24 | 24.1 | 26.6 | 1.51 | 1.5 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:40:00 | 2097.34 | 883.42 | 824953.72 | 801355.52 | 27.34 | 2590.438 | 1837.661 | 791.123 | 43 | 184 | 29.9 | 51.4 | 28.2 | 55 | 0 | 0 | - | - | 32.7 | 48.2 | 0 | 0 | 0 | 0 | 27.7 | 37.9 | 28.7 | 1.5 | 13.7 | 3.3 | 0 | 30.3 | 30.6 | 27.7 | 1.48 | 6.7 | 7 | 24.2 | 24.3 | 26.7 | 1.52 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:45:00 | 2152.54 | 883.42 | 825007.02 | 801355.52 | 27.48 | 2524.016 | 1904.082 | 248.329 | 45 | 184 | 29.6 | 51.9 | 28.1 | 55.2 | 0 | 0 | - | - | 32.1 | 48.8 | 0 | 0 | 0 | 0 | 27.8 | 36.6 | 28.4 | 1.51 | 12.2 | 3.2 | 0 | 29.7 | 29.8 | 27.6 | 1.48 | 5.9 | 6.2 | 24.4 | 24.6 | 26.7 | 1.53 | 1.52 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:50:00 | 2175.94 | 883.42 | 825030.72 | 801355.52 | 27.59 | 2501.874 | 1926.222 | 377.026 | 45 | 184 | 29.2 | 52.5 | 28 | 55.4 | 0 | 0 | - | - | 31.7 | 49.2 | 0 | 0 | 0 | 0 | 28 | 34.9 | 28.2 | 1.52 | 10.3 | 3.2 | 0 | 29.1 | 29.3 | 27.4 | 1.49 | 5.2 | 5.5 | 24.6 | 24.8 | 26.4 | 1.54 | 1.53 | 1.48 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 14:55:00 | 2214.26 | 883.42 | 825068.94 | 801355.52 | 27.72 | 2457.594 | 1970.502 | 311.776 | 46 | 184 | 29 | 53 | 27.9 | 55.6 | 0 | 0 | - | - | 31.4 | 49.8 | 0 | 0 | 0 | 0 | 28.1 | 33.6 | 28.1 | 1.52 | 8.7 | 3.2 | 0 | 28.7 | 29.1 | 27.3 | 1.49 | 4.8 | 5.1 | 24.7 | 24.9 | 26.7 | 1.54 | 1.54 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:00:00 | 2220.36 | 893.12 | 825074.54 | 801365.86 | 27.82 | 2457.594 | 1970.502 | -218.774 | 46 | 184 | 28.7 | 53.6 | 27.8 | 55.8 | 0 | 0 | - | - | 31.1 | 50 | 0 | 0 | 0 | 0 | 28.1 | 32.4 | 28 | 1.53 | 7.6 | 3.1 | 0 | 28.4 | 28.8 | 27.3 | 1.5 | 4.5 | 4.7 | 24.8 | 25 | 26.4 | 1.54 | 1.54 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:05:00 | 2227.76 | 898.78 | 825082.26 | 801370.88 | 27.92 | 2457.594 | 1970.502 | 344.193 | 46 | 184 | 28.4 | 54 | 27.8 | 55.9 | 0 | 0 | - | - | 30.9 | 50.3 | 0 | 0 | 0 | 0 | 28.2 | 31.7 | 27.9 | 1.53 | 6.7 | 3 | 0 | 28.3 | 28.7 | 27.3 | 1.5 | 4.2 | 4.4 | 24.9 | 25.1 | 26.3 | 1.55 | 1.54 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:10:00 | 2235.72 | 903.08 | 825090.06 | 801375.18 | 28.02 | 2457.594 | 1970.502 | 87.064 | 46 | 184 | 28.2 | 54.5 | 27.7 | 56.1 | 0 | 0 | - | - | 30.7 | 50.6 | 0 | 0 | 0 | 0 | 28.2 | 31.1 | 27.8 | 1.53 | 6 | 2.9 | 0 | 28.2 | 28.6 | 27.3 | 1.51 | 4.1 | 4.2 | 24.9 | 25.1 | 25.7 | 1.55 | 1.54 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:15:00 | 2253.84 | 903.08 | 825108.82 | 801375.18 | 28.11 | 2442.834 | 1985.262 | 381.8 | 47 | 184 | 28.1 | 54.7 | 27.6 | 56.2 | 0 | 0 | - | - | 30.5 | 50.8 | 0 | 0 | 0 | 0 | 28.1 | 30.2 | 27.7 | 1.53 | 5.2 | 2.9 | 0 | 27.8 | 28.4 | 27.2 | 1.51 | 3.9 | 3.9 | 25 | 25.2 | 25.8 | 1.54 | 1.54 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:20:00 | 2269.3 | 903.08 | 825123.68 | 801375.18 | 28.21 | 2420.694 | 2007.403 | 187.946 | 47 | 184 | 27.9 | 55.1 | 27.5 | 56.4 | 0 | 0 | - | - | 30.3 | 51 | 0 | 0 | 0 | 0 | 27.9 | 29.6 | 27.6 | 1.53 | 4.6 | 2.8 | 0 | 27.7 | 28.2 | 27.1 | 1.51 | 3.6 | 3.6 | 25 | 25.2 | 25.3 | 1.53 | 1.53 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:25:00 | 2283.18 | 903.08 | 825137.52 | 801375.18 | 28.3 | 2405.934 | 2022.164 | 126.077 | 47 | 184 | 27.8 | 55.4 | 27.5 | 56.5 | 0 | 0 | - | - | 30.1 | 51.2 | 0 | 0 | 0 | 0 | 27.7 | 29.1 | 27.3 | 1.52 | 4.3 | 3 | 0 | 27.4 | 27.9 | 26.9 | 1.51 | 3.4 | 3.3 | 25.1 | 25.2 | 25.2 | 1.53 | 1.53 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:30:00 | 2299.98 | 903.08 | 825154.36 | 801375.18 | 28.39 | 2398.554 | 2029.544 | 187.987 | 48 | 184 | 27.6 | 55.7 | 27.4 | 56.7 | 0 | 0 | - | - | 29.9 | 51.4 | 0 | 0 | 0 | 0 | 27.6 | 28.7 | 27.2 | 1.51 | 3.9 | 2.8 | 0 | 27.2 | 27.8 | 26.7 | 1.52 | 3.2 | 3 | 25.1 | 25.2 | 25.3 | 1.53 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:35:00 | 2304.36 | 905.22 | 825158.54 | 801377.62 | 28.48 | 2383.793 | 2044.304 | -120.496 | 48 | 184 | 27.5 | 56 | 27.3 | 56.8 | 0 | 0 | - | - | 29.7 | 51.6 | 0 | 0 | 0 | 0 | 27.4 | 28.2 | 27.1 | 1.51 | 3.5 | 2.8 | 0 | 26.9 | 27.7 | 26.7 | 1.52 | 2.9 | 2.7 | 25.1 | 25.3 | 25.4 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:40:00 | 2304.36 | 912.88 | 825158.54 | 801385.06 | 28.56 | 2405.934 | 2022.164 | -65.861 | 48 | 184 | 27.4 | 56.2 | 27.3 | 56.9 | 0 | 0 | - | - | 29.5 | 51.8 | 0 | 0 | 0 | 0 | 27.4 | 28.1 | 27.1 | 1.51 | 3.3 | 2.8 | 0 | 26.8 | 27.7 | 26.6 | 1.52 | 2.9 | 2.6 | 25.2 | 25.3 | 25.5 | 1.53 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:45:00 | 2304.52 | 916.44 | 825158.7 | 801388.56 | 28.64 | 2405.934 | 2022.164 | -11.822 | 48 | 184 | 27.3 | 56.4 | 27.2 | 57 | 0 | 0 | - | - | 29.4 | 52.1 | 0 | 0 | 0 | 0 | 27.3 | 27.8 | 27.1 | 1.51 | 3.1 | 2.7 | 0 | 26.7 | 27.6 | 26.6 | 1.52 | 2.8 | 2.4 | 25.2 | 25.4 | 25.8 | 1.53 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:50:00 | 2305.08 | 917.7 | 825159.26 | 801389.86 | 28.72 | 2405.934 | 2022.164 | 12.882 | 48 | 184 | 27.1 | 56.6 | 27.1 | 57.2 | 0 | 0 | - | - | 29.3 | 52.2 | 0 | 0 | 0 | 0 | 27.3 | 27.7 | 27.1 | 1.52 | 3 | 2.6 | 0 | 26.7 | 27.6 | 26.6 | 1.52 | 2.8 | 2.4 | 25.2 | 25.4 | 26 | 1.53 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 15:55:00 | 2306.16 | 919.86 | 825160.34 | 801392.1 | 28.8 | 2405.934 | 2022.164 | -134.007 | 47 | 184 | 27.1 | 56.8 | 27.1 | 57.2 | 0 | 0 | - | - | 29.2 | 52.3 | 0 | 0 | 0 | 0 | 27.2 | 27.7 | 27.1 | 1.52 | 2.9 | 2.4 | 0 | 26.7 | 27.7 | 26.7 | 1.53 | 2.8 | 2.3 | 25.2 | 25.4 | 26.2 | 1.54 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:00:00 | 2306.36 | 924.78 | 825160.62 | 801396.88 | 28.88 | 2405.934 | 2022.164 | 61.586 | 47 | 184 | 27 | 56.9 | 27 | 57.3 | 0 | 0 | - | - | 29.2 | 52.4 | 0 | 0 | 0 | 0 | 27.3 | 27.7 | 27.1 | 1.52 | 2.8 | 2.3 | 0 | 26.7 | 27.7 | 26.7 | 1.53 | 2.8 | 2.2 | 25.2 | 25.4 | 26.2 | 1.54 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:05:00 | 2313.16 | 926.2 | 825167.88 | 801398.3 | 28.96 | 2405.934 | 2022.164 | 416.534 | 48 | 184 | 26.9 | 57.1 | 27 | 57.5 | 0 | 0 | - | - | 29.2 | 52.4 | 0 | 0 | 0 | 0 | 27.2 | 27.7 | 27.2 | 1.52 | 2.8 | 2.3 | 0 | 26.7 | 27.8 | 26.8 | 1.53 | 2.9 | 2.3 | 25.2 | 25.4 | 26.3 | 1.54 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:10:00 | 2350.28 | 926.2 | 825205.06 | 801398.3 | 29.05 | 2361.652 | 2066.444 | 384.509 | 48 | 184 | 26.8 | 57.2 | 26.9 | 57.6 | 0 | 0 | - | - | 29.2 | 52.3 | 0 | 0 | 0 | 0 | 27.3 | 27.7 | 27.3 | 1.53 | 2.8 | 2.3 | 0 | 26.7 | 27.8 | 26.9 | 1.53 | 2.9 | 2.2 | 25.3 | 25.5 | 26.3 | 1.54 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:15:00 | 2381.24 | 926.2 | 825236.28 | 801398.3 | 29.14 | 2332.132 | 2095.967 | 338.267 | 49 | 184 | 26.8 | 57.4 | 26.8 | 57.8 | 0 | 0 | - | - | 29.1 | 52.4 | 0 | 0 | 0 | 0 | 27.3 | 27.8 | 27.3 | 1.53 | 2.8 | 2.3 | 0 | 26.7 | 27.8 | 26.9 | 1.53 | 2.8 | 2.3 | 25.3 | 25.5 | 26.4 | 1.54 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:20:00 | 2406.56 | 926.2 | 825261.18 | 801398.3 | 29.22 | 2309.991 | 2118.108 | 279.278 | 50 | 184 | 26.7 | 57.5 | 26.8 | 57.8 | 0 | 0 | - | - | 29.1 | 52.4 | 0 | 0 | 0 | 0 | 27.3 | 27.7 | 27.3 | 1.53 | 2.7 | 2.3 | 0 | 26.8 | 27.8 | 27 | 1.53 | 2.8 | 2.2 | 25.4 | 25.6 | 26.3 | 1.54 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:25:00 | 2430.84 | 926.2 | 825285.32 | 801398.3 | 29.31 | 2280.468 | 2147.628 | 131.985 | 50 | 184 | 26.7 | 57.6 | 26.7 | 57.9 | 0 | 0 | - | - | 29.1 | 52.4 | 0 | 0 | 0 | 0 | 27.3 | 27.8 | 27.3 | 1.53 | 2.8 | 2.4 | 0 | 26.8 | 27.8 | 27.1 | 1.53 | 2.8 | 2.3 | 25.5 | 25.7 | 26.2 | 1.54 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:30:00 | 2444.68 | 926.2 | 825299.06 | 801398.3 | 29.38 | 2250.948 | 2177.148 | 216.591 | 51 | 184 | 26.6 | 57.8 | 26.7 | 58 | 0 | 0 | - | - | 29.1 | 52.4 | 0 | 0 | 0 | 0 | 27.3 | 27.8 | 27.2 | 1.52 | 2.7 | 2.4 | 0 | 26.8 | 27.8 | 27.1 | 1.53 | 2.7 | 2.2 | 25.5 | 25.7 | 26.1 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:35:00 | 2462.84 | 926.2 | 825317.56 | 801398.3 | 29.46 | 2236.188 | 2191.908 | 255.217 | 51 | 184 | 26.6 | 57.8 | 26.7 | 58.1 | 0 | 0 | - | - | 29 | 52.5 | 0 | 0 | 0 | 0 | 27.2 | 27.7 | 27.2 | 1.53 | 2.6 | 2.3 | 0 | 26.7 | 27.7 | 27 | 1.54 | 2.6 | 2.1 | 25.6 | 25.8 | 26 | 1.54 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:40:00 | 2482.76 | 926.2 | 825337.32 | 801398.3 | 29.53 | 2214.048 | 2214.048 | 250.395 | 52 | 184 | 26.5 | 58 | 26.6 | 58.2 | 0 | 0 | - | - | 29 | 52.5 | 0 | 0 | 0 | 0 | 27.2 | 27.7 | 27.1 | 1.52 | 2.6 | 2.3 | 0 | 26.7 | 27.7 | 26.9 | 1.54 | 2.6 | 2.1 | 25.7 | 25.8 | 25.9 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:45:00 | 2503.72 | 926.2 | 825358.32 | 801398.3 | 29.61 | 2199.288 | 2228.808 | 263.713 | 52 | 184 | 26.5 | 58.1 | 26.6 | 58.3 | 0 | 0 | - | - | 28.9 | 52.6 | 0 | 0 | 0 | 0 | 27.2 | 27.7 | 27.1 | 1.52 | 2.6 | 2.3 | 0 | 26.7 | 27.7 | 26.9 | 1.54 | 2.4 | 2 | 25.7 | 25.9 | 26.1 | 1.54 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:50:00 | 2518.54 | 926.2 | 825372.9 | 801398.3 | 29.68 | 2162.388 | 2265.708 | 88.308 | 53 | 184 | 26.4 | 58.2 | 26.5 | 58.5 | 0 | 0 | - | - | 28.9 | 52.6 | 0 | 0 | 0 | 0 | 27.1 | 27.7 | 27.1 | 1.52 | 2.6 | 2.3 | 0 | 26.7 | 27.7 | 26.8 | 1.54 | 2.4 | 1.9 | 25.7 | 25.9 | 26.1 | 1.53 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 16:55:00 | 2520.78 | 931.48 | 825374.96 | 801404.08 | 29.75 | 2162.388 | 2265.708 | -188.928 | 52 | 184 | 26.4 | 58.3 | 26.5 | 58.5 | 0 | 0 | - | - | 28.8 | 52.7 | 0 | 0 | 0 | 0 | 27.1 | 27.7 | 27.1 | 1.52 | 2.6 | 2.2 | 0 | 26.7 | 27.7 | 26.8 | 1.54 | 2.3 | 1.8 | 25.8 | 26 | 26.1 | 1.53 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:00:00 | 2520.78 | 962.42 | 825374.96 | 801435.76 | 29.83 | 2199.288 | 2228.808 | -449.432 | 52 | 184 | 26.3 | 58.4 | 26.5 | 58.6 | 0 | 0 | - | - | 28.8 | 52.7 | 0 | 0 | 0 | 0 | 27 | 27.7 | 26.9 | 1.52 | 2.5 | 2.2 | 0 | 26.7 | 27.6 | 26.8 | 1.54 | 2.3 | 1.8 | 25.8 | 26 | 26.1 | 1.53 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:05:00 | 2520.78 | 981.42 | 825374.96 | 801453.52 | 29.91 | 2236.188 | 2191.908 | -0.946 | 51 | 184 | 26.3 | 58.6 | 26.4 | 58.8 | 0 | 0 | - | - | 28.7 | 52.8 | 0 | 0 | 0 | 0 | 26.8 | 27.6 | 26.8 | 1.52 | 2.4 | 2 | 0 | 26.6 | 27.5 | 26.7 | 1.55 | 2.1 | 1.7 | 25.8 | 26 | 26.1 | 1.53 | 1.55 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:10:00 | 2521.46 | 982.86 | 825375.64 | 801455.04 | 29.97 | 2228.808 | 2199.288 | -51.406 | 51 | 184 | 26.3 | 58.6 | 26.5 | 58.7 | 0 | 0 | - | - | 28.6 | 52.9 | 0 | 0 | 0 | 0 | 26.8 | 27.6 | 26.7 | 1.52 | 2.4 | 2 | 0 | 26.6 | 27.5 | 26.7 | 1.55 | 2.1 | 1.7 | 25.8 | 26 | 26.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:15:00 | 2521.52 | 987.7 | 825375.7 | 801459.96 | 30.04 | 2236.188 | 2191.908 | -109.907 | 51 | 184 | 26.3 | 58.7 | 26.5 | 58.7 | 0 | 0 | - | - | 28.6 | 53 | 0 | 0 | 0 | 0 | 26.7 | 27.6 | 26.7 | 1.52 | 2.4 | 1.9 | 0 | 26.6 | 27.4 | 26.7 | 1.55 | 2 | 1.5 | 25.9 | 26 | 26.2 | 1.53 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:20:00 | 2521.52 | 1000.56 | 825375.7 | 801472.76 | 30.12 | 2243.568 | 2184.528 | -197.295 | 51 | 184 | 26.2 | 58.8 | 26.4 | 58.8 | 0 | 0 | - | - | 28.5 | 53.1 | 0 | 0 | 0 | 0 | 26.7 | 27.6 | 26.7 | 1.52 | 2.4 | 1.8 | 0 | 26.4 | 27.4 | 26.7 | 1.55 | 1.9 | 1.4 | 25.9 | 26.1 | 26.3 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:25:00 | 2521.52 | 1020.96 | 825375.7 | 801493.42 | 30.19 | 2273.088 | 2155.008 | -233.552 | 50 | 184 | 26.2 | 58.8 | 26.4 | 58.9 | 0 | 0 | - | - | 28.5 | 53.2 | 0 | 0 | 0 | 0 | 26.7 | 27.4 | 26.7 | 1.53 | 2.4 | 1.7 | 0 | 26.4 | 27.4 | 26.7 | 1.55 | 1.9 | 1.4 | 25.8 | 26.1 | 26.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:30:00 | 2521.52 | 1042.66 | 825375.7 | 801515.2 | 30.26 | 2287.849 | 2140.248 | -286.175 | 50 | 184 | 26.2 | 58.9 | 26.3 | 59 | 0 | 0 | - | - | 28.4 | 53.2 | 0 | 0 | 0 | 0 | 26.7 | 27.4 | 26.7 | 1.53 | 2.3 | 1.6 | 0 | 26.3 | 27.4 | 26.7 | 1.56 | 1.8 | 1.3 | 25.8 | 26.1 | 26.3 | 1.54 | 1.54 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:35:00 | 2521.52 | 1069.34 | 825375.7 | 801541.84 | 30.34 | 2317.372 | 2110.728 | -341.207 | 49 | 184 | 26.2 | 58.9 | 26.3 | 59 | 0 | 0 | - | - | 28.4 | 53.3 | 0 | 0 | 0 | 0 | 26.6 | 27.4 | 26.6 | 1.53 | 2.3 | 1.4 | 0 | 26.3 | 27.3 | 26.6 | 1.56 | 1.8 | 1.2 | 25.9 | 26.1 | 26.3 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:40:00 | 2521.52 | 1099.08 | 825375.7 | 801571.54 | 30.42 | 2354.272 | 2073.825 | -388.079 | 48 | 184 | 26.1 | 59 | 26.3 | 59 | 0 | 0 | - | - | 28.3 | 53.4 | 0 | 0 | 0 | 0 | 26.6 | 27.4 | 26.6 | 1.53 | 2.3 | 1.5 | 0 | 26.2 | 27.3 | 26.6 | 1.55 | 1.8 | 1.2 | 25.8 | 26.1 | 26.3 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:45:00 | 2521.52 | 1127.26 | 825375.7 | 801600.12 | 30.51 | 2376.413 | 2051.684 | -331.178 | 48 | 184 | 26.1 | 59 | 26.3 | 59.1 | 0 | 0 | - | - | 28.3 | 53.5 | 0 | 0 | 0 | 0 | 26.6 | 27.3 | 26.6 | 1.53 | 2.2 | 1.4 | 0 | 26.2 | 27.3 | 26.6 | 1.55 | 1.8 | 1.2 | 25.8 | 26 | 26.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:50:00 | 2521.52 | 1151.68 | 825375.7 | 801624.02 | 30.59 | 2413.314 | 2014.783 | -227.279 | 47 | 184 | 26.1 | 59.1 | 26.3 | 59.1 | 0 | 0 | - | - | 28.3 | 53.4 | 0 | 0 | 0 | 0 | 26.6 | 27.3 | 26.6 | 1.53 | 2.3 | 1.4 | 0 | 26.2 | 27.3 | 26.6 | 1.55 | 1.8 | 1.2 | 25.8 | 25.9 | 26.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 17:55:00 | 2521.52 | 1168.66 | 825375.7 | 801641.02 | 30.67 | 2435.454 | 1992.642 | -256.89 | 47 | 184 | 26.1 | 59.2 | 26.3 | 59 | 0 | 0 | - | - | 28.3 | 53.6 | 0 | 0 | 0 | 0 | 26.5 | 27.3 | 26.6 | 1.53 | 2.2 | 1.5 | 0 | 26.2 | 27.3 | 26.6 | 1.55 | 1.9 | 1.1 | 25.7 | 25.9 | 26.3 | 1.55 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:00:00 | 2521.52 | 1203.96 | 825375.7 | 801677.44 | 30.75 | 2457.594 | 1970.502 | -317.233 | 46 | 184 | 26.1 | 59.2 | 26.3 | 59.1 | 0 | 0 | - | - | 28.3 | 53.6 | 0 | 0 | 0 | 0 | 26.6 | 27.3 | 26.6 | 1.53 | 2.3 | 1.5 | 0 | 26.2 | 27.3 | 26.6 | 1.55 | 1.9 | 1.2 | 25.7 | 25.9 | 26.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:05:00 | 2521.52 | 1230.02 | 825375.7 | 801702.54 | 30.83 | 2494.494 | 1933.602 | -325.323 | 45 | 184 | 26.1 | 59.2 | 26.3 | 59 | 0 | 0 | - | - | 28.2 | 53.7 | 0 | 0 | 0 | 0 | 26.6 | 27.4 | 26.6 | 1.53 | 2.4 | 1.5 | 0 | 26.2 | 27.3 | 26.6 | 1.55 | 1.9 | 1.3 | 25.7 | 25.9 | 26.3 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:10:00 | 2521.52 | 1255.84 | 825375.7 | 801728.6 | 30.91 | 2524.016 | 1904.082 | -322.388 | 44 | 184 | 26.1 | 59.1 | 26.3 | 59 | 0 | 0 | - | - | 28.2 | 53.7 | 0 | 0 | 0 | 0 | 26.6 | 27.4 | 26.6 | 1.53 | 2.3 | 1.5 | 0 | 26.2 | 27.3 | 26.6 | 1.55 | 1.9 | 1.2 | 25.7 | 25.9 | 26.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:15:00 | 2521.52 | 1294.08 | 825375.7 | 801767.26 | 31 | 2568.298 | 1859.802 | -746.429 | 43 | 184 | 26 | 59.2 | 26.3 | 59.1 | 0 | 0 | - | - | 28.2 | 53.7 | 0 | 0 | 0 | 0 | 26.6 | 27.4 | 26.7 | 1.53 | 2.4 | 1.6 | 0 | 26.2 | 27.3 | 26.6 | 1.55 | 1.9 | 1.2 | 25.7 | 25.8 | 26.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:20:00 | 2521.52 | 1352.6 | 825375.7 | 801825.5 | 31.09 | 2634.72 | 1793.379 | -473.987 | 42 | 184 | 26 | 59.3 | 26.3 | 59 | 0 | 0 | - | - | 28.2 | 53.8 | 0 | 0 | 0 | 0 | 26.6 | 27.4 | 26.7 | 1.53 | 2.4 | 1.6 | 0 | 26.3 | 27.4 | 26.6 | 1.55 | 2 | 1.4 | 25.7 | 25.8 | 26.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:25:00 | 2521.52 | 1399.6 | 825375.7 | 801872.66 | 31.19 | 2693.76 | 1734.336 | -607.276 | 41 | 184 | 26.1 | 59.3 | 26.3 | 59 | 0 | 0 | - | - | 28.2 | 53.8 | 0 | 0 | 0 | 0 | 26.7 | 27.4 | 26.7 | 1.53 | 2.4 | 1.6 | 0 | 26.3 | 27.4 | 26.6 | 1.55 | 2 | 1.4 | 25.7 | 25.8 | 26.2 | 1.54 | 1.54 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:30:00 | 2521.52 | 1459.4 | 825375.7 | 801932.72 | 31.28 | 2745.42 | 1682.676 | -791.525 | 39 | 184 | 26.1 | 59.3 | 26.3 | 59 | 0 | 0 | - | - | 28.1 | 53.9 | 0 | 0 | 0 | 0 | 26.7 | 27.4 | 26.7 | 1.53 | 2.4 | 1.7 | 0 | 26.3 | 27.4 | 26.7 | 1.55 | 2.1 | 1.4 | 25.6 | 25.8 | 26.1 | 1.54 | 1.54 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:35:00 | 2521.52 | 1535.16 | 825375.7 | 802008.52 | 31.38 | 2841.364 | 1586.736 | -761.296 | 37 | 184 | 26.1 | 59.2 | 26.4 | 59 | 0 | 0 | - | - | 28.1 | 53.9 | 0 | 0 | 0 | 0 | 26.7 | 27.4 | 26.7 | 1.53 | 2.5 | 1.7 | 0 | 26.3 | 27.4 | 26.7 | 1.54 | 2.1 | 1.4 | 25.6 | 25.7 | 26.1 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:40:00 | 2521.52 | 1593.22 | 825375.7 | 802066.74 | 31.48 | 2900.406 | 1527.693 | -712.106 | 36 | 184 | 26 | 59.3 | 26.4 | 59 | 0 | 0 | - | - | 28.1 | 53.9 | 0 | 0 | 0 | 0 | 26.7 | 27.4 | 26.7 | 1.53 | 2.5 | 1.7 | 0 | 26.2 | 27.4 | 26.7 | 1.54 | 2.1 | 1.4 | 25.6 | 25.7 | 26.1 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:45:00 | 2521.52 | 1661.72 | 825375.7 | 802135.72 | 31.57 | 2988.966 | 1439.13 | -867.307 | 34 | 184 | 25.9 | 59.5 | 26.4 | 59 | 0 | 0 | - | - | 28.1 | 54 | 0 | 0 | 0 | 0 | 26.7 | 27.3 | 26.7 | 1.53 | 2.4 | 1.6 | 0 | 26.3 | 27.3 | 26.7 | 1.54 | 2 | 1.5 | 25.6 | 25.7 | 26.2 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:50:00 | 2521.52 | 1740.88 | 825375.7 | 802214.78 | 31.68 | 3062.768 | 1365.33 | -894.91 | 32 | 184 | 26 | 59.5 | 26.5 | 58.8 | 0 | 0 | - | - | 28.1 | 53.9 | 0 | 0 | 0 | 0 | 26.6 | 27.3 | 26.7 | 1.53 | 2.4 | 1.6 | 0 | 26.2 | 27.3 | 26.7 | 1.54 | 2.1 | 1.4 | 25.6 | 25.7 | 26.1 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 18:55:00 | 2521.52 | 1815.86 | 825375.7 | 802289.96 | 31.78 | 3136.572 | 1291.529 | -971.302 | 31 | 184 | 26.1 | 59.3 | 26.6 | 58.6 | 0 | 0 | - | - | 28.1 | 53.9 | 0 | 0 | 0 | 0 | 26.6 | 27.3 | 26.7 | 1.53 | 2.4 | 1.6 | 0 | 26.2 | 27.3 | 26.7 | 1.54 | 2 | 1.5 | 25.6 | 25.7 | 26.1 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:00:00 | 2521.52 | 1876.3 | 825375.7 | 802350.38 | 31.87 | 3173.472 | 1254.627 | -641.141 | 30 | 184 | 26.2 | 59.1 | 26.6 | 58.6 | 0 | 0 | - | - | 28.1 | 53.9 | 0 | 0 | 0 | 0 | 26.6 | 27.3 | 26.6 | 1.53 | 2.4 | 1.6 | 0 | 26.2 | 27.3 | 26.6 | 1.54 | 2 | 1.5 | 25.6 | 25.8 | 25.9 | 1.54 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:05:00 | 2521.52 | 1929.52 | 825375.7 | 802402.54 | 31.97 | 3217.752 | 1210.344 | -589.95 | 29 | 184 | 26.3 | 59 | 26.7 | 58.5 | 0 | 0 | - | - | 28.1 | 54 | 0 | 0 | 0 | 0 | 26.6 | 27.3 | 26.6 | 1.53 | 2.3 | 1.6 | 0 | 26.3 | 27.2 | 26.6 | 1.55 | 1.9 | 1.4 | 25.7 | 25.9 | 26.1 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:10:00 | 2521.52 | 1976.16 | 825375.7 | 802448.76 | 32.08 | 3262.032 | 1166.064 | -568.538 | 28 | 184 | 26.3 | 59 | 26.7 | 58.4 | 0 | 0 | - | - | 28.1 | 54 | 0 | 0 | 0 | 0 | 26.6 | 27.3 | 26.6 | 1.53 | 2.3 | 1.6 | 0 | 26.2 | 27.2 | 26.6 | 1.55 | 1.9 | 1.4 | 25.8 | 26 | 26 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:15:00 | 2521.52 | 2022.76 | 825375.7 | 802496.44 | 32.17 | 3291.554 | 1136.544 | -646.976 | 27 | 184 | 26.4 | 58.9 | 26.8 | 58.4 | 0 | 0 | - | - | 28.1 | 54 | 0 | 0 | 0 | 0 | 26.6 | 27.2 | 26.6 | 1.53 | 2.3 | 1.5 | 0 | 26.2 | 27.2 | 26.6 | 1.55 | 1.8 | 1.3 | 25.9 | 26.1 | 26 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:20:00 | 2521.52 | 2075.84 | 825375.7 | 802548.2 | 32.27 | 3335.834 | 1092.262 | -549.844 | 26 | 184 | 26.4 | 58.9 | 26.8 | 58.3 | 0 | 0 | - | - | 28.1 | 53.9 | 0 | 0 | 0 | 0 | 26.6 | 27.2 | 26.6 | 1.53 | 2.2 | 1.5 | 0 | 26.2 | 27.2 | 26.6 | 1.55 | 1.7 | 1.2 | 26.1 | 26.3 | 25.9 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:25:00 | 2521.52 | 2124.74 | 825375.7 | 802597.76 | 32.36 | 3380.116 | 1047.982 | -618.108 | 25 | 184 | 26.4 | 58.9 | 26.8 | 58.3 | 0 | 0 | - | - | 28.2 | 54 | 0 | 0 | 0 | 0 | 26.6 | 27.2 | 26.6 | 1.53 | 2.1 | 1.4 | 0 | 26.2 | 27.2 | 26.6 | 1.56 | 1.6 | 1.2 | 26.2 | 26.4 | 25.9 | 1.55 | 1.54 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:30:00 | 2521.52 | 2176.16 | 825375.7 | 802648.92 | 32.46 | 3424.398 | 1003.7 | -596.213 | 24 | 184 | 26.5 | 58.8 | 26.9 | 58.3 | 0 | 0 | - | - | 28.1 | 54 | 0 | 0 | 0 | 0 | 26.6 | 27.2 | 26.6 | 1.53 | 2.1 | 1.5 | 0 | 26.3 | 27.2 | 26.6 | 1.56 | 1.5 | 1.1 | 26.4 | 26.6 | 25.9 | 1.55 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:35:00 | 2521.52 | 2209.52 | 825375.7 | 802681.84 | 32.55 | 3461.298 | 966.798 | -214.695 | 23 | 184 | 26.5 | 58.8 | 26.9 | 58.4 | 0 | 0 | - | - | 28.1 | 54 | 0 | 0 | 0 | 0 | 26.7 | 27.2 | 26.6 | 1.54 | 1.9 | 1.5 | 0 | 26.3 | 27.2 | 26.6 | 1.57 | 1.4 | 1 | 26.6 | 26.7 | 25.9 | 1.55 | 1.55 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:40:00 | 2521.52 | 2228.46 | 825375.7 | 802700.86 | 32.62 | 3476.058 | 952.038 | -203.786 | 23 | 184 | 26.4 | 59 | 27.1 | 58.1 | 0 | 0 | - | - | 28.1 | 54.1 | 0 | 0 | 0 | 0 | 26.9 | 27.2 | 26.6 | 1.54 | 1.9 | 1.6 | 0 | 26.5 | 27.2 | 26.6 | 1.57 | 1.3 | 1.1 | 26.7 | 26.8 | 26.1 | 1.56 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:45:00 | 2521.52 | 2244.04 | 825375.7 | 802716.56 | 32.7 | 3505.578 | 922.518 | -244.862 | 22 | 184 | 26.4 | 59.1 | 27.1 | 58.1 | 0 | 0 | - | - | 28.1 | 54.1 | 0 | 0 | 0 | 0 | 27.1 | 27.2 | 26.6 | 1.55 | 1.8 | 1.7 | 0 | 26.6 | 27.2 | 26.6 | 1.57 | 1.2 | 1.1 | 26.7 | 26.9 | 26.2 | 1.56 | 1.56 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:50:00 | 2521.52 | 2264.8 | 825375.7 | 802737.14 | 32.78 | 3505.578 | 922.518 | -162.652 | 22 | 184 | 26.4 | 59.2 | 27.1 | 58.2 | 0 | 0 | - | - | 28.1 | 54.2 | 0 | 0 | 0 | 0 | 27.3 | 27.3 | 26.6 | 1.55 | 1.7 | 1.8 | 0 | 26.6 | 27.3 | 26.6 | 1.58 | 1.2 | 1 | 26.8 | 27 | 26.2 | 1.57 | 1.57 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 19:55:00 | 2521.52 | 2289.02 | 825375.7 | 802761.7 | 32.86 | 3542.48 | 885.618 | -225.918 | 21 | 184 | 26.4 | 59.2 | 27 | 58.4 | 0 | 0 | - | - | 28.1 | 54.1 | 0 | 0 | 0 | 0 | 27.5 | 27.3 | 26.6 | 1.55 | 1.7 | 1.9 | 0 | 26.7 | 27.3 | 26.6 | 1.58 | 1.2 | 1 | 26.8 | 27.1 | 26.3 | 1.57 | 1.57 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:00:00 | 2521.52 | 2323.48 | 825375.7 | 802797 | 33.18 | 3549.86 | 878.238 | -364.26 | 21 | 184 | 26.4 | 59.3 | 26.9 | 58.5 | 0 | 0 | - | - | 28.1 | 54.2 | 0 | 0 | 20.2 | 0 | 27.6 | 27.4 | 26.6 | 1.55 | 1.9 | 2.1 | 19.9 | 26.7 | 27.4 | 26.6 | 1.58 | 1.2 | 0.9 | 23.7 | 26.2 | 26.5 | 2.77 | 1.11 | 2.76 | 1.14 | 255 | 213 | 2400 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:05:00 | 2521.52 | 2343.66 | 825375.7 | 802815.82 | 33.88 | 3594.14 | 833.956 | 0.768 | 20 | 184 | 26.3 | 59.2 | 26.9 | 58.6 | 0 | 0 | - | - | 28.1 | 54.3 | 252 | 210 | 57 | 57.2 | 66.6 | 25.4 | 44.1 | 2.5 | 10.1 | 22.1 | 55.9 | 65.7 | 25.6 | 45.6 | 2.69 | 9.1 | 19.1 | 21.9 | 23.9 | 27.9 | 2.53 | 1.13 | 2.78 | 1.17 | 252 | 209 | 2400 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:10:00 | 2522.08 | 2347.12 | 825376.26 | 802819.32 | 34.59 | 3594.14 | 833.956 | -50.906 | 20 | 184 | 26.2 | 59.3 | 26.8 | 58.6 | 0 | 0 | - | - | 28.1 | 54.4 | 252 | 205 | 61.5 | 61.4 | 66.5 | 23.6 | 42.3 | 2.46 | 9.4 | 22.6 | 61.9 | 69.6 | 23.8 | 46.4 | 2.77 | 8.4 | 21.7 | 21.2 | 23.2 | 28.7 | 2.52 | 1.1 | 2.81 | 1.14 | 252 | 196 | 2400 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:15:00 | 2522.08 | 2355.2 | 825376.26 | 802827.44 | 35.31 | 3594.14 | 833.956 | -197.505 | 20 | 184 | 26.2 | 59.2 | 26.7 | 58.6 | 0 | 0 | - | - | 28.1 | 54.4 | 252 | 195 | 62.5 | 62.3 | 66.3 | 22.8 | 42.1 | 2.45 | 9.2 | 22.8 | 63.2 | 71.1 | 23.2 | 46.7 | 2.79 | 8.4 | 22.9 | 20.7 | 22.7 | 28.6 | 2.51 | 1.09 | 2.81 | 1.12 | 252 | 192 | 2400 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:20:00 | 2522.08 | 2362.48 | 825376.26 | 802834.6 | 36.04 | 3594.14 | 833.956 | -3.207 | 20 | 184 | 26.2 | 59.2 | 26.6 | 58.6 | 0 | 0 | - | - | 28.2 | 54.3 | 252 | 191 | 62.7 | 63 | 66.3 | 22.4 | 42.1 | 2.44 | 9.1 | 22.9 | 62.7 | 71.9 | 22.7 | 46.9 | 2.79 | 8.5 | 23.7 | 20.4 | 22.4 | 28.7 | 2.5 | 1.09 | 2.81 | 1.11 | 252 | 191 | 2400 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:25:00 | 2522.12 | 2365.66 | 825376.3 | 802837.84 | 36.77 | 3594.14 | 833.956 | -74.559 | 20 | 184 | 26.1 | 59.1 | 26.5 | 58.5 | 0 | 0 | - | - | 28.2 | 54.3 | 252 | 190 | 63.3 | 63 | 66.1 | 22.2 | 42 | 2.44 | 9 | 22.8 | 64 | 72.2 | 22.4 | 46.9 | 2.79 | 8.4 | 24 | 20.2 | 22.2 | 28.7 | 2.5 | 1.08 | 2.82 | 1.1 | 252 | 189 | 2400 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:30:00 | 2522.18 | 2369.88 | 825376.36 | 802842.04 | 37.49 | 3608.9 | 819.196 | -37.815 | 20 | 184 | 26.1 | 59 | 26.4 | 58.4 | 0 | 0 | - | - | 28.3 | 54.2 | 252 | 189 | 63 | 63.2 | 66.3 | 21.8 | 41.9 | 2.43 | 8.9 | 22.9 | 62.3 | 72.4 | 22.2 | 46.9 | 2.79 | 8.5 | 24.1 | 19.9 | 21.9 | 29.1 | 2.5 | 1.07 | 2.81 | 1.1 | 252 | 189 | 2400 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:35:00 | 2522.18 | 2373.5 | 825376.36 | 802845.68 | 38.21 | 3623.66 | 804.436 | -114.669 | 20 | 184 | 26.1 | 58.7 | 26.4 | 58.3 | 0 | 0 | - | - | 28.4 | 54.1 | 252 | 189 | 63.6 | 63.7 | 66.2 | 21.7 | 41.9 | 2.44 | 8.9 | 22.9 | 65 | 72.5 | 21.9 | 46.9 | 2.79 | 8.6 | 24.3 | 19.7 | 21.7 | 29.7 | 2.5 | 1.06 | 2.81 | 1.09 | 252 | 189 | 2400 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:40:00 | 2522.18 | 2381.14 | 825376.36 | 802853.28 | 38.93 | 3631.04 | 797.056 | -70.046 | 19 | 184 | 26.1 | 58.6 | 26.3 | 58.3 | 0 | 0 | - | - | 28.5 | 54 | 252 | 189 | 63.3 | 63.6 | 66.3 | 21.4 | 42 | 2.44 | 8.9 | 22.9 | 64.9 | 72.8 | 21.7 | 46.9 | 2.8 | 8.5 | 24.5 | 19.6 | 21.4 | 30.2 | 2.49 | 1.06 | 2.81 | 1.08 | 252 | 188 | 2385 | 2385
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:45:00 | 2522.2 | 2387.44 | 825376.38 | 802859.6 | 39.65 | 3638.421 | 789.676 | -47.807 | 19 | 184 | 26.1 | 58.4 | 26.3 | 58.2 | 0 | 0 | - | - | 28.5 | 53.9 | 252 | 188 | 63.5 | 63.5 | 66.2 | 21.3 | 41.7 | 2.42 | 8.8 | 23 | 61.5 | 72.7 | 21.6 | 46.9 | 2.79 | 8.5 | 24.6 | 19.3 | 21.3 | 30.2 | 2.49 | 1.06 | 2.81 | 1.07 | 252 | 187 | 2392 | 2392
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:50:00 | 2522.2 | 2395.22 | 825376.38 | 802867.52 | 40.38 | 3638.421 | 789.676 | -108.848 | 19 | 184 | 26.1 | 58.2 | 26.2 | 58.1 | 0 | 0 | - | - | 28.6 | 53.7 | 252 | 187 | 63.5 | 63.9 | 66 | 21.1 | 41.7 | 2.42 | 8.8 | 22.8 | 65.7 | 72.8 | 21.3 | 46.9 | 2.79 | 8.5 | 24.6 | 19.2 | 21.1 | 29.9 | 2.48 | 1.05 | 2.81 | 1.07 | 252 | 187 | 2397 | 2397
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 20:55:00 | 2522.2 | 2409.88 | 825376.38 | 802882.4 | 40.94 | 3638.421 | 789.676 | -215.891 | 19 | 184 | 26.1 | 58 | 26.1 | 58.1 | 0 | 0 | - | - | 28.6 | 53.7 | 252 | 187 | 63.1 | 63.2 | 66 | 20.8 | 41.6 | 2.41 | 8.8 | 23 | 62.6 | 72.9 | 21.2 | 46.7 | 2.78 | 8.5 | 24.8 | 20.3 | 21.6 | 29.4 | 1.64 | 1.3 | 2.76 | 1.1 | 0 | 154 | 0 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:00:00 | 2522.2 | 2423.92 | 825376.38 | 802896.38 | 41.38 | 3667.943 | 760.156 | -125.976 | 18 | 184 | 26 | 57.9 | 26 | 58.1 | 0 | 0 | - | - | 28.7 | 53.6 | 0 | 145 | 60.7 | 60.5 | 38.4 | 32.5 | 32.1 | 1.62 | 11.6 | 11.6 | 60.8 | 71 | 21.8 | 46 | 2.74 | 8.1 | 23.5 | 20.8 | 22.1 | 28.6 | 1.59 | 1.41 | 2.76 | 1.11 | 0 | 129 | 0 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:05:00 | 2522.2 | 2433.68 | 825376.38 | 802905.94 | 41.81 | 3675.324 | 752.776 | -105.366 | 18 | 184 | 26 | 58 | 26.1 | 58 | 0 | 0 | - | - | 28.7 | 53.5 | 0 | 127 | 60.3 | 60.1 | 29.6 | 41.3 | 30.3 | 1.56 | 19.1 | 3.7 | 59.7 | 71 | 22.2 | 45.6 | 2.74 | 8.3 | 23.6 | 20.9 | 22.2 | 28.2 | 1.46 | 1.42 | 2.75 | 1.1 | 0 | 121 | 0 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:10:00 | 2522.2 | 2439.42 | 825376.38 | 802911.54 | 42.24 | 3682.704 | 745.395 | -87.834 | 18 | 184 | 25.9 | 57.9 | 26 | 58 | 0 | 0 | - | - | 28.7 | 53.5 | 0 | 120 | 60.2 | 60.4 | 29.3 | 42.7 | 29.2 | 1.42 | 20.6 | 6.8 | 61 | 71.1 | 22.3 | 45.6 | 2.74 | 8.6 | 23.7 | 20.9 | 22.3 | 28.2 | 1.43 | 1.42 | 2.75 | 1.1 | 0 | 119 | 0 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:15:00 | 2522.24 | 2442.32 | 825376.42 | 802914.44 | 42.67 | 3682.704 | 745.395 | -5.548 | 18 | 184 | 25.9 | 57.9 | 26 | 57.9 | 0 | 0 | - | - | 28.6 | 53.6 | 0 | 118 | 59.6 | 60.4 | 29.7 | 40.4 | 28.7 | 1.42 | 18.3 | 7.3 | 60.9 | 71.1 | 22.2 | 45.5 | 2.73 | 8.6 | 23.8 | 20.9 | 22.2 | 28.2 | 1.43 | 1.42 | 2.74 | 1.1 | 0 | 118 | 0 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:20:00 | 2522.24 | 2448.16 | 825376.42 | 802920.36 | 43.1 | 3682.704 | 745.395 | -56.012 | 18 | 184 | 25.9 | 57.8 | 25.9 | 57.9 | 0 | 0 | - | - | 28.6 | 53.6 | 0 | 118 | 60.1 | 59.8 | 29.9 | 39.1 | 28.4 | 1.42 | 17 | 7.6 | 59.9 | 71.2 | 22.2 | 45.5 | 2.72 | 8.7 | 24 | 20.8 | 22.2 | 28.2 | 1.43 | 1.41 | 2.73 | 1.09 | 0 | 118 | 0 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:25:00 | 2522.24 | 2453.36 | 825376.42 | 802925.58 | 43.53 | 3682.704 | 745.395 | -42.321 | 18 | 184 | 25.8 | 57.8 | 25.9 | 57.9 | 0 | 0 | - | - | 28.5 | 53.7 | 0 | 118 | 59.5 | 59.7 | 29.9 | 38.1 | 28.2 | 1.41 | 16.1 | 7.7 | 60 | 71.1 | 22.1 | 45.4 | 2.71 | 8.6 | 24.1 | 20.7 | 22.1 | 27.9 | 1.42 | 1.41 | 2.73 | 1.1 | 0 | 118 | 0 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:30:00 | 2522.24 | 2457.1 | 825376.42 | 802929.26 | 43.95 | 3682.704 | 745.395 | -24.589 | 18 | 184 | 25.8 | 57.7 | 25.8 | 57.9 | 0 | 0 | - | - | 28.5 | 53.7 | 0 | 118 | 59.4 | 59.2 | 29.8 | 37.2 | 28.1 | 1.41 | 15.3 | 7.7 | 59 | 71 | 22 | 45.2 | 2.71 | 8.6 | 24 | 20.6 | 21.9 | 27.8 | 1.42 | 1.41 | 2.72 | 1.09 | 0 | 118 | 0 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:35:00 | 2526.7 | 2457.94 | 825381.18 | 802930.04 | 44.38 | 3682.704 | 745.395 | 64.783 | 18 | 184 | 25.8 | 57.7 | 25.7 | 57.9 | 0 | 0 | - | - | 28.5 | 53.8 | 0 | 118 | 59.2 | 59.1 | 29.7 | 36.4 | 27.8 | 1.4 | 14.5 | 7.6 | 59.5 | 70.9 | 21.8 | 45.1 | 2.7 | 8.5 | 24 | 20.5 | 21.8 | 27.8 | 1.41 | 1.4 | 2.72 | 1.09 | 0 | 118 | 0 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:40:00 | 2528.12 | 2460.3 | 825382.3 | 802932.46 | 44.8 | 3682.704 | 745.395 | 12.403 | 18 | 184 | 25.7 | 57.7 | 25.7 | 57.9 | 0 | 0 | - | - | 28.4 | 53.8 | 0 | 118 | 58.5 | 59 | 29.4 | 34.9 | 27.7 | 1.39 | 13.3 | 7.6 | 59.2 | 70.9 | 21.8 | 45.1 | 2.7 | 8.6 | 24 | 20.4 | 21.7 | 27.8 | 1.4 | 1.39 | 2.72 | 1.08 | 0 | 118 | 0 | 2400
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:45:00 | 2531.08 | 2460.94 | 825385.42 | 802933.04 | 45.15 | 3682.704 | 745.395 | 102.373 | 18 | 184 | 25.7 | 57.5 | 25.6 | 57.9 | 0 | 0 | - | - | 28.4 | 53.8 | 0 | 118 | 58.9 | 59.3 | 29.1 | 32.7 | 27.7 | 1.39 | 11.2 | 7.4 | 59.4 | 70.8 | 21.7 | 45.1 | 2.7 | 8.6 | 24.1 | 21.5 | 21.7 | 27.8 | 1.4 | 1.4 | 1.93 | 1.16 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:50:00 | 2539.28 | 2460.94 | 825393.7 | 802933.04 | 45.23 | 3682.704 | 745.395 | 152.914 | 18 | 184 | 25.7 | 57.6 | 25.5 | 58 | 0 | 0 | - | - | 28.4 | 53.8 | 0 | 0 | 0 | 0 | 28.9 | 31.1 | 27.7 | 1.39 | 9.2 | 7.2 | 0 | 36.7 | 33 | 34.2 | 1.75 | 10.5 | 7.8 | 22.8 | 23 | 27.9 | 1.41 | 1.42 | 1.49 | 1.47 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 21:55:00 | 2544.56 | 2461.18 | 825398.78 | 802933.32 | 45.31 | 3682.704 | 745.395 | -85.979 | 18 | 184 | 25.6 | 57.7 | 25.5 | 58 | 0 | 0 | - | - | 28.3 | 53.8 | 0 | 0 | 0 | 0 | 28.9 | 29.8 | 27.7 | 1.4 | 7.6 | 7 | 0 | 28.4 | 44.5 | 29.9 | 1.48 | 21.2 | 5.1 | 23.2 | 23.4 | 27.8 | 1.42 | 1.43 | 1.47 | 1.48 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:00:00 | 2544.62 | 2472.82 | 825398.8 | 802945.24 | 45.4 | 3682.704 | 745.395 | -119.227 | 18 | 184 | 25.5 | 57.8 | 25.5 | 58.1 | 0 | 0 | - | - | 28.3 | 53.8 | 0 | 0 | 0 | 0 | 28.8 | 29.3 | 27.7 | 1.41 | 6.8 | 6.7 | 0 | 28.2 | 42.1 | 29.3 | 1.48 | 18.5 | 4.8 | 23.3 | 23.5 | 27.7 | 1.43 | 1.44 | 1.48 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:05:00 | 2544.62 | 2475.56 | 825398.8 | 802947.68 | 45.47 | 3645.802 | 782.296 | -8.853 | 18 | 184 | 25.5 | 57.9 | 25.5 | 58.2 | 0 | 0 | - | - | 28.2 | 53.8 | 0 | 0 | 0 | 0 | 28.7 | 29.1 | 27.7 | 1.42 | 6.4 | 6.4 | 0 | 28.1 | 40.2 | 28.7 | 1.49 | 16.5 | 4.5 | 23.4 | 23.6 | 27.7 | 1.43 | 1.44 | 1.48 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:10:00 | 2544.62 | 2476.44 | 825398.8 | 802948.58 | 45.55 | 3645.802 | 782.296 | -11.418 | 18 | 184 | 25.5 | 58 | 25.5 | 58.2 | 0 | 0 | - | - | 28.2 | 53.8 | 0 | 0 | 0 | 0 | 28.7 | 29 | 27.8 | 1.42 | 6.2 | 6.2 | 0 | 27.9 | 39.1 | 28.2 | 1.49 | 15.2 | 4.4 | 23.5 | 23.7 | 27.7 | 1.44 | 1.45 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:15:00 | 2544.62 | 2477.32 | 825398.8 | 802949.42 | 45.62 | 3645.802 | 782.296 | -8.795 | 18 | 184 | 25.4 | 58 | 25.4 | 58.2 | 0 | 0 | - | - | 28.2 | 53.8 | 0 | 0 | 0 | 0 | 28.7 | 28.9 | 27.8 | 1.43 | 6 | 6 | 0 | 28 | 38 | 27.9 | 1.49 | 14 | 4.4 | 23.6 | 23.7 | 27.6 | 1.44 | 1.45 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:20:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3645.802 | 782.296 | -0.038 | 18 | 184 | 25.4 | 58 | 25.4 | 58.3 | 0 | 0 | - | - | 28.1 | 53.8 | 0 | 0 | 0 | 0 | 28.6 | 28.8 | 27.7 | 1.43 | 5.8 | 5.8 | 0 | 27.9 | 36.9 | 27.7 | 1.49 | 12.8 | 4.3 | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:25:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3638.421 | 789.676 | -0.031 | 18 | 184 | 25.3 | 58.2 | 25.4 | 58.3 | 0 | 0 | - | - | 28.1 | 53.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:30:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3638.421 | 789.676 | -0.025 | 18 | 184 | 25.3 | 58.3 | 25.4 | 58.4 | 0 | 0 | - | - | 28.1 | 53.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:35:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3638.421 | 789.676 | -0.022 | 18 | 184 | 25.3 | 58.3 | 25.4 | 58.4 | 0 | 0 | - | - | 28 | 53.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:40:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3638.421 | 789.676 | -0.022 | 18 | 184 | 25.2 | 58.3 | 25.3 | 58.4 | 0 | 0 | - | - | 27.9 | 53.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:45:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3638.421 | 789.676 | -0.022 | 18 | 184 | 25.2 | 58.4 | 25.3 | 58.4 | 0 | 0 | - | - | 27.9 | 53.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:50:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3631.041 | 797.056 | -0.022 | 18 | 184 | 25.2 | 58.4 | 25.3 | 58.4 | 0 | 0 | - | - | 27.8 | 54 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 22:55:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3631.041 | 797.056 | -0.022 | 18 | 184 | 25.1 | 58.5 | 25.3 | 58.4 | 0 | 0 | - | - | 27.7 | 54 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:00:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3631.041 | 797.056 | -0.022 | 18 | 184 | 25.1 | 58.5 | 25.3 | 58.4 | 0 | 0 | - | - | 27.6 | 54.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:05:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3631.041 | 797.056 | -0.022 | 18 | 184 | 25.1 | 58.5 | 25.3 | 58.4 | 0 | 0 | - | - | 27.6 | 54.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:10:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3623.661 | 804.436 | -0.022 | 18 | 184 | 25.1 | 58.5 | 25.3 | 58.4 | 0 | 0 | - | - | 27.5 | 54.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:15:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3623.661 | 804.436 | -0.022 | 18 | 184 | 25 | 58.6 | 25.3 | 58.4 | 0 | 0 | - | - | 27.4 | 54.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:20:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3623.661 | 804.436 | -0.022 | 18 | 184 | 25 | 58.6 | 25.3 | 58.5 | 0 | 0 | - | - | 27.4 | 54.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:25:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3623.661 | 804.436 | -0.022 | 18 | 184 | 25 | 58.6 | 25.3 | 58.5 | 0 | 0 | - | - | 27.3 | 54.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:30:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3623.661 | 804.436 | -0.022 | 18 | 184 | 25 | 58.7 | 25.3 | 58.5 | 0 | 0 | - | - | 27.3 | 54.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:35:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3623.661 | 804.436 | -0.022 | 18 | 184 | 25 | 58.7 | 25.2 | 58.5 | 0 | 0 | - | - | 27.2 | 54.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:40:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3623.661 | 804.436 | -0.022 | 18 | 184 | 25 | 58.8 | 25.2 | 58.5 | 0 | 0 | - | - | 27.2 | 54.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:45:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3623.661 | 804.436 | -0.022 | 18 | 184 | 25 | 58.8 | 25.2 | 58.5 | 0 | 0 | - | - | 27.1 | 54.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:50:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3623.661 | 804.436 | -0.022 | 18 | 184 | 25 | 58.8 | 25.2 | 58.5 | 0 | 0 | - | - | 27.1 | 54.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-18/B18-ESS01 | 2026-06-02 23:55:00 | 2544.62 | 2477.92 | 825398.8 | 802950.02 | 45.67 | 3623.661 | 804.436 | -0.022 | 18 | 184 | 25 | 58.8 | 25.2 | 58.5 | 0 | 0 | - | - | 27 | 54.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -