## 5 minutes
Time range: | 2026-06-02 00:00:00 - 2026-06-02 23:59:59
Export time: | 2026-06-03 01:05:02
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge energy(kWh) | Total discharge energy(kWh) | Daily auxiliary power consumption(kWh) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge power(kW) | SOC(%) | Equivalent number of cycles | Battery cabin temperature 1(℃) | Battery cabin humidity 1(%) | Battery cabin temperature 2(℃) | Battery cabin humidity 2(%) | CO concentration 1(ppm) | CO concentration 2(ppm) | H2 concentration 1(ppm) | H2 concentration 2(ppm) | Control unit cabin temperature 1(℃) | Control unit cabin humidity 1(%) | Control status of EEV 1(step) | Control status of EEV 2(step) | Running status of outdoor fan 1(%) | Running status of outdoor fan 2(%) | Discharge temperature of compressor 1(℃) | Suction temperature of refrigerant system 1(℃) | Condenser outlet temperature of refrigerant system 1(℃) | Condenser outlet pressure of refrigerant system 1(Mpa) | Suction superheat degree of refrigerant system 1(℃) | Discharge superheat degree of compressor 1(℃) | Running status of outdoor fan 3(%) | Discharge temperature of compressor 2(℃) | Suction temperature of refrigerant system 2(℃) | Condenser outlet temperature of refrigerant system 2(℃) | Condenser outlet pressure of refrigerant system 2(Mpa) | Suction superheat degree of refrigerant system 2(℃) | Discharge superheat degree of compressor 2(℃) | Battery-side supply water temperature(℃) | Battery-side return water temperature(℃) | Air intake temperature(℃) | Discharge pressure of refrigerant system 1(Mpa) | Suction pressure of refrigerant system 1(Mpa) | Discharge pressure of refrigerant system 2(Mpa) | Suction pressure of refrigerant system 2(Mpa) | Running status of EEV 1(step) | Running status of EEV 2(step) | Compressor 1 running status(rpm) | Compressor 2 running status(rpm)
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:00:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 26 | 54.2 | 26 | 53.9 | 0 | 0 | - | - | 28.3 | 48.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:05:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 26 | 54.2 | 26 | 53.9 | 0 | 0 | - | - | 28.3 | 48.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:10:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 26 | 54.2 | 26 | 53.9 | 0 | 0 | - | - | 28.2 | 48.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:15:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 26 | 54.2 | 26 | 53.9 | 0 | 0 | - | - | 28.2 | 48.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:20:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 26 | 54.3 | 26 | 53.9 | 0 | 0 | - | - | 28.1 | 48.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:25:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.9 | 54.3 | 25.9 | 53.9 | 0 | 0 | - | - | 28.1 | 48.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:30:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.9 | 54.4 | 25.9 | 53.9 | 0 | 0 | - | - | 28 | 48.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:35:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.9 | 54.4 | 25.9 | 54 | 0 | 0 | - | - | 28 | 48.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:40:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.9 | 54.4 | 25.9 | 54 | 0 | 0 | - | - | 27.9 | 48.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:45:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.9 | 54.4 | 25.9 | 54 | 0 | 0 | - | - | 27.9 | 48.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:50:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.9 | 54.5 | 25.9 | 54 | 0 | 0 | - | - | 27.8 | 48.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 00:55:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.8 | 54.5 | 25.9 | 54 | 0 | 0 | - | - | 27.8 | 48.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:00:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.8 | 54.5 | 25.9 | 54 | 0 | 0 | - | - | 27.7 | 48.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:05:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.8 | 54.5 | 25.9 | 54 | 0 | 0 | - | - | 27.7 | 48.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:10:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.9 | 54.5 | 25.9 | 54 | 0 | 0 | - | - | 27.7 | 48.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:15:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.9 | 54.5 | 25.9 | 54 | 0 | 0 | - | - | 27.7 | 48.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:20:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.9 | 54.5 | 25.9 | 53.9 | 0 | 0 | - | - | 27.7 | 49 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:25:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 3809.359 | 663.467 | -0.022 | 15 | 184 | 25.9 | 54.5 | 26 | 53.9 | 0 | 0 | - | - | 27.6 | 49 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:30:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.9 | 54.4 | 25.9 | 54 | 0 | 0 | - | - | 27.6 | 49 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:35:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.9 | 54.5 | 25.8 | 54.1 | 0 | 0 | - | - | 27.6 | 49.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:40:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.9 | 54.5 | 25.8 | 54.2 | 0 | 0 | - | - | 27.6 | 49.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:45:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.9 | 54.5 | 25.8 | 54.2 | 0 | 0 | - | - | 27.6 | 49.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:50:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.2 | 0 | 0 | - | - | 27.6 | 49.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 01:55:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.2 | 0 | 0 | - | - | 27.6 | 49.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:00:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.2 | 0 | 0 | - | - | 27.5 | 49.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:05:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.2 | 0 | 0 | - | - | 27.5 | 49.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:10:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.2 | 0 | 0 | - | - | 27.5 | 49.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:15:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.2 | 0 | 0 | - | - | 27.5 | 49.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:20:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.2 | 0 | 0 | - | - | 27.5 | 49.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:25:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.3 | 0 | 0 | - | - | 27.5 | 49.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:30:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.3 | 0 | 0 | - | - | 27.5 | 49.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:35:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.3 | 0 | 0 | - | - | 27.5 | 49.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:40:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.3 | 0 | 0 | - | - | 27.4 | 49.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:45:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.3 | 0 | 0 | - | - | 27.4 | 49.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:50:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.3 | 0 | 0 | - | - | 27.4 | 49.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 02:55:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.4 | 25.7 | 54.3 | 0 | 0 | - | - | 27.4 | 49.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:00:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.4 | 25.7 | 54.3 | 0 | 0 | - | - | 27.4 | 49.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:05:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.4 | 25.7 | 54.4 | 0 | 0 | - | - | 27.4 | 49.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:10:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.4 | 25.7 | 54.4 | 0 | 0 | - | - | 27.4 | 49.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:15:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.4 | 25.7 | 54.4 | 0 | 0 | - | - | 27.4 | 49.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:20:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.4 | 0 | 0 | - | - | 27.3 | 49.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:25:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.7 | 54.4 | 0 | 0 | - | - | 27.3 | 49.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:30:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.5 | 25.6 | 54.4 | 0 | 0 | - | - | 27.3 | 49.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:35:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.8 | 54.6 | 25.6 | 54.5 | 0 | 0 | - | - | 27.3 | 49.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:40:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.7 | 54.6 | 25.6 | 54.5 | 0 | 0 | - | - | 27.2 | 49.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:45:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.7 | 54.6 | 25.5 | 54.5 | 0 | 0 | - | - | 27.2 | 49.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:50:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.7 | 54.7 | 25.5 | 54.6 | 0 | 0 | - | - | 27.2 | 49.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 03:55:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.6 | 54.7 | 25.5 | 54.6 | 0 | 0 | - | - | 27.2 | 49.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:00:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.6 | 54.8 | 25.5 | 54.7 | 0 | 0 | - | - | 27.1 | 49.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:05:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.6 | 54.8 | 25.4 | 54.7 | 0 | 0 | - | - | 27.1 | 49.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:10:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.5 | 54.9 | 25.4 | 54.8 | 0 | 0 | - | - | 27.1 | 49.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:15:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.5 | 55 | 25.4 | 54.8 | 0 | 0 | - | - | 27.1 | 49.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:20:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.5 | 55 | 25.3 | 54.8 | 0 | 0 | - | - | 27 | 50 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:25:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.4 | 55.1 | 25.3 | 54.9 | 0 | 0 | - | - | 27 | 50 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:30:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.4 | 55.1 | 25.3 | 54.9 | 0 | 0 | - | - | 27 | 50 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:35:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.4 | 55.2 | 25.3 | 55 | 0 | 0 | - | - | 27 | 50 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:40:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.3 | 55.2 | 25.2 | 55 | 0 | 0 | - | - | 27 | 50.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:45:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.3 | 55.3 | 25.2 | 55 | 0 | 0 | - | - | 27 | 50.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:50:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.3 | 55.3 | 25.2 | 55 | 0 | 0 | - | - | 26.9 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 04:55:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.3 | 55.4 | 25.2 | 55.1 | 0 | 0 | - | - | 26.9 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:00:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.4 | 25.2 | 55.1 | 0 | 0 | - | - | 26.9 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:05:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.4 | 25.2 | 55.1 | 0 | 0 | - | - | 26.9 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:10:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.5 | 25.2 | 55.1 | 0 | 0 | - | - | 26.9 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:15:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.5 | 25.1 | 55.2 | 0 | 0 | - | - | 26.8 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:20:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.5 | 25.1 | 55.2 | 0 | 0 | - | - | 26.8 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:25:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.5 | 25.1 | 55.2 | 0 | 0 | - | - | 26.8 | 50.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:30:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.5 | 25.1 | 55.2 | 0 | 0 | - | - | 26.8 | 50.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:35:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.5 | 25.1 | 55.2 | 0 | 0 | - | - | 26.8 | 50.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:40:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.5 | 25.1 | 55.2 | 0 | 0 | - | - | 26.8 | 50.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:45:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.5 | 25.1 | 55.2 | 0 | 0 | - | - | 26.8 | 50.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:50:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.5 | 25.1 | 55.2 | 0 | 0 | - | - | 26.8 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 05:55:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.5 | 25.1 | 55.2 | 0 | 0 | - | - | 26.8 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:00:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.5 | 25.2 | 55.1 | 0 | 0 | - | - | 26.8 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:05:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.2 | 55.4 | 25.2 | 55.1 | 0 | 0 | - | - | 26.8 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:10:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.3 | 55.3 | 25.2 | 55.1 | 0 | 0 | - | - | 26.9 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:15:00 | 0 | 0 | 825337.5 | 801133.18 | 0 | 0 | 0 | 0 | - | 184 | 25.3 | 55.3 | 25.2 | 55.1 | 0 | 0 | - | - | 26.9 | 50.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:20:00 | 0 | 0 | 825337.5 | 801133.18 | 0.04 | 3861.541 | 611.285 | -0.007 | 15 | 184 | 25.4 | 55.2 | 25.3 | 54.9 | 0 | 0 | - | - | 27 | 50 | 0 | 0 | 0 | 0 | 26 | 26.2 | 26.2 | 1.49 | 1.7 | 1.5 | 0 | 26.2 | 26.1 | 26.1 | 1.5 | 1.4 | 2 | 24.1 | 24.2 | 26.6 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:25:00 | 0 | 0 | 825337.5 | 801133.18 | 0.14 | 3816.813 | 656.013 | -2.423 | 15 | 184 | 25.4 | 55.1 | 25.4 | 54.8 | 0 | 0 | - | - | 27.1 | 49.9 | 0 | 0 | 0 | 0 | 26 | 26.3 | 26.3 | 1.49 | 1.7 | 1.5 | 0 | 26.2 | 26.2 | 26.1 | 1.5 | 1.4 | 2 | 23.9 | 24.1 | 26.7 | 1.52 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:30:00 | 3.56 | 0.22 | 825341.18 | 801133.4 | 0.22 | 3809.359 | 663.467 | 110.594 | 15 | 184 | 25.5 | 55.1 | 25.4 | 54.8 | 0 | 0 | - | - | 27.3 | 49.8 | 0 | 0 | 0 | 0 | 26.1 | 26.5 | 26.4 | 1.49 | 1.9 | 1.7 | 0 | 26.2 | 26.3 | 26.2 | 1.5 | 1.6 | 2.1 | 23.9 | 24.1 | 26.8 | 1.52 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:35:00 | 16.72 | 0.22 | 825354.42 | 801133.4 | 0.32 | 3809.359 | 663.467 | 218.339 | 15 | 184 | 25.5 | 55.1 | 25.5 | 54.7 | 0 | 0 | - | - | 27.4 | 49.7 | 0 | 0 | 0 | 0 | 26.3 | 26.6 | 26.5 | 1.49 | 2.1 | 1.9 | 0 | 26.3 | 26.5 | 26.3 | 1.5 | 1.8 | 2.3 | 23.9 | 24.1 | 26.9 | 1.51 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:40:00 | 37.62 | 0.22 | 825375.4 | 801133.4 | 0.4 | 3809.359 | 663.467 | 299.822 | 16 | 184 | 25.6 | 55 | 25.6 | 54.6 | 0 | 0 | - | - | 27.4 | 49.6 | 0 | 0 | 0 | 0 | 26.4 | 26.8 | 26.6 | 1.49 | 2.3 | 2 | 0 | 26.4 | 26.6 | 26.4 | 1.49 | 1.9 | 2.4 | 23.9 | 24.1 | 27 | 1.52 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:45:00 | 71.74 | 0.22 | 825409.68 | 801133.4 | 0.51 | 3779.541 | 693.285 | 425.652 | 17 | 184 | 25.7 | 54.9 | 25.7 | 54.5 | 0 | 0 | - | - | 27.5 | 49.5 | 0 | 0 | 0 | 0 | 26.6 | 26.9 | 26.7 | 1.49 | 2.4 | 2.2 | 0 | 26.5 | 26.7 | 26.5 | 1.5 | 2 | 2.5 | 23.9 | 24.1 | 27.5 | 1.51 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:50:00 | 108.26 | 0.22 | 825446.12 | 801133.4 | 0.61 | 3734.812 | 738.014 | 362.646 | 18 | 184 | 25.8 | 54.7 | 25.7 | 54.4 | 0 | 0 | - | - | 27.6 | 49.4 | 0 | 0 | 0 | 0 | 26.8 | 27.2 | 26.9 | 1.49 | 2.7 | 2.4 | 0 | 26.7 | 26.9 | 26.7 | 1.5 | 2.2 | 2.6 | 23.9 | 24.1 | 28.2 | 1.52 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 06:55:00 | 138.18 | 0.22 | 825475.84 | 801133.4 | 0.71 | 3719.902 | 752.924 | 247.799 | 18 | 184 | 26 | 54.5 | 26 | 54.1 | 0 | 0 | - | - | 27.8 | 49.3 | 0 | 0 | 0 | 0 | 27.1 | 27.6 | 27.2 | 1.49 | 3 | 2.7 | 0 | 27 | 27.2 | 26.9 | 1.5 | 2.5 | 2.9 | 24 | 24.1 | 28.6 | 1.52 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:00:00 | 146.3 | 0.74 | 825483.8 | 801134.16 | 0.81 | 3704.993 | 767.833 | -121.114 | 18 | 184 | 26.2 | 54.2 | 26.2 | 53.8 | 0 | 0 | - | - | 27.9 | 49.2 | 0 | 0 | 0 | 0 | 27.5 | 28 | 27.6 | 1.49 | 3.4 | 3 | 0 | 27.3 | 27.5 | 27.3 | 1.5 | 2.7 | 3.2 | 24 | 24.2 | 28.7 | 1.52 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:05:00 | 146.3 | 25.94 | 825483.8 | 801159.84 | 0.92 | 3727.357 | 745.469 | -467.971 | 18 | 184 | 26.5 | 53.9 | 26.4 | 53.5 | 0 | 0 | - | - | 28.1 | 49 | 0 | 0 | 0 | 0 | 27.8 | 28.4 | 27.8 | 1.49 | 3.7 | 3.3 | 0 | 27.5 | 27.8 | 27.6 | 1.5 | 3 | 3.4 | 24.1 | 24.2 | 28.8 | 1.52 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:10:00 | 146.3 | 86.52 | 825483.8 | 801221.3 | 1.05 | 3786.996 | 685.83 | -1007.107 | 17 | 184 | 26.7 | 53.7 | 26.6 | 53.3 | 0 | 0 | - | - | 28.3 | 48.8 | 0 | 0 | 0 | 0 | 28 | 28.6 | 28 | 1.5 | 3.9 | 3.4 | 0 | 27.8 | 28.1 | 27.8 | 1.51 | 3.2 | 3.5 | 24.1 | 24.3 | 28.9 | 1.52 | 1.53 | 1.51 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:15:00 | 146.3 | 149.6 | 825483.8 | 801283.96 | 1.19 | 3861.541 | 611.285 | -654.186 | 14 | 184 | 26.9 | 53.4 | 26.8 | 53 | 0 | 0 | - | - | 28.4 | 48.6 | 0 | 0 | 0 | 0 | 28.3 | 28.9 | 28.3 | 1.5 | 4 | 3.6 | 0 | 28 | 28.3 | 28.1 | 1.51 | 3.3 | 3.7 | 24.3 | 24.4 | 29.1 | 1.53 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:20:00 | 148.16 | 169.52 | 825485.74 | 801302.7 | 1.31 | 3891.36 | 581.466 | 3.983 | 14 | 184 | 27 | 53.2 | 27 | 52.8 | 0 | 0 | - | - | 28.6 | 48.5 | 0 | 0 | 0 | 0 | 28.5 | 29.1 | 28.6 | 1.51 | 4.1 | 3.7 | 0 | 28.3 | 28.6 | 28.3 | 1.52 | 3.4 | 3.7 | 24.4 | 24.6 | 29.2 | 1.54 | 1.54 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:25:00 | 148.32 | 182.02 | 825485.82 | 801315.94 | 1.43 | 3891.36 | 581.466 | -513.019 | 14 | 184 | 27.2 | 53.1 | 27.1 | 52.7 | 0 | 0 | - | - | 28.7 | 48.3 | 0 | 0 | 0 | 0 | 28.8 | 29.3 | 28.7 | 1.51 | 4.3 | 3.8 | 0 | 28.5 | 28.8 | 28.6 | 1.52 | 3.5 | 3.9 | 24.5 | 24.7 | 28.6 | 1.54 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:30:00 | 148.32 | 213.18 | 825485.82 | 801346.56 | 1.56 | 3936.09 | 536.736 | -124.336 | 13 | 184 | 27.3 | 52.9 | 27.2 | 52.6 | 0 | 0 | - | - | 28.8 | 48.2 | 0 | 0 | 0 | 0 | 28.8 | 29.4 | 28.7 | 1.52 | 4.2 | 3.8 | 0 | 28.6 | 28.9 | 28.6 | 1.52 | 3.5 | 3.9 | 24.6 | 24.7 | 28.7 | 1.54 | 1.55 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:35:00 | 158.3 | 214.82 | 825496.04 | 801348 | 1.67 | 3928.635 | 544.191 | 243.206 | 13 | 184 | 27.4 | 52.9 | 27.3 | 52.5 | 0 | 0 | - | - | 29 | 48.2 | 0 | 0 | 0 | 0 | 28.9 | 29.4 | 28.7 | 1.52 | 4.2 | 3.8 | 0 | 28.7 | 29 | 28.7 | 1.53 | 3.6 | 3.9 | 24.7 | 24.8 | 28.8 | 1.54 | 1.55 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:40:00 | 174.74 | 214.82 | 825512.36 | 801348 | 1.79 | 3913.725 | 559.101 | 84.262 | 13 | 184 | 27.5 | 52.8 | 27.4 | 52.4 | 0 | 0 | - | - | 29.1 | 48.1 | 0 | 0 | 0 | 0 | 29 | 29.4 | 28.8 | 1.52 | 4.2 | 4 | 0 | 28.8 | 29.1 | 28.8 | 1.53 | 3.6 | 3.9 | 24.7 | 24.8 | 29 | 1.54 | 1.55 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:45:00 | 179.56 | 214.82 | 825517.48 | 801348 | 1.91 | 3906.27 | 566.556 | 190.596 | 14 | 184 | 27.6 | 52.7 | 27.5 | 52.4 | 0 | 0 | - | - | 29.2 | 48 | 0 | 0 | 0 | 0 | 29.2 | 29.4 | 29 | 1.52 | 4.2 | 4.1 | 0 | 28.9 | 29.2 | 28.8 | 1.53 | 3.7 | 4 | 24.7 | 24.8 | 29.4 | 1.54 | 1.55 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:50:00 | 207.3 | 214.82 | 825545.26 | 801348 | 2.03 | 3876.45 | 596.376 | 196.568 | 14 | 184 | 27.7 | 52.6 | 27.6 | 52.3 | 0 | 0 | - | - | 29.3 | 47.9 | 0 | 0 | 0 | 0 | 29.3 | 29.4 | 29.2 | 1.52 | 4.2 | 4.2 | 0 | 29 | 29.3 | 29 | 1.53 | 3.8 | 4.1 | 24.7 | 24.8 | 29.7 | 1.55 | 1.55 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 07:55:00 | 246.48 | 214.82 | 825584.32 | 801348 | 2.16 | 3846.631 | 626.195 | 311.387 | 15 | 184 | 27.8 | 52.5 | 27.8 | 52.1 | 0 | 0 | - | - | 29.4 | 47.7 | 0 | 0 | 0 | 0 | 29.6 | 29.6 | 29.5 | 1.52 | 4.3 | 4.4 | 0 | 29.1 | 29.5 | 29.2 | 1.53 | 4 | 4.3 | 24.8 | 24.9 | 30.1 | 1.55 | 1.55 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:00:00 | 259.88 | 218.22 | 825597.38 | 801351.96 | 2.28 | 3831.722 | 641.104 | -319.824 | 15 | 184 | 28 | 52.3 | 27.9 | 52 | 0 | 0 | - | - | 29.6 | 47.6 | 0 | 0 | 0 | 0 | 29.8 | 29.8 | 29.7 | 1.52 | 4.5 | 4.6 | 0 | 29.4 | 29.7 | 29.4 | 1.53 | 4.1 | 4.5 | 24.7 | 24.9 | 30.6 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:05:00 | 259.88 | 242.42 | 825597.38 | 801375.92 | 2.4 | 3846.631 | 626.195 | -217.224 | 15 | 184 | 28.2 | 52.1 | 28.1 | 51.8 | 0 | 0 | - | - | 29.8 | 47.4 | 0 | 0 | 0 | 0 | 30 | 29.9 | 30 | 1.52 | 4.6 | 4.8 | 0 | 29.6 | 29.8 | 29.7 | 1.53 | 4.2 | 4.7 | 24.8 | 24.9 | 30.4 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:10:00 | 259.88 | 259.2 | 825597.38 | 801392.44 | 2.52 | 3876.45 | 596.376 | -4.356 | 14 | 184 | 28.4 | 51.9 | 28.3 | 51.6 | 0 | 0 | - | - | 30 | 47.2 | 0 | 0 | 0 | 0 | 30.2 | 30.1 | 30.2 | 1.53 | 4.7 | 4.9 | 0 | 29.8 | 29.9 | 29.9 | 1.54 | 4.3 | 4.9 | 24.9 | 25 | 30.7 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:15:00 | 259.88 | 260.56 | 825597.38 | 801393.74 | 2.63 | 3876.45 | 596.376 | -1.966 | 14 | 184 | 28.6 | 51.6 | 28.4 | 51.4 | 0 | 0 | - | - | 30.2 | 47 | 0 | 0 | 0 | 0 | 30.3 | 30.2 | 30.3 | 1.53 | 4.8 | 5 | 0 | 29.9 | 30 | 30.1 | 1.54 | 4.4 | 4.9 | 24.9 | 25.1 | 30.6 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:20:00 | 259.88 | 268.1 | 825597.38 | 801401.88 | 2.75 | 3883.905 | 588.921 | -236.627 | 14 | 184 | 28.9 | 51.4 | 28.6 | 51.3 | 0 | 0 | - | - | 30.3 | 46.8 | 0 | 0 | 0 | 0 | 30.4 | 30.3 | 30.4 | 1.53 | 4.8 | 5.1 | 0 | 30.1 | 30.1 | 30.3 | 1.54 | 4.4 | 5.1 | 25 | 25.1 | 30.7 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:25:00 | 259.88 | 287.2 | 825597.38 | 801420.58 | 2.86 | 3898.815 | 574.011 | -103.536 | 14 | 184 | 29 | 51.2 | 28.8 | 51.1 | 0 | 0 | - | - | 30.5 | 46.7 | 0 | 0 | 0 | 0 | 30.6 | 30.4 | 30.6 | 1.53 | 4.9 | 5.2 | 0 | 30.2 | 30.1 | 30.4 | 1.54 | 4.4 | 5.2 | 25 | 25.1 | 30.8 | 1.56 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:30:00 | 261.7 | 292.72 | 825599.2 | 801426.2 | 2.96 | 3906.27 | 566.556 | -206.769 | 14 | 184 | 29.3 | 50.9 | 28.9 | 50.9 | 0 | 0 | - | - | 30.7 | 46.5 | 0 | 0 | 0 | 0 | 30.7 | 30.5 | 30.7 | 1.53 | 5 | 5.3 | 0 | 30.3 | 30.2 | 30.6 | 1.54 | 4.5 | 5.3 | 25 | 25.2 | 31.2 | 1.56 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:35:00 | 261.7 | 319.54 | 825599.2 | 801453.24 | 3.08 | 3965.91 | 506.916 | -207.339 | 13 | 184 | 29.4 | 50.7 | 29.2 | 50.7 | 0 | 0 | - | - | 30.8 | 46.4 | 0 | 0 | 0 | 0 | 30.8 | 30.6 | 30.8 | 1.53 | 5.1 | 5.4 | 0 | 30.4 | 30.2 | 30.7 | 1.54 | 4.5 | 5.3 | 25.1 | 25.2 | 31.2 | 1.56 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:40:00 | 261.7 | 329.86 | 825599.2 | 801463.18 | 3.19 | 3980.818 | 492.008 | -15.706 | 12 | 184 | 29.7 | 50.4 | 29.4 | 50.4 | 0 | 0 | - | - | 31 | 46.3 | 0 | 0 | 0 | 0 | 30.9 | 30.7 | 30.9 | 1.53 | 5.1 | 5.5 | 0 | 30.6 | 30.3 | 30.9 | 1.54 | 4.5 | 5.4 | 25.1 | 25.2 | 31.2 | 1.56 | 1.56 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:45:00 | 267.12 | 330.62 | 825605.28 | 801463.8 | 3.29 | 3973.364 | 499.462 | 262.303 | 12 | 184 | 29.9 | 50 | 29.6 | 50.1 | 0 | 0 | - | - | 31.1 | 46.3 | 0 | 0 | 0 | 0 | 31 | 30.8 | 31.1 | 1.53 | 5.3 | 5.6 | 0 | 30.7 | 30.5 | 31 | 1.55 | 4.6 | 5.5 | 25.1 | 25.3 | 31.3 | 1.56 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:50:00 | 293.38 | 330.62 | 825631.54 | 801463.8 | 3.4 | 3943.545 | 529.281 | 406.976 | 13 | 184 | 30.2 | 49.8 | 29.8 | 49.8 | 0 | 0 | - | - | 31.2 | 46.1 | 0 | 0 | 0 | 0 | 31.2 | 30.9 | 31.2 | 1.53 | 5.4 | 5.7 | 0 | 30.8 | 30.6 | 31.1 | 1.55 | 4.7 | 5.6 | 25.2 | 25.3 | 31.6 | 1.56 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 08:55:00 | 337.54 | 330.62 | 825676.1 | 801463.8 | 3.51 | 3891.36 | 581.466 | 617.541 | 14 | 184 | 30.5 | 49.4 | 30.1 | 49.5 | 0 | 0 | - | - | 31.4 | 46 | 0 | 0 | 0 | 0 | 31.3 | 31 | 31.3 | 1.53 | 5.4 | 5.8 | 0 | 30.9 | 30.7 | 31.3 | 1.55 | 4.7 | 5.7 | 25.2 | 25.3 | 31.9 | 1.56 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:00:00 | 387.88 | 330.62 | 825726.26 | 801463.8 | 3.63 | 3846.632 | 626.194 | 349.722 | 15 | 184 | 30.8 | 49.1 | 30.4 | 49.2 | 0 | 0 | - | - | 31.5 | 45.9 | 0 | 0 | 0 | 0 | 31.4 | 31.1 | 31.6 | 1.54 | 5.5 | 6 | 0 | 31 | 30.8 | 31.5 | 1.55 | 4.9 | 5.8 | 25.2 | 25.3 | 32 | 1.56 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:05:00 | 406.16 | 330.62 | 825743.68 | 801463.8 | 3.74 | 3831.723 | 641.103 | 27.445 | 16 | 184 | 31.1 | 48.7 | 30.6 | 49 | 0 | 0 | - | - | 31.7 | 45.8 | 0 | 0 | 0 | 0 | 31.6 | 31.3 | 31.7 | 1.54 | 5.6 | 6.1 | 0 | 31.2 | 30.9 | 31.7 | 1.55 | 5 | 6 | 25.2 | 25.4 | 32.3 | 1.56 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:10:00 | 407.66 | 334.96 | 825745.3 | 801468.14 | 3.85 | 3831.723 | 641.103 | 140.53 | 15 | 184 | 31.4 | 48.4 | 30.8 | 48.8 | 0 | 0 | - | - | 31.9 | 45.7 | 0 | 0 | 0 | 0 | 31.8 | 31.4 | 31.9 | 1.54 | 5.7 | 6.3 | 0 | 31.3 | 31 | 31.9 | 1.55 | 5.1 | 6.1 | 25.2 | 25.4 | 32.5 | 1.56 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:15:00 | 437.18 | 334.96 | 825774.98 | 801468.14 | 3.96 | 3801.904 | 670.922 | 669.57 | 16 | 184 | 31.7 | 48 | 31 | 48.5 | 0 | 0 | - | - | 32 | 45.5 | 0 | 0 | 0 | 0 | 31.9 | 31.5 | 32.1 | 1.54 | 5.8 | 6.4 | 0 | 31.5 | 31.1 | 32.1 | 1.55 | 5.2 | 6.2 | 25.3 | 25.5 | 32.8 | 1.57 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:20:00 | 495.06 | 334.96 | 825833.94 | 801468.14 | 4.09 | 3749.721 | 723.105 | 678.862 | 18 | 184 | 31.9 | 47.7 | 31.2 | 48.3 | 0 | 0 | - | - | 32.2 | 45.4 | 0 | 0 | 0 | 0 | 32.2 | 31.7 | 32.3 | 1.54 | 6 | 6.6 | 0 | 31.7 | 31.3 | 32.3 | 1.55 | 5.3 | 6.4 | 25.3 | 25.5 | 32.6 | 1.57 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:25:00 | 554.26 | 334.96 | 825892.02 | 801468.14 | 4.22 | 3682.63 | 790.196 | 518.85 | 19 | 184 | 32.2 | 47.5 | 31.4 | 48.1 | 0 | 0 | - | - | 32.4 | 45.2 | 0 | 0 | 0 | 0 | 32.3 | 31.7 | 32.4 | 1.54 | 6 | 6.7 | 0 | 31.8 | 31.4 | 32.4 | 1.55 | 5.4 | 6.5 | 25.4 | 25.5 | 32.9 | 1.57 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:30:00 | 588.96 | 334.96 | 825926.96 | 801468.14 | 4.34 | 3637.902 | 834.924 | 235.106 | 20 | 184 | 32.4 | 47.3 | 31.6 | 48 | 0 | 0 | - | - | 32.6 | 45.1 | 0 | 0 | 0 | 0 | 32.5 | 31.7 | 32.6 | 1.54 | 5.9 | 6.8 | 0 | 32 | 31.4 | 32.6 | 1.55 | 5.5 | 6.7 | 25.4 | 25.6 | 33.4 | 1.57 | 1.58 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:35:00 | 602.44 | 335.3 | 825939.98 | 801468.48 | 4.46 | 3637.902 | 834.924 | 13.808 | 20 | 184 | 32.5 | 47.2 | 31.7 | 47.9 | 0 | 0 | - | - | 32.8 | 45 | 0 | 0 | 0 | 0 | 32.7 | 31.9 | 32.7 | 1.55 | 6 | 6.9 | 0 | 32.1 | 31.6 | 32.7 | 1.55 | 5.5 | 6.7 | 25.5 | 25.6 | 33.3 | 1.57 | 1.58 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:40:00 | 602.62 | 348.26 | 825940.12 | 801481.64 | 4.57 | 3637.902 | 834.924 | -80.631 | 20 | 184 | 32.7 | 47 | 31.8 | 47.8 | 0 | 0 | - | - | 32.9 | 44.9 | 0 | 0 | 0 | 0 | 32.8 | 31.9 | 32.9 | 1.55 | 6.1 | 7 | 0 | 32.3 | 31.6 | 32.9 | 1.56 | 5.6 | 6.9 | 25.5 | 25.7 | 33.7 | 1.58 | 1.58 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:45:00 | 603.08 | 355.98 | 825940.58 | 801489.38 | 4.69 | 3637.902 | 834.924 | -70.977 | 19 | 184 | 32.8 | 46.8 | 32 | 47.6 | 0 | 0 | - | - | 33.1 | 44.7 | 0 | 0 | 0 | 0 | 33 | 32 | 33.1 | 1.55 | 6.1 | 7.2 | 0 | 32.4 | 31.8 | 33.1 | 1.56 | 5.6 | 7 | 25.6 | 25.7 | 34.1 | 1.58 | 1.58 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:50:00 | 603.08 | 372.64 | 825940.58 | 801506.06 | 4.81 | 3667.721 | 805.105 | -191.762 | 19 | 184 | 33 | 46.7 | 32.1 | 47.5 | 0 | 0 | - | - | 33.3 | 44.6 | 0 | 0 | 0 | 0 | 33.1 | 32.1 | 33.3 | 1.55 | 6.1 | 7.3 | 0 | 32.6 | 31.9 | 33.3 | 1.56 | 5.7 | 7.1 | 25.6 | 25.7 | 33.6 | 1.58 | 1.58 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 09:55:00 | 620.5 | 374.7 | 825959.08 | 801507.88 | 4.93 | 3660.266 | 812.56 | 567.404 | 19 | 184 | 33.1 | 46.6 | 32.2 | 47.4 | 0 | 0 | - | - | 33.5 | 44.5 | 0 | 0 | 0 | 0 | 33.2 | 32.2 | 33.3 | 1.55 | 6.2 | 7.4 | 0 | 32.7 | 31.9 | 33.4 | 1.56 | 5.7 | 7.2 | 25.7 | 25.8 | 33.6 | 1.58 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:00:00 | 649.7 | 374.7 | 825987.44 | 801507.88 | 5.05 | 3637.902 | 834.924 | 7.501 | 20 | 184 | 33.2 | 46.5 | 32.3 | 47.4 | 0 | 0 | - | - | 33.5 | 44.5 | 0 | 0 | 0 | 0 | 33.3 | 32.2 | 33.4 | 1.56 | 6.2 | 7.4 | 0 | 32.8 | 31.9 | 33.6 | 1.56 | 5.7 | 7.2 | 25.7 | 25.8 | 33.5 | 1.58 | 1.59 | 1.57 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:05:00 | 659.82 | 374.7 | 825997.72 | 801507.88 | 5.16 | 3622.992 | 849.834 | 394.88 | 20 | 184 | 33.2 | 46.5 | 32.3 | 47.4 | 0 | 0 | - | - | 33.6 | 44.4 | 0 | 0 | 0 | 0 | 33.3 | 32.3 | 33.4 | 1.55 | 6.2 | 7.4 | 0 | 32.8 | 31.8 | 33.6 | 1.56 | 5.6 | 7.2 | 25.7 | 25.8 | 33.5 | 1.58 | 1.59 | 1.57 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:10:00 | 691.86 | 374.7 | 826029.84 | 801507.88 | 5.28 | 3585.717 | 887.109 | 323.579 | 21 | 184 | 33.3 | 46.5 | 32.3 | 47.5 | 0 | 0 | - | - | 33.7 | 44.4 | 0 | 0 | 0 | 0 | 33.3 | 32.3 | 33.4 | 1.56 | 6.2 | 7.4 | 0 | 32.9 | 31.8 | 33.6 | 1.56 | 5.5 | 7.2 | 25.7 | 25.8 | 33.7 | 1.58 | 1.59 | 1.57 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:15:00 | 725.88 | 374.7 | 826064.1 | 801507.88 | 5.41 | 3540.987 | 931.839 | 461.569 | 22 | 184 | 33.3 | 46.5 | 32.3 | 47.5 | 0 | 0 | - | - | 33.8 | 44.4 | 0 | 0 | 0 | 0 | 33.4 | 32.4 | 33.6 | 1.56 | 6.3 | 7.5 | 0 | 32.9 | 31.8 | 33.7 | 1.57 | 5.6 | 7.3 | 25.8 | 25.9 | 33.6 | 1.58 | 1.59 | 1.57 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:20:00 | 775.38 | 374.7 | 826113.62 | 801507.88 | 5.54 | 3496.262 | 976.564 | 553 | 23 | 184 | 33.7 | 46.2 | 32 | 48 | 0 | 0 | - | - | 33.9 | 44.4 | 0 | 0 | 0 | 0 | 33.6 | 32.5 | 33.7 | 1.56 | 6.4 | 7.6 | 0 | 33 | 31.9 | 33.8 | 1.57 | 5.6 | 7.4 | 25.7 | 25.9 | 33.7 | 1.58 | 1.59 | 1.57 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:25:00 | 812.92 | 374.7 | 826151.4 | 801507.88 | 5.67 | 3458.988 | 1013.838 | 388.437 | 24 | 184 | 34 | 45.9 | 31.7 | 48.5 | 0 | 0 | - | - | 34 | 44.3 | 0 | 0 | 0 | 0 | 33.6 | 32.6 | 33.8 | 1.56 | 6.4 | 7.6 | 0 | 33.1 | 32 | 33.8 | 1.57 | 5.7 | 7.4 | 25.8 | 26 | 34.4 | 1.59 | 1.59 | 1.57 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:30:00 | 831.08 | 374.7 | 826168.66 | 801507.88 | 5.79 | 3436.623 | 1036.203 | 28.805 | 24 | 184 | 33.9 | 45.9 | 32 | 48.2 | 0 | 0 | - | - | 34.1 | 44.2 | 0 | 0 | 0 | 0 | 33.8 | 32.7 | 33.9 | 1.56 | 6.5 | 7.8 | 0 | 33.3 | 32.1 | 34 | 1.57 | 5.8 | 7.5 | 25.9 | 26 | 33.9 | 1.59 | 1.59 | 1.57 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:35:00 | 841.76 | 374.7 | 826179.3 | 801507.88 | 5.9 | 3429.168 | 1043.658 | 83.108 | 25 | 184 | 33.7 | 46.2 | 32.3 | 47.9 | 0 | 0 | - | - | 34.3 | 44.1 | 0 | 0 | 0 | 0 | 33.8 | 32.7 | 33.9 | 1.56 | 6.5 | 7.7 | 0 | 33.3 | 32.2 | 34 | 1.57 | 5.8 | 7.6 | 25.9 | 26.1 | 34.6 | 1.59 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:40:00 | 855.8 | 374.7 | 826193.6 | 801507.88 | 6 | 3406.803 | 1066.023 | 116.224 | 25 | 184 | 33.7 | 46.3 | 32.5 | 47.7 | 0 | 0 | - | - | 34.4 | 44 | 0 | 0 | 0 | 0 | 34 | 32.8 | 34.1 | 1.56 | 6.5 | 7.8 | 0 | 33.4 | 32.3 | 34.2 | 1.57 | 5.8 | 7.6 | 25.9 | 26.1 | 34.5 | 1.59 | 1.6 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:45:00 | 858.56 | 381.42 | 826196.06 | 801514.8 | 6.11 | 3406.803 | 1066.023 | -179.086 | 25 | 184 | 33.8 | 46.3 | 32.6 | 47.6 | 0 | 0 | - | - | 34.5 | 43.9 | 0 | 0 | 0 | 0 | 34.1 | 32.9 | 34.1 | 1.57 | 6.6 | 7.9 | 0 | 33.6 | 32.4 | 34.2 | 1.57 | 5.9 | 7.8 | 25.9 | 26.1 | 34.6 | 1.59 | 1.6 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:50:00 | 869.76 | 384.02 | 826208.16 | 801517.2 | 6.23 | 3406.803 | 1066.023 | 425.495 | 25 | 184 | 33.8 | 46.3 | 32.7 | 47.4 | 0 | 0 | - | - | 34.7 | 43.9 | 0 | 0 | 0 | 0 | 34.1 | 33 | 34.1 | 1.57 | 6.7 | 8 | 0 | 33.7 | 32.4 | 34.3 | 1.57 | 5.9 | 7.8 | 26 | 26.1 | 34.1 | 1.59 | 1.6 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 10:55:00 | 906.54 | 384.02 | 826244.64 | 801517.2 | 6.36 | 3362.078 | 1110.753 | 278.019 | 26 | 184 | 33.9 | 46.3 | 32.9 | 47.3 | 0 | 0 | - | - | 34.8 | 43.8 | 0 | 0 | 0 | 0 | 34.1 | 33.1 | 34.1 | 1.57 | 6.8 | 7.9 | 0 | 33.7 | 32.5 | 34.3 | 1.58 | 6 | 7.8 | 26 | 26.2 | 33.7 | 1.59 | 1.6 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:00:00 | 930.96 | 384.02 | 826269.88 | 801517.2 | 6.48 | 3324.804 | 1148.024 | 452.509 | 27 | 184 | 33.9 | 46.3 | 32.9 | 47.3 | 0 | 0 | - | - | 34.8 | 43.8 | 0 | 0 | 0 | 0 | 34.2 | 33.1 | 34.1 | 1.57 | 6.8 | 8 | 0 | 33.7 | 32.6 | 34.2 | 1.58 | 6 | 7.9 | 26 | 26.2 | 33.4 | 1.6 | 1.6 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:05:00 | 997.62 | 384.02 | 826337.02 | 801517.2 | 6.62 | 3265.164 | 1207.662 | 873.207 | 28 | 184 | 33.8 | 46.4 | 32.9 | 47.3 | 0 | 0 | - | - | 34.8 | 43.8 | 0 | 0 | 0 | 0 | 34.1 | 33.1 | 33.9 | 1.57 | 6.8 | 7.9 | 0 | 33.7 | 32.6 | 34.2 | 1.58 | 6 | 7.9 | 26.1 | 26.2 | 33.3 | 1.59 | 1.6 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:10:00 | 1061.78 | 384.14 | 826399.28 | 801517.32 | 6.75 | 3190.618 | 1282.208 | -48.311 | 30 | 184 | 33.8 | 46.5 | 33 | 47.3 | 0 | 0 | - | - | 34.9 | 43.8 | 0 | 0 | 0 | 0 | 34.1 | 33.1 | 33.9 | 1.57 | 6.6 | 7.9 | 0 | 33.7 | 32.6 | 34.1 | 1.58 | 5.9 | 7.7 | 26.2 | 26.3 | 33.9 | 1.6 | 1.6 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:15:00 | 1072.72 | 385.04 | 826410.72 | 801518.22 | 6.87 | 3183.164 | 1289.662 | 234.905 | 30 | 184 | 33.9 | 46.5 | 33 | 47.4 | 0 | 0 | - | - | 34.9 | 43.8 | 0 | 0 | 0 | 0 | 34.2 | 33.1 | 34.1 | 1.57 | 6.5 | 7.9 | 0 | 33.7 | 32.6 | 34.2 | 1.58 | 5.8 | 7.7 | 26.2 | 26.4 | 33.4 | 1.6 | 1.61 | 1.59 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:20:00 | 1093.54 | 385.04 | 826431.1 | 801518.22 | 7 | 3160.8 | 1312.026 | 69.299 | 31 | 184 | 34 | 46.5 | 33.1 | 47.3 | 0 | 0 | - | - | 35 | 43.8 | 0 | 0 | 0 | 0 | 34.2 | 33.1 | 34.1 | 1.57 | 6.6 | 7.9 | 0 | 33.8 | 32.6 | 34.2 | 1.58 | 5.8 | 7.8 | 26.3 | 26.4 | 33.8 | 1.6 | 1.61 | 1.59 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:25:00 | 1098.24 | 386 | 826435.94 | 801519.18 | 7.13 | 3153.345 | 1319.481 | 138.907 | 31 | 184 | 34.1 | 46.3 | 33.2 | 47.3 | 0 | 0 | - | - | 35 | 43.7 | 0 | 0 | 0 | 0 | 34.3 | 33.2 | 34.2 | 1.58 | 6.6 | 7.9 | 0 | 33.9 | 32.6 | 34.3 | 1.59 | 5.8 | 7.8 | 26.3 | 26.5 | 33.8 | 1.6 | 1.61 | 1.59 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:30:00 | 1136.34 | 386 | 826476.08 | 801519.18 | 7.27 | 3101.16 | 1371.666 | 899.821 | 32 | 184 | 34.2 | 46.3 | 33.4 | 47.1 | 0 | 0 | - | - | 35.1 | 43.7 | 0 | 0 | 0 | 0 | 34.4 | 33.2 | 34.4 | 1.58 | 6.6 | 8 | 0 | 34 | 32.7 | 34.4 | 1.59 | 5.8 | 7.8 | 26.4 | 26.6 | 33.8 | 1.61 | 1.61 | 1.59 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:35:00 | 1218.92 | 386 | 826557.46 | 801519.18 | 7.42 | 3019.158 | 1453.668 | 962.943 | 34 | 184 | 34.4 | 46.2 | 33.5 | 46.9 | 0 | 0 | - | - | 35.2 | 43.6 | 0 | 0 | 0 | 0 | 34.5 | 33.3 | 34.5 | 1.58 | 6.6 | 8 | 0 | 34 | 32.7 | 34.4 | 1.59 | 5.8 | 7.8 | 26.5 | 26.7 | 34.2 | 1.61 | 1.62 | 1.6 | 1.63 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:40:00 | 1310.58 | 386 | 826652.46 | 801519.18 | 7.59 | 2922.246 | 1550.58 | 1404.676 | 36 | 184 | 34.5 | 46 | 33.7 | 46.8 | 0 | 0 | - | - | 35.3 | 43.5 | 0 | 0 | 0 | 0 | 34.7 | 33.4 | 34.7 | 1.59 | 6.5 | 8 | 0 | 34.2 | 32.8 | 34.6 | 1.6 | 5.7 | 7.8 | 26.8 | 26.9 | 34.7 | 1.61 | 1.63 | 1.6 | 1.63 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:45:00 | 1429.1 | 386 | 826768.12 | 801519.18 | 7.77 | 2802.972 | 1669.854 | 1447.524 | 39 | 184 | 34.7 | 45.9 | 33.8 | 46.8 | 0 | 0 | - | - | 35.5 | 43.5 | 0 | 0 | 0 | 0 | 34.9 | 33.4 | 34.9 | 1.59 | 6.4 | 8.1 | 0 | 34.3 | 32.9 | 34.8 | 1.6 | 5.6 | 7.9 | 27.1 | 27.2 | 34.9 | 1.62 | 1.64 | 1.61 | 1.65 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:50:00 | 1559.34 | 386 | 826898.54 | 801519.18 | 8.51 | 2676.243 | 1796.583 | 1470.373 | 42 | 184 | 35 | 45.8 | 34 | 46.6 | 0 | 0 | - | - | 35.6 | 43.3 | 219 | 201 | 65.7 | 65.5 | 66.2 | 26.7 | 44.9 | 2.66 | 11.5 | 19.1 | 65.6 | 67.3 | 26.7 | 47.5 | 2.89 | 11.1 | 17.4 | 22.8 | 25.4 | 35.2 | 2.78 | 1.13 | 2.99 | 1.14 | 219 | 201 | 3039 | 3039
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 11:55:00 | 1682.24 | 386 | 827021.54 | 801519.18 | 9.54 | 2542.059 | 1930.767 | 1059.987 | 45 | 184 | 35.2 | 45.4 | 34.2 | 46.4 | 0 | 0 | - | - | 35.8 | 43.2 | 219 | 201 | 69.5 | 69.8 | 72.9 | 23.9 | 45.4 | 2.66 | 10.2 | 25.9 | 69.6 | 77.6 | 24.1 | 49.4 | 2.94 | 9.8 | 26.9 | 21.4 | 23.7 | 35.4 | 2.71 | 1.1 | 2.95 | 1.12 | 219 | 201 | 2761 | 2761
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:00:00 | 1736.5 | 386 | 827075.78 | 801519.18 | 10.39 | 2489.874 | 1982.952 | 438.978 | 46 | 184 | 35.5 | 45.1 | 34.3 | 46.2 | 0 | 0 | - | - | 36 | 43 | 219 | 201 | 62.4 | 62.1 | 70.2 | 23.6 | 43.6 | 2.52 | 9.2 | 25.5 | 62.4 | 75.7 | 23.7 | 47.4 | 2.78 | 9.1 | 27.5 | 21.5 | 23.5 | 34.2 | 2.58 | 1.13 | 2.83 | 1.14 | 219 | 201 | 2376 | 2376
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:05:00 | 1763.46 | 386 | 827101.4 | 801519.18 | 11.14 | 2452.599 | 2020.227 | 185.376 | 47 | 184 | 35.7 | 44.8 | 34.3 | 46.1 | 0 | 0 | - | - | 36.2 | 42.9 | 219 | 201 | 60.3 | 60.1 | 69 | 23.7 | 43.1 | 2.49 | 9.2 | 24.8 | 60.3 | 74.2 | 23.8 | 46.7 | 2.74 | 9.1 | 26.4 | 21.7 | 23.6 | 33.6 | 2.54 | 1.13 | 2.77 | 1.14 | 219 | 201 | 2301 | 2301
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:10:00 | 1769.36 | 387.1 | 827106.86 | 801520.7 | 11.84 | 2452.599 | 2020.227 | -173.752 | 47 | 184 | 35.9 | 44.5 | 34.3 | 46 | 0 | 0 | - | - | 36.3 | 42.8 | 219 | 201 | 60.4 | 60.2 | 68.5 | 23.8 | 43.1 | 2.48 | 9.3 | 24.4 | 60.3 | 73.5 | 23.8 | 46.7 | 2.74 | 9.1 | 25.9 | 21.7 | 23.6 | 35 | 2.55 | 1.13 | 2.78 | 1.14 | 219 | 201 | 2274 | 2274
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:15:00 | 1769.36 | 398.98 | 827106.86 | 801532.22 | 12.56 | 2452.599 | 2020.227 | -47.481 | 47 | 184 | 35.9 | 44.4 | 34.3 | 46 | 0 | 0 | - | - | 36.5 | 42.7 | 219 | 201 | 60.2 | 60.2 | 68.7 | 23.7 | 42.9 | 2.45 | 9.2 | 25.1 | 60.3 | 73.8 | 23.8 | 46.7 | 2.73 | 9.1 | 26.3 | 21.7 | 23.6 | 34.6 | 2.53 | 1.13 | 2.76 | 1.14 | 219 | 201 | 2211 | 2211
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:20:00 | 1776.9 | 400.4 | 827114.56 | 801533.58 | 13.23 | 2452.599 | 2020.227 | 138.097 | 47 | 184 | 35.9 | 44.3 | 34.2 | 46 | 0 | 0 | - | - | 36.6 | 42.7 | 219 | 201 | 58.2 | 58 | 67.6 | 23.7 | 42.7 | 2.48 | 8.9 | 23.5 | 58.2 | 72.3 | 23.7 | 46.1 | 2.7 | 8.8 | 25.3 | 21.6 | 23.5 | 33.7 | 2.52 | 1.13 | 2.74 | 1.14 | 219 | 201 | 2178 | 2178
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:25:00 | 1787.28 | 400.4 | 827124.94 | 801533.58 | 13.91 | 2452.599 | 2020.227 | 84.845 | 47 | 184 | 35.8 | 44.4 | 34.1 | 46.1 | 0 | 0 | - | - | 36.6 | 42.6 | 219 | 201 | 58.8 | 58.6 | 67.6 | 23.6 | 42.7 | 2.47 | 9.1 | 23.7 | 58.6 | 72.3 | 23.6 | 46 | 2.7 | 8.9 | 25.2 | 21.4 | 23.3 | 33.9 | 2.54 | 1.13 | 2.75 | 1.14 | 219 | 201 | 2163 | 2163
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:30:00 | 1789.34 | 407 | 827126.84 | 801540.68 | 14.59 | 2452.599 | 2020.227 | -351.316 | 47 | 184 | 35.8 | 44.4 | 34 | 46.2 | 0 | 0 | - | - | 36.6 | 42.6 | 219 | 201 | 58.7 | 59.1 | 67.8 | 23.4 | 43 | 2.48 | 8.8 | 23.7 | 58.6 | 72.3 | 23.4 | 46.2 | 2.7 | 8.6 | 25.2 | 21.3 | 23.2 | 33.9 | 2.52 | 1.13 | 2.74 | 1.14 | 219 | 201 | 2166 | 2166
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:35:00 | 1789.34 | 437.28 | 827126.84 | 801570.98 | 15.27 | 2460.054 | 2012.772 | -338.67 | 46 | 184 | 35.7 | 44.4 | 33.9 | 46.3 | 0 | 0 | - | - | 36.7 | 42.6 | 219 | 201 | 60.1 | 60.3 | 68 | 23.2 | 43.4 | 2.51 | 8.9 | 23.3 | 60.1 | 72.6 | 23.3 | 46.5 | 2.74 | 8.6 | 25 | 21.3 | 23.1 | 34.4 | 2.5 | 1.13 | 2.75 | 1.14 | 219 | 201 | 2142 | 2142
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:40:00 | 1789.34 | 477.56 | 827126.84 | 801611.6 | 15.95 | 2497.329 | 1975.497 | -401.956 | 45 | 184 | 35.6 | 44.5 | 33.7 | 46.4 | 0 | 0 | - | - | 36.7 | 42.5 | 219 | 200 | 60.1 | 60.2 | 68 | 23.2 | 43.1 | 2.49 | 8.8 | 23.7 | 60.1 | 72.6 | 23.2 | 46.6 | 2.73 | 8.6 | 25.1 | 21.2 | 23.1 | 34.9 | 2.53 | 1.13 | 2.76 | 1.14 | 219 | 200 | 2109 | 2109
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:45:00 | 1795.92 | 488.28 | 827133.58 | 801621.46 | 16.62 | 2534.604 | 1938.222 | 359.02 | 45 | 184 | 35.5 | 44.5 | 33.6 | 46.5 | 0 | 0 | - | - | 36.7 | 42.5 | 219 | 200 | 58.5 | 58.7 | 67.5 | 23.1 | 42.7 | 2.45 | 8.8 | 23.9 | 58.6 | 72.3 | 23.1 | 46.1 | 2.69 | 8.6 | 25.4 | 21 | 22.8 | 34.5 | 2.53 | 1.12 | 2.76 | 1.13 | 219 | 200 | 2130 | 2130
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:50:00 | 1806.58 | 500.08 | 827144.08 | 801634.12 | 17.29 | 2527.149 | 1945.677 | -439.2 | 45 | 184 | 35.4 | 44.5 | 33.5 | 46.6 | 0 | 0 | - | - | 36.7 | 42.5 | 219 | 200 | 59.5 | 59.3 | 67.4 | 22.7 | 42.7 | 2.47 | 8.9 | 23.5 | 59.6 | 72.3 | 22.8 | 46.2 | 2.71 | 8.5 | 25 | 20.8 | 22.7 | 35.1 | 2.56 | 1.12 | 2.76 | 1.13 | 219 | 199 | 2094 | 2094
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 12:55:00 | 1808.1 | 522.18 | 827145.9 | 801655.36 | 17.96 | 2542.059 | 1930.767 | 186.224 | 45 | 184 | 35.3 | 44.6 | 33.4 | 46.6 | 0 | 0 | - | - | 36.7 | 42.5 | 219 | 198 | 59.5 | 59.3 | 67.2 | 22.7 | 42.3 | 2.44 | 8.9 | 23.7 | 59.6 | 72.4 | 22.7 | 46.1 | 2.71 | 8.6 | 25.3 | 20.7 | 22.4 | 35 | 2.55 | 1.11 | 2.76 | 1.12 | 219 | 198 | 2100 | 2100
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:00:00 | 1811.1 | 532.74 | 827148.6 | 801666.94 | 18.62 | 2542.059 | 1930.767 | -343.715 | 44 | 184 | 35.2 | 44.6 | 33.3 | 46.6 | 0 | 0 | - | - | 36.7 | 42.4 | 219 | 195 | 60 | 59.8 | 67.6 | 22.6 | 42.9 | 2.48 | 8.5 | 23.5 | 60.1 | 72.7 | 22.7 | 46.5 | 2.73 | 8.5 | 25.3 | 20.7 | 22.3 | 35.4 | 2.53 | 1.11 | 2.75 | 1.12 | 219 | 195 | 2077 | 2077
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:05:00 | 1813.14 | 543.42 | 827151.1 | 801676.6 | 19.28 | 2579.33 | 1893.496 | 324.833 | 44 | 184 | 35.1 | 44.6 | 33.2 | 46.6 | 0 | 0 | - | - | 36.8 | 42.4 | 219 | 194 | 59.5 | 59.8 | 67.6 | 22.4 | 42.6 | 2.45 | 8.6 | 23.8 | 59.6 | 72.6 | 22.4 | 46.4 | 2.7 | 8.6 | 25.5 | 20.3 | 22.2 | 34.6 | 2.55 | 1.07 | 2.75 | 1.07 | 219 | 194 | 2400 | 2400
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:10:00 | 1848.36 | 543.42 | 827186.4 | 801676.6 | 20.04 | 2542.059 | 1930.767 | 336.321 | 45 | 184 | 35 | 44.6 | 33.2 | 46.6 | 0 | 0 | - | - | 36.8 | 42.3 | 219 | 194 | 61.6 | 61.5 | 68.9 | 21.9 | 43.1 | 2.47 | 9.2 | 24.9 | 61.4 | 73.8 | 22.1 | 46.5 | 2.73 | 9.3 | 26.4 | 19.7 | 21.7 | 33.9 | 2.55 | 1.08 | 2.75 | 1.08 | 219 | 194 | 2172 | 2172
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:15:00 | 1882.66 | 543.42 | 827220.36 | 801676.6 | 20.73 | 2497.329 | 1975.497 | 74.789 | 46 | 184 | 35 | 44.5 | 33 | 46.6 | 0 | 0 | - | - | 36.8 | 42.2 | 217 | 193 | 59 | 59.2 | 67.8 | 21.7 | 42.4 | 2.43 | 8.6 | 24.3 | 59.2 | 73 | 21.8 | 45.9 | 2.68 | 8.6 | 26.3 | 19.8 | 21.7 | 33.6 | 2.49 | 1.08 | 2.72 | 1.08 | 217 | 193 | 2181 | 2181
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:20:00 | 1883.18 | 554.78 | 827220.68 | 801688.84 | 21.4 | 2497.329 | 1975.497 | -521.086 | 45 | 184 | 34.8 | 44.6 | 32.9 | 46.8 | 0 | 0 | - | - | 36.8 | 42.2 | 217 | 193 | 60 | 59.7 | 67.6 | 21.7 | 42.4 | 2.45 | 8.6 | 24 | 59.7 | 72.9 | 21.7 | 46 | 2.69 | 8.6 | 26 | 19.7 | 21.6 | 33.9 | 2.5 | 1.08 | 2.7 | 1.08 | 217 | 193 | 2172 | 2172
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:25:00 | 1883.18 | 611.42 | 827220.68 | 801744.94 | 22.09 | 2549.514 | 1923.312 | -142.513 | 44 | 184 | 34.7 | 44.6 | 32.7 | 46.8 | 0 | 0 | - | - | 36.8 | 42.1 | 215 | 192 | 59 | 58.8 | 67.6 | 21.7 | 42.4 | 2.4 | 8.5 | 24.8 | 58.5 | 72.6 | 21.7 | 45.9 | 2.66 | 8.6 | 26.2 | 19.7 | 21.5 | 34.5 | 2.5 | 1.08 | 2.71 | 1.08 | 215 | 192 | 2128 | 2128
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:30:00 | 1885.7 | 612.98 | 827223.2 | 801746.16 | 22.73 | 2571.876 | 1900.95 | -27.14 | 44 | 184 | 34.6 | 44.7 | 32.6 | 46.9 | 0 | 0 | - | - | 36.7 | 42.1 | 215 | 190 | 59 | 58.9 | 67.5 | 21.6 | 42.1 | 2.41 | 8.6 | 24.4 | 58.5 | 72.4 | 21.6 | 45.9 | 2.67 | 8.5 | 25.8 | 19.6 | 21.3 | 35.5 | 2.5 | 1.08 | 2.71 | 1.08 | 215 | 190 | 2065 | 2065
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:35:00 | 1889.94 | 614.82 | 827227.44 | 801748.24 | 23.37 | 2571.876 | 1900.95 | -112.951 | 44 | 184 | 34.4 | 44.7 | 32.5 | 46.9 | 0 | 0 | - | - | 36.7 | 42.1 | 215 | 187 | 58.5 | 58.4 | 66.8 | 21.4 | 41.6 | 2.41 | 8.7 | 23.8 | 58.5 | 72.2 | 21.4 | 45.5 | 2.66 | 8.6 | 25.7 | 19.5 | 21.2 | 35.5 | 2.49 | 1.07 | 2.7 | 1.07 | 215 | 187 | 2070 | 2070
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:40:00 | 1889.94 | 640.38 | 827227.44 | 801774.88 | 24.02 | 2594.239 | 1878.587 | -657.82 | 44 | 184 | 34.3 | 44.8 | 32.3 | 47 | 0 | 0 | - | - | 36.6 | 42.1 | 213 | 187 | 58 | 58.4 | 66.9 | 21.3 | 42 | 2.42 | 8.5 | 23.6 | 58 | 72 | 21.3 | 45.4 | 2.65 | 8.5 | 25.6 | 19.4 | 21.2 | 35.9 | 2.48 | 1.07 | 2.69 | 1.07 | 213 | 187 | 2049 | 2050
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:45:00 | 1889.94 | 703.62 | 827227.44 | 801838.66 | 24.65 | 2683.698 | 1789.128 | -914.262 | 42 | 184 | 34.2 | 44.8 | 32.2 | 47.1 | 0 | 0 | - | - | 36.6 | 42.1 | 211 | 186 | 57.4 | 57.2 | 66.4 | 21.2 | 41.4 | 2.37 | 8.6 | 23.9 | 57.5 | 71.7 | 21.2 | 45.1 | 2.63 | 8.5 | 25.7 | 19.2 | 20.9 | 35.6 | 2.44 | 1.06 | 2.66 | 1.07 | 211 | 186 | 2074 | 2074
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:50:00 | 1889.94 | 773.98 | 827227.44 | 801907.7 | 25.14 | 2743.332 | 1729.494 | -511.734 | 40 | 184 | 34 | 44.9 | 31.9 | 47.3 | 0 | 0 | - | - | 36.5 | 42.2 | 0 | 0 | 53.2 | 53 | 65.8 | 20.9 | 41.2 | 2.27 | 33.6 | 25.3 | 52.6 | 69.6 | 20.9 | 41.2 | 2.12 | 12.1 | 32.9 | 21 | 21.1 | 34.9 | 1.95 | 0.92 | 1.91 | 1.4 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 13:55:00 | 1889.94 | 792.56 | 827227.44 | 801925.92 | 25.31 | 2765.697 | 1707.129 | -151.391 | 40 | 184 | 33.7 | 45.3 | 31.7 | 47.7 | 0 | 0 | - | - | 36.3 | 42.3 | 0 | 0 | 0 | 0 | 37.4 | 35.3 | 31.4 | 1.69 | 12.3 | 8.6 | 0 | 32.4 | 46.6 | 33.1 | 1.47 | 23.1 | 8.9 | 22.8 | 22.9 | 33.9 | 1.66 | 1.47 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:00:00 | 1889.94 | 823.58 | 827227.44 | 801957.98 | 25.48 | 2780.607 | 1692.219 | -447.469 | 39 | 184 | 33.4 | 45.7 | 31.5 | 48 | 0 | 0 | - | - | 36.1 | 42.5 | 0 | 0 | 0 | 0 | 30.9 | 42.4 | 31.7 | 1.52 | 18.5 | 5.8 | 0 | 32.6 | 45.6 | 32.4 | 1.47 | 21.4 | 9.1 | 23.4 | 23.5 | 33.1 | 1.53 | 1.5 | 1.48 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:05:00 | 1889.94 | 849.28 | 827227.44 | 801982.9 | 25.64 | 2825.337 | 1647.489 | -447.249 | 38 | 184 | 33.1 | 46.1 | 31.2 | 48.4 | 0 | 0 | - | - | 35.9 | 42.6 | 0 | 0 | 0 | 0 | 30.8 | 43.5 | 31.6 | 1.5 | 19.3 | 6.2 | 0 | 33.1 | 43.9 | 31.7 | 1.49 | 19.4 | 9.3 | 23.7 | 23.8 | 28.6 | 1.52 | 1.51 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:10:00 | 1889.94 | 879.94 | 827227.44 | 802013.48 | 25.79 | 2862.611 | 1610.215 | -365.561 | 38 | 184 | 32.8 | 46.5 | 31 | 48.7 | 0 | 0 | - | - | 35.5 | 43 | 0 | 0 | 0 | 0 | 30.7 | 42.9 | 31.1 | 1.49 | 18.5 | 6.3 | 0 | 32.4 | 42.6 | 30.9 | 1.49 | 18.1 | 8.5 | 23.7 | 23.9 | 28.1 | 1.52 | 1.51 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:15:00 | 1899.9 | 887.66 | 827237.8 | 802020.84 | 25.94 | 2862.611 | 1610.215 | 251.816 | 38 | 184 | 32.4 | 47 | 30.7 | 49.2 | 0 | 0 | - | - | 35 | 43.5 | 0 | 0 | 0 | 0 | 30.2 | 41.1 | 29.9 | 1.49 | 16.7 | 5.6 | 0 | 31.4 | 40.7 | 30.2 | 1.49 | 16.2 | 7.5 | 23.8 | 23.9 | 27.7 | 1.52 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:20:00 | 1919.54 | 887.66 | 827257.14 | 802020.84 | 26.09 | 2825.337 | 1647.489 | 81.176 | 38 | 184 | 31.9 | 47.6 | 30.3 | 49.9 | 0 | 0 | - | - | 34.4 | 44.1 | 0 | 0 | 0 | 0 | 29.2 | 39.4 | 28.8 | 1.49 | 14.8 | 4.7 | 0 | 30.3 | 39.1 | 29.2 | 1.5 | 14.4 | 6.3 | 23.9 | 24 | 27.3 | 1.52 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:25:00 | 1927.76 | 887.9 | 827265.6 | 802021.08 | 26.23 | 2825.337 | 1647.489 | 228.222 | 38 | 184 | 31.4 | 48.3 | 29.8 | 50.5 | 0 | 0 | - | - | 33.9 | 44.8 | 0 | 0 | 0 | 0 | 28.3 | 37.2 | 28.2 | 1.49 | 12.7 | 3.9 | 0 | 29.6 | 37.2 | 28.4 | 1.5 | 12.6 | 5.5 | 23.9 | 24.1 | 26.9 | 1.52 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:30:00 | 1975.44 | 887.9 | 827313.42 | 802021.08 | 26.38 | 2780.607 | 1692.219 | 967.192 | 40 | 184 | 31 | 48.9 | 29.3 | 51.5 | 0 | 0 | - | - | 33.3 | 45.3 | 0 | 0 | 0 | 0 | 27.8 | 35.4 | 27.7 | 1.49 | 10.8 | 3.3 | 0 | 28.8 | 35.7 | 27.9 | 1.5 | 11 | 4.7 | 24 | 24.1 | 26.7 | 1.52 | 1.52 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:35:00 | 2057.68 | 887.9 | 827395.18 | 802021.08 | 26.52 | 2691.152 | 1781.674 | 918.159 | 41 | 184 | 30.7 | 49.4 | 28.8 | 52.3 | 0 | 0 | - | - | 32.9 | 45.8 | 0 | 0 | 0 | 0 | 27.4 | 34.1 | 27.3 | 1.5 | 9.3 | 2.8 | 0 | 28.3 | 34.4 | 27.6 | 1.5 | 9.6 | 4.1 | 24.1 | 24.3 | 26.8 | 1.52 | 1.53 | 1.51 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:40:00 | 2128.94 | 887.9 | 827468.52 | 802021.08 | 26.66 | 2624.058 | 1848.768 | 837.307 | 43 | 184 | 30.3 | 49.9 | 28.6 | 52.6 | 0 | 0 | - | - | 32.5 | 46.3 | 0 | 0 | 0 | 0 | 27.2 | 32.9 | 27.2 | 1.51 | 7.9 | 2.4 | 0 | 27.9 | 33.4 | 27.3 | 1.51 | 8.3 | 3.5 | 24.3 | 24.5 | 26.8 | 1.53 | 1.54 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:45:00 | 2184 | 887.9 | 827521.72 | 802021.08 | 26.79 | 2549.514 | 1923.312 | 256.611 | 45 | 185 | 30 | 50.5 | 28.6 | 52.6 | 0 | 0 | - | - | 32.2 | 46.7 | 0 | 0 | 0 | 0 | 27.1 | 31.8 | 27.1 | 1.51 | 6.7 | 2.1 | 0 | 27.7 | 32.6 | 27.2 | 1.52 | 7.2 | 3.1 | 24.6 | 24.7 | 26.8 | 1.54 | 1.55 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:50:00 | 2208.08 | 887.9 | 827546.1 | 802021.08 | 26.92 | 2527.149 | 1945.677 | 402.296 | 45 | 185 | 29.6 | 51.1 | 28.6 | 52.7 | 0 | 0 | - | - | 31.9 | 47 | 0 | 0 | 0 | 0 | 27 | 31.2 | 27.1 | 1.52 | 5.8 | 1.8 | 0 | 27.6 | 31.7 | 27.2 | 1.53 | 6.2 | 2.8 | 24.7 | 24.9 | 26.7 | 1.55 | 1.55 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 14:55:00 | 2246.34 | 887.9 | 827584.18 | 802021.08 | 27.04 | 2497.329 | 1975.497 | 297.265 | 46 | 185 | 29.4 | 51.6 | 28.5 | 52.9 | 0 | 0 | - | - | 31.7 | 47.3 | 0 | 0 | 0 | 0 | 26.9 | 30.6 | 27 | 1.53 | 5.2 | 1.7 | 0 | 27.4 | 30.9 | 27.2 | 1.53 | 5.3 | 2.5 | 24.9 | 25 | 26.8 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:00:00 | 2252.48 | 897.78 | 827589.98 | 802031.74 | 27.15 | 2489.874 | 1982.952 | -216.518 | 46 | 185 | 29.1 | 52.1 | 28.4 | 53 | 0 | 0 | - | - | 31.6 | 47.5 | 0 | 0 | 0 | 0 | 26.9 | 30.2 | 27 | 1.53 | 4.7 | 1.5 | 0 | 27.3 | 30.6 | 27.1 | 1.54 | 4.8 | 2.3 | 25 | 25.1 | 26.8 | 1.56 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:05:00 | 2260 | 903.28 | 827597.82 | 802036.46 | 27.25 | 2497.329 | 1975.497 | 348.428 | 46 | 185 | 28.8 | 52.5 | 28.3 | 53.2 | 0 | 0 | - | - | 31.4 | 47.7 | 0 | 0 | 0 | 0 | 26.8 | 29.8 | 26.9 | 1.53 | 4.3 | 1.4 | 0 | 27.2 | 30.1 | 27.1 | 1.54 | 4.3 | 2.2 | 25 | 25.2 | 27 | 1.56 | 1.57 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:10:00 | 2268.12 | 907.62 | 827605.82 | 802040.8 | 27.35 | 2482.419 | 1990.407 | 88.189 | 46 | 185 | 28.6 | 52.9 | 28.2 | 53.3 | 0 | 0 | - | - | 31.2 | 47.8 | 0 | 0 | 0 | 0 | 26.8 | 29.6 | 26.9 | 1.53 | 4 | 1.4 | 0 | 27.2 | 29.8 | 27.1 | 1.54 | 4 | 2.1 | 25.1 | 25.2 | 26.8 | 1.56 | 1.57 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:15:00 | 2287.14 | 907.62 | 827625.24 | 802040.8 | 27.45 | 2460.054 | 2012.772 | 391.176 | 47 | 185 | 28.4 | 53.1 | 28.1 | 53.5 | 0 | 0 | - | - | 31.1 | 48 | 0 | 0 | 0 | 0 | 26.7 | 29.3 | 26.8 | 1.53 | 3.7 | 1.3 | 0 | 27.2 | 29.4 | 27 | 1.54 | 3.7 | 2 | 25.1 | 25.3 | 26.7 | 1.56 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:20:00 | 2302.06 | 907.62 | 827640.04 | 802040.8 | 27.54 | 2452.599 | 2020.227 | 190.947 | 47 | 185 | 28.3 | 53.5 | 28 | 53.7 | 0 | 0 | - | - | 31 | 48.1 | 0 | 0 | 0 | 0 | 26.7 | 29.1 | 26.7 | 1.53 | 3.5 | 1.3 | 0 | 27.1 | 29.2 | 26.9 | 1.54 | 3.4 | 2 | 25.1 | 25.3 | 26.6 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:25:00 | 2316.5 | 907.62 | 827654.08 | 802040.8 | 27.63 | 2437.689 | 2035.137 | 129.771 | 47 | 185 | 28.1 | 53.8 | 27.9 | 53.8 | 0 | 0 | - | - | 30.8 | 48.2 | 0 | 0 | 0 | 0 | 26.6 | 28.7 | 26.6 | 1.53 | 3.3 | 1.3 | 0 | 26.9 | 28.8 | 26.8 | 1.54 | 3.1 | 1.9 | 25.2 | 25.3 | 26.4 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:30:00 | 2333.62 | 907.62 | 827671.48 | 802040.8 | 27.72 | 2415.324 | 2057.502 | 191.377 | 48 | 185 | 27.9 | 54 | 27.8 | 54 | 0 | 0 | - | - | 30.7 | 48.3 | 0 | 0 | 0 | 0 | 26.4 | 28.4 | 26.4 | 1.52 | 3 | 1.2 | 0 | 26.7 | 28.6 | 26.7 | 1.54 | 2.9 | 1.8 | 25.2 | 25.4 | 26.4 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:35:00 | 2337.84 | 910.04 | 827675.34 | 802043.28 | 27.81 | 2415.324 | 2057.502 | -120.433 | 48 | 185 | 27.8 | 54.3 | 27.7 | 54.2 | 0 | 0 | - | - | 30.6 | 48.5 | 0 | 0 | 0 | 0 | 26.3 | 28.2 | 26.4 | 1.52 | 2.8 | 1.2 | 0 | 26.7 | 28.3 | 26.6 | 1.53 | 2.7 | 1.7 | 25.3 | 25.4 | 26.5 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:40:00 | 2337.84 | 917.4 | 827675.34 | 802050.72 | 27.89 | 2422.779 | 2050.047 | -66.294 | 47 | 185 | 27.7 | 54.5 | 27.7 | 54.3 | 0 | 0 | - | - | 30.5 | 48.6 | 0 | 0 | 0 | 0 | 26.3 | 28.1 | 26.4 | 1.52 | 2.7 | 1.2 | 0 | 26.7 | 28.2 | 26.6 | 1.53 | 2.4 | 1.7 | 25.3 | 25.5 | 26.3 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:45:00 | 2338.02 | 921 | 827675.52 | 802054.18 | 27.98 | 2422.779 | 2050.047 | 4.844 | 47 | 185 | 27.6 | 54.7 | 27.6 | 54.4 | 0 | 0 | - | - | 30.4 | 48.7 | 0 | 0 | 0 | 0 | 26.3 | 27.9 | 26.4 | 1.52 | 2.5 | 1.1 | 0 | 26.6 | 27.9 | 26.6 | 1.54 | 2.2 | 1.6 | 25.3 | 25.4 | 26.4 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:50:00 | 2338.62 | 922.28 | 827676.12 | 802055.56 | 28.06 | 2430.234 | 2042.592 | 38.522 | 47 | 185 | 27.5 | 54.9 | 27.5 | 54.6 | 0 | 0 | - | - | 30.3 | 48.8 | 0 | 0 | 0 | 0 | 26.4 | 28 | 26.6 | 1.52 | 2.6 | 1.2 | 0 | 26.7 | 27.9 | 26.6 | 1.54 | 2.1 | 1.6 | 25.3 | 25.5 | 26.1 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 15:55:00 | 2339.72 | 924.5 | 827677.22 | 802057.82 | 28.14 | 2430.234 | 2042.592 | -133.74 | 47 | 185 | 27.4 | 55 | 27.5 | 54.7 | 0 | 0 | - | - | 30.3 | 48.9 | 0 | 0 | 0 | 0 | 26.5 | 28.1 | 26.7 | 1.52 | 2.6 | 1.4 | 0 | 26.7 | 27.8 | 26.6 | 1.54 | 2.1 | 1.6 | 25.3 | 25.5 | 26.1 | 1.54 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:00:00 | 2339.88 | 929.3 | 827677.48 | 802062.48 | 28.22 | 2430.234 | 2042.592 | 63.077 | 47 | 185 | 27.3 | 55.2 | 27.4 | 54.7 | 0 | 0 | - | - | 30.2 | 53.2 | 0 | 0 | 0 | 0 | 26.6 | 28.1 | 26.7 | 1.52 | 2.7 | 1.5 | 0 | 26.7 | 27.8 | 26.7 | 1.54 | 2 | 1.5 | 25.4 | 25.5 | 26.1 | 1.54 | 1.56 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:05:00 | 2347 | 930.7 | 827685.26 | 802063.88 | 28.3 | 2430.234 | 2042.592 | 423.356 | 47 | 185 | 27.3 | 55.3 | 27.4 | 54.8 | 0 | 0 | - | - | 30.2 | 52.7 | 0 | 0 | 0 | 0 | 26.7 | 28.1 | 26.8 | 1.52 | 2.7 | 1.6 | 0 | 26.7 | 27.7 | 26.7 | 1.54 | 1.9 | 1.6 | 25.3 | 25.5 | 25.9 | 1.55 | 1.56 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:10:00 | 2385.14 | 930.7 | 827723.04 | 802063.88 | 28.4 | 2385.508 | 2087.318 | 393.719 | 48 | 185 | 27.2 | 55.5 | 27.3 | 54.9 | 0 | 0 | - | - | 30 | 52.4 | 0 | 0 | 0 | 0 | 26.7 | 28.1 | 26.8 | 1.53 | 2.6 | 1.5 | 0 | 26.7 | 27.7 | 26.7 | 1.55 | 1.9 | 1.5 | 25.4 | 25.6 | 25.8 | 1.55 | 1.56 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:15:00 | 2416.1 | 930.7 | 827754.3 | 802063.88 | 28.49 | 2363.145 | 2109.681 | 341.819 | 49 | 185 | 27.2 | 55.6 | 27.4 | 55 | 0 | 0 | - | - | 29.9 | 52.2 | 0 | 0 | 0 | 0 | 26.7 | 28.1 | 26.7 | 1.53 | 2.5 | 1.4 | 0 | 26.7 | 27.7 | 26.7 | 1.55 | 1.7 | 1.4 | 25.5 | 25.6 | 26.1 | 1.55 | 1.56 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:20:00 | 2441.96 | 930.7 | 827779.74 | 802063.88 | 28.58 | 2333.325 | 2139.501 | 284.098 | 50 | 185 | 27.2 | 55.7 | 27.4 | 55 | 0 | 0 | - | - | 29.8 | 52 | 0 | 0 | 0 | 0 | 26.8 | 28.1 | 26.9 | 1.53 | 2.6 | 1.5 | 0 | 26.7 | 27.6 | 26.7 | 1.55 | 1.7 | 1.5 | 25.5 | 25.7 | 26.1 | 1.55 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:25:00 | 2466.76 | 930.7 | 827804.64 | 802063.88 | 28.67 | 2310.96 | 2161.866 | 136.93 | 50 | 185 | 27.2 | 55.7 | 27.4 | 55 | 0 | 0 | - | - | 29.7 | 51.9 | 0 | 0 | 0 | 0 | 26.8 | 28.1 | 26.8 | 1.53 | 2.5 | 1.5 | 0 | 26.7 | 27.6 | 26.8 | 1.55 | 1.7 | 1.5 | 25.6 | 25.7 | 25.8 | 1.55 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:30:00 | 2480.84 | 930.7 | 827818.58 | 802063.88 | 28.75 | 2288.595 | 2184.231 | 224.128 | 51 | 185 | 27.2 | 55.7 | 27.4 | 54.9 | 0 | 0 | - | - | 29.6 | 51.8 | 0 | 0 | 0 | 0 | 26.7 | 28.1 | 26.8 | 1.52 | 2.4 | 1.6 | 0 | 26.7 | 27.6 | 26.7 | 1.54 | 1.5 | 1.5 | 25.7 | 25.8 | 25.4 | 1.54 | 1.57 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:35:00 | 2499.24 | 930.7 | 827837.12 | 802063.88 | 28.82 | 2281.14 | 2191.686 | 259.535 | 51 | 185 | 27.1 | 55.8 | 27.4 | 55 | 0 | 0 | - | - | 29.5 | 51.8 | 0 | 0 | 0 | 0 | 26.6 | 27.9 | 26.7 | 1.51 | 2.4 | 1.6 | 0 | 26.6 | 27.3 | 26.7 | 1.54 | 1.4 | 1.5 | 25.7 | 25.8 | 25.2 | 1.54 | 1.57 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:40:00 | 2519.58 | 930.7 | 827857.46 | 802063.88 | 28.91 | 2243.87 | 2228.961 | 252.62 | 51 | 185 | 27.1 | 55.9 | 27.4 | 55 | 0 | 0 | - | - | 29.3 | 51.8 | 0 | 0 | 0 | 0 | 26.4 | 27.7 | 26.4 | 1.51 | 2.2 | 1.5 | 0 | 26.4 | 27.2 | 26.6 | 1.53 | 1.2 | 1.5 | 25.7 | 25.9 | 25.4 | 1.54 | 1.57 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:45:00 | 2540.72 | 930.7 | 827878.78 | 802063.88 | 28.99 | 2214.051 | 2258.778 | 268.429 | 52 | 185 | 27.1 | 56 | 27.4 | 55 | 0 | 0 | - | - | 29.2 | 51.9 | 0 | 0 | 0 | 0 | 26.3 | 27.7 | 26.4 | 1.51 | 2.1 | 1.4 | 0 | 26.3 | 27.1 | 26.4 | 1.53 | 1.1 | 1.4 | 25.8 | 26 | 25.7 | 1.54 | 1.57 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:50:00 | 2555.76 | 930.72 | 827893.4 | 802063.9 | 29.07 | 2191.686 | 2281.14 | 90.653 | 52 | 185 | 27.1 | 56 | 27.4 | 55.1 | 0 | 0 | - | - | 29.1 | 51.8 | 0 | 0 | 0 | 0 | 26.4 | 27.7 | 26.5 | 1.52 | 2.1 | 1.3 | 0 | 26.3 | 27.1 | 26.5 | 1.53 | 1.1 | 1.3 | 25.9 | 26.1 | 25.2 | 1.54 | 1.57 | 1.54 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 16:55:00 | 2557.9 | 936.28 | 827895.4 | 802069.72 | 29.14 | 2191.686 | 2281.14 | -191.25 | 52 | 185 | 27 | 56.1 | 27.4 | 55.1 | 0 | 0 | - | - | 29 | 51.8 | 0 | 0 | 0 | 0 | 26.3 | 27.7 | 26.4 | 1.51 | 2 | 1.3 | 0 | 26.2 | 27 | 26.3 | 1.54 | 1 | 1.3 | 25.9 | 26.1 | 25.1 | 1.54 | 1.57 | 1.54 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:00:00 | 2557.9 | 967.34 | 827895.4 | 802101.6 | 29.23 | 2214.051 | 2258.778 | -447.928 | 51 | 185 | 27 | 56.2 | 27.3 | 55.2 | 0 | 0 | - | - | 28.9 | 51.8 | 0 | 0 | 0 | 0 | 26.2 | 27.4 | 26.2 | 1.51 | 1.8 | 1.3 | 0 | 26.2 | 26.8 | 26.2 | 1.53 | 0.8 | 1.2 | 26 | 26.1 | 25 | 1.54 | 1.57 | 1.54 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:05:00 | 2557.9 | 985.98 | 827895.4 | 802119.22 | 29.31 | 2281.14 | 2191.686 | -0.524 | 51 | 185 | 27 | 56.2 | 27.3 | 55.3 | 0 | 0 | - | - | 28.8 | 51.9 | 0 | 0 | 0 | 0 | 26.1 | 27.3 | 26.2 | 1.51 | 1.7 | 1.1 | 0 | 25.9 | 26.7 | 26.1 | 1.53 | 0.7 | 1 | 25.9 | 26.1 | 25.1 | 1.54 | 1.57 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:10:00 | 2558.62 | 987.46 | 827896.12 | 802120.8 | 29.39 | 2281.14 | 2191.686 | -48.918 | 51 | 185 | 27 | 56.3 | 27.4 | 55.3 | 0 | 0 | - | - | 28.7 | 52 | 0 | 0 | 0 | 0 | 25.9 | 27.2 | 26.1 | 1.51 | 1.5 | 0.9 | 0 | 25.9 | 26.7 | 26 | 1.53 | 0.6 | 1 | 26 | 26.1 | 25.3 | 1.54 | 1.57 | 1.54 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:15:00 | 2558.64 | 992.42 | 827896.14 | 802125.7 | 29.46 | 2281.14 | 2191.686 | -110.738 | 51 | 185 | 27 | 56.4 | 27.4 | 55.3 | 0 | 0 | - | - | 28.7 | 52.1 | 0 | 0 | 0 | 0 | 25.8 | 27.2 | 25.9 | 1.51 | 1.5 | 0.9 | 0 | 25.8 | 26.6 | 25.9 | 1.53 | 0.6 | 0.9 | 26 | 26.2 | 24.9 | 1.54 | 1.57 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:20:00 | 2558.64 | 1005.26 | 827896.14 | 802138.66 | 29.54 | 2281.14 | 2191.686 | -194.298 | 51 | 185 | 26.9 | 56.4 | 27.4 | 55.3 | 0 | 0 | - | - | 28.6 | 52.1 | 0 | 0 | 0 | 0 | 25.8 | 27.2 | 25.9 | 1.51 | 1.5 | 0.9 | 0 | 25.7 | 26.6 | 25.9 | 1.53 | 0.5 | 0.9 | 26 | 26.2 | 25 | 1.54 | 1.57 | 1.53 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:25:00 | 2558.64 | 1025.74 | 827896.14 | 802159.52 | 29.63 | 2288.595 | 2184.231 | -233.115 | 50 | 185 | 26.9 | 56.5 | 27.3 | 55.4 | 0 | 0 | - | - | 28.5 | 52.2 | 0 | 0 | 0 | 0 | 25.9 | 27.1 | 26 | 1.51 | 1.8 | 1 | 0 | 25.7 | 26.5 | 25.8 | 1.53 | 0.5 | 0.8 | 26 | 26.2 | 24.9 | 1.54 | 1.55 | 1.53 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:30:00 | 2558.64 | 1047.68 | 827896.14 | 802181.6 | 29.71 | 2325.87 | 2146.956 | -287.631 | 50 | 185 | 26.9 | 56.5 | 27.3 | 55.5 | 0 | 0 | - | - | 28.4 | 52.2 | 0 | 0 | 0 | 0 | 26 | 27 | 25.9 | 1.52 | 1.6 | 1 | 0 | 25.7 | 26.4 | 25.8 | 1.53 | 0.4 | 0.8 | 26 | 26.2 | 25.1 | 1.54 | 1.56 | 1.53 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:35:00 | 2558.64 | 1074.38 | 827896.14 | 802208.14 | 29.79 | 2340.78 | 2132.046 | -342.114 | 49 | 185 | 26.9 | 56.5 | 27.2 | 55.5 | 0 | 0 | - | - | 28.4 | 52.2 | 0 | 0 | 0 | 0 | 26.1 | 27 | 26 | 1.52 | 1.7 | 1 | 0 | 25.6 | 26.5 | 25.8 | 1.53 | 0.6 | 0.7 | 26 | 26.2 | 25.1 | 1.54 | 1.56 | 1.53 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:40:00 | 2558.64 | 1103.86 | 827896.14 | 802237.96 | 29.88 | 2378.054 | 2094.772 | -377.796 | 48 | 185 | 26.9 | 56.6 | 27.2 | 55.6 | 0 | 0 | - | - | 28.3 | 52.3 | 0 | 0 | 0 | 0 | 26.1 | 27.1 | 26.1 | 1.52 | 1.7 | 1 | 0 | 25.7 | 26.5 | 25.8 | 1.53 | 0.6 | 0.8 | 26 | 26.1 | 25.2 | 1.54 | 1.56 | 1.53 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:45:00 | 2558.64 | 1132.68 | 827896.14 | 802266.34 | 29.97 | 2415.324 | 2057.502 | -331.734 | 47 | 185 | 26.9 | 56.6 | 27.2 | 55.6 | 0 | 0 | - | - | 28.3 | 52.3 | 0 | 0 | 0 | 0 | 26.1 | 27.2 | 26.1 | 1.52 | 1.8 | 1 | 0 | 25.8 | 26.6 | 25.9 | 1.53 | 0.7 | 0.9 | 25.9 | 26.1 | 25.2 | 1.55 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:50:00 | 2558.64 | 1156.86 | 827896.14 | 802290.36 | 30.06 | 2430.234 | 2042.592 | -227.832 | 47 | 185 | 26.9 | 56.6 | 27.2 | 55.6 | 0 | 0 | - | - | 28.3 | 52.3 | 0 | 0 | 0 | 0 | 26.1 | 27.2 | 26.2 | 1.52 | 1.8 | 1 | 0 | 25.8 | 26.6 | 25.9 | 1.53 | 0.7 | 0.9 | 25.9 | 26.1 | 25.1 | 1.54 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 17:55:00 | 2558.64 | 1173.56 | 827896.14 | 802307.22 | 30.14 | 2460.054 | 2012.772 | -300.796 | 46 | 185 | 26.9 | 56.6 | 27.2 | 55.6 | 0 | 0 | - | - | 28.3 | 52.3 | 0 | 0 | 0 | 0 | 26.2 | 27.4 | 26.3 | 1.52 | 2.1 | 1.1 | 0 | 25.9 | 26.7 | 25.9 | 1.54 | 0.9 | 0.9 | 25.9 | 26.1 | 25.1 | 1.54 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:00:00 | 2558.64 | 1209.92 | 827896.14 | 802344.1 | 30.23 | 2482.419 | 1990.407 | -291.569 | 46 | 185 | 26.9 | 56.6 | 27.2 | 55.6 | 0 | 0 | - | - | 28.3 | 52.2 | 0 | 0 | 0 | 0 | 26.2 | 27.3 | 26.2 | 1.51 | 2.1 | 1.1 | 0 | 25.9 | 26.7 | 25.9 | 1.54 | 0.9 | 0.9 | 25.8 | 26.1 | 24.9 | 1.54 | 1.55 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:05:00 | 2558.64 | 1235.8 | 827896.14 | 802369.3 | 30.31 | 2512.239 | 1960.587 | -301.528 | 45 | 185 | 26.9 | 56.7 | 27.2 | 55.6 | 0 | 0 | - | - | 28.3 | 52.2 | 0 | 0 | 0 | 0 | 26.1 | 27.3 | 26.2 | 1.52 | 2 | 1 | 0 | 25.9 | 26.7 | 25.9 | 1.54 | 0.9 | 1 | 25.8 | 26.1 | 25.1 | 1.54 | 1.55 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:10:00 | 2558.64 | 1261.72 | 827896.14 | 802395.4 | 30.4 | 2549.514 | 1923.312 | -322.793 | 44 | 185 | 26.9 | 56.6 | 27.2 | 55.7 | 0 | 0 | - | - | 28.2 | 52.2 | 0 | 0 | 0 | 0 | 26.1 | 27.4 | 26.2 | 1.52 | 2 | 1 | 0 | 25.9 | 26.7 | 25.9 | 1.54 | 1 | 1 | 25.8 | 26 | 25.2 | 1.54 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:15:00 | 2558.64 | 1300.92 | 827896.14 | 802434.82 | 30.49 | 2601.693 | 1871.133 | -788.411 | 43 | 185 | 26.9 | 56.6 | 27.2 | 55.7 | 0 | 0 | - | - | 28.2 | 52.2 | 0 | 0 | 0 | 0 | 26.2 | 27.4 | 26.3 | 1.52 | 2.1 | 1.1 | 0 | 25.9 | 26.8 | 26 | 1.54 | 1.1 | 1 | 25.8 | 25.9 | 25.3 | 1.54 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:20:00 | 2558.64 | 1359.14 | 827896.14 | 802492.84 | 30.59 | 2668.788 | 1804.038 | -476.384 | 42 | 185 | 26.8 | 56.7 | 27.1 | 55.7 | 0 | 0 | - | - | 28.2 | 52.2 | 0 | 0 | 0 | 0 | 26.2 | 27.5 | 26.4 | 1.52 | 2.2 | 1.1 | 0 | 26 | 26.8 | 26 | 1.54 | 1.1 | 1.1 | 25.8 | 25.8 | 25.3 | 1.54 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:25:00 | 2558.64 | 1406.4 | 827896.14 | 802540.2 | 30.69 | 2713.514 | 1759.312 | -611.833 | 41 | 185 | 26.8 | 56.7 | 27.2 | 55.7 | 0 | 0 | - | - | 28.2 | 52.3 | 0 | 0 | 0 | 0 | 26.2 | 27.5 | 26.4 | 1.52 | 2.2 | 1.1 | 0 | 26.1 | 26.9 | 26.1 | 1.54 | 1.2 | 1.1 | 25.7 | 25.8 | 25.4 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:30:00 | 2558.64 | 1466.7 | 827896.14 | 802601.1 | 30.79 | 2780.607 | 1692.219 | -794.695 | 39 | 185 | 26.9 | 56.7 | 27.2 | 55.7 | 0 | 0 | - | - | 28.2 | 52.2 | 0 | 0 | 0 | 0 | 26.2 | 27.6 | 26.4 | 1.52 | 2.2 | 1.2 | 0 | 26.1 | 26.9 | 26.2 | 1.54 | 1.2 | 1.1 | 25.7 | 25.8 | 25.5 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:35:00 | 2558.64 | 1543.28 | 827896.14 | 802677.72 | 30.9 | 2870.066 | 1602.76 | -759.32 | 37 | 185 | 26.9 | 56.7 | 27.2 | 55.6 | 0 | 0 | - | - | 28.3 | 52.2 | 0 | 0 | 0 | 0 | 26.2 | 27.6 | 26.4 | 1.52 | 2.2 | 1.1 | 0 | 26.1 | 27 | 26.2 | 1.54 | 1.3 | 1.1 | 25.7 | 25.8 | 25.6 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:40:00 | 2558.64 | 1602.4 | 827896.14 | 802735.94 | 31 | 2929.701 | 1543.125 | -715.936 | 36 | 185 | 26.9 | 56.6 | 27.2 | 55.6 | 0 | 0 | - | - | 28.3 | 52.2 | 0 | 0 | 0 | 0 | 26.2 | 27.6 | 26.4 | 1.52 | 2.2 | 1.1 | 0 | 26.1 | 27 | 26.2 | 1.54 | 1.3 | 1.1 | 25.7 | 25.8 | 25.6 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:45:00 | 2558.64 | 1670.56 | 827896.14 | 802804.22 | 31.12 | 3004.25 | 1468.576 | -874.411 | 34 | 185 | 26.7 | 56.9 | 27.1 | 55.8 | 0 | 0 | - | - | 28.3 | 52.1 | 0 | 0 | 0 | 0 | 26.2 | 27.6 | 26.5 | 1.52 | 2.2 | 1.1 | 0 | 26.1 | 27 | 26.3 | 1.54 | 1.3 | 1.1 | 25.7 | 25.8 | 25.7 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:50:00 | 2558.64 | 1752.06 | 827896.14 | 802885.24 | 31.24 | 3086.25 | 1386.576 | -900.776 | 32 | 185 | 26.6 | 57.1 | 27.1 | 55.9 | 0 | 0 | - | - | 28.3 | 52.1 | 0 | 0 | 0 | 0 | 26.3 | 27.7 | 26.6 | 1.51 | 2.4 | 1.4 | 0 | 26.1 | 27.1 | 26.3 | 1.54 | 1.4 | 1.2 | 25.7 | 25.8 | 25.5 | 1.54 | 1.55 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 18:55:00 | 2558.64 | 1826.9 | 827896.14 | 802961.1 | 31.36 | 3160.8 | 1312.026 | -982.109 | 31 | 185 | 26.8 | 56.9 | 27.3 | 55.5 | 0 | 0 | - | - | 28.4 | 52 | 0 | 0 | 0 | 0 | 26.3 | 27.7 | 26.6 | 1.51 | 2.4 | 1.4 | 0 | 26.1 | 27.1 | 26.3 | 1.53 | 1.4 | 1.2 | 25.7 | 25.8 | 25.4 | 1.54 | 1.55 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:00:00 | 2558.64 | 1886.48 | 827896.14 | 803022.26 | 31.48 | 3205.526 | 1267.3 | -640.347 | 30 | 185 | 26.9 | 56.8 | 27.5 | 55.3 | 0 | 0 | - | - | 28.4 | 51.9 | 0 | 0 | 0 | 0 | 26.4 | 27.7 | 26.7 | 1.51 | 2.4 | 1.5 | 0 | 26.2 | 27.1 | 26.3 | 1.53 | 1.5 | 1.2 | 25.8 | 25.9 | 25.6 | 1.54 | 1.55 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:05:00 | 2558.64 | 1938.76 | 827896.14 | 803073.12 | 31.61 | 3250.254 | 1222.572 | -593.371 | 29 | 185 | 26.9 | 56.7 | 27.5 | 55.2 | 0 | 0 | - | - | 28.4 | 51.9 | 0 | 0 | 0 | 0 | 26.5 | 27.7 | 26.7 | 1.52 | 2.4 | 1.5 | 0 | 26.2 | 27.2 | 26.3 | 1.53 | 1.4 | 1.2 | 25.9 | 26 | 25.6 | 1.54 | 1.55 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:10:00 | 2558.64 | 1985.56 | 827896.14 | 803119.52 | 31.73 | 3287.529 | 1185.297 | -567.301 | 28 | 185 | 27 | 56.7 | 27.5 | 55.2 | 0 | 0 | - | - | 28.5 | 51.9 | 0 | 0 | 0 | 0 | 26.7 | 27.7 | 26.8 | 1.52 | 2.3 | 1.6 | 0 | 26.2 | 27.2 | 26.3 | 1.54 | 1.5 | 1.3 | 25.9 | 26.1 | 25.7 | 1.55 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:15:00 | 2558.64 | 2033.64 | 827896.14 | 803168.18 | 31.85 | 3339.712 | 1133.115 | -653.984 | 27 | 185 | 27 | 56.6 | 27.5 | 55.2 | 0 | 0 | - | - | 28.5 | 51.9 | 0 | 0 | 0 | 0 | 26.8 | 27.7 | 26.9 | 1.52 | 2.3 | 1.7 | 0 | 26.3 | 27.2 | 26.3 | 1.54 | 1.4 | 1.2 | 26.1 | 26.2 | 25.7 | 1.55 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:20:00 | 2558.64 | 2086.34 | 827896.14 | 803220.4 | 31.97 | 3384.441 | 1088.387 | -556.12 | 26 | 185 | 27 | 56.6 | 27.6 | 55.2 | 0 | 0 | - | - | 28.5 | 51.8 | 0 | 0 | 0 | 0 | 27 | 27.7 | 26.9 | 1.52 | 2.2 | 1.8 | 0 | 26.2 | 27.2 | 26.4 | 1.54 | 1.4 | 1.2 | 26.2 | 26.4 | 25.6 | 1.55 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:25:00 | 2558.64 | 2135.22 | 827896.14 | 803269.42 | 32.08 | 3421.715 | 1051.113 | -619.295 | 25 | 185 | 27 | 56.6 | 27.6 | 55.2 | 0 | 0 | - | - | 28.5 | 51.8 | 0 | 0 | 0 | 0 | 27.4 | 27.7 | 27 | 1.52 | 2.2 | 2.3 | 0 | 25.9 | 27.2 | 26.4 | 1.54 | 1.3 | 0.8 | 26.4 | 26.5 | 25.7 | 1.55 | 1.56 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:30:00 | 2558.64 | 2186.94 | 827896.14 | 803321.36 | 32.2 | 3466.441 | 1006.385 | -596.514 | 24 | 185 | 27 | 56.6 | 27.6 | 55.2 | 0 | 0 | - | - | 28.5 | 51.7 | 0 | 0 | 0 | 0 | 27.8 | 27.6 | 26.9 | 1.53 | 2 | 2.6 | 0 | 25.9 | 27.2 | 26.4 | 1.55 | 1.2 | 0.8 | 26.5 | 26.6 | 25.7 | 1.55 | 1.57 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:35:00 | 2558.64 | 2220.46 | 827896.14 | 803354.06 | 32.32 | 3496.26 | 976.566 | -212.796 | 23 | 185 | 27 | 56.7 | 27.7 | 55.2 | 0 | 0 | - | - | 28.5 | 51.7 | 0 | 0 | 0 | 0 | 28.2 | 27.6 | 26.9 | 1.53 | 1.9 | 2.9 | 0 | 26 | 27.2 | 26.5 | 1.55 | 1.1 | 0.7 | 26.7 | 26.8 | 25.9 | 1.56 | 1.57 | 1.55 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:40:00 | 2558.64 | 2239.54 | 827896.14 | 803372.82 | 32.42 | 3518.625 | 954.201 | -204.648 | 23 | 185 | 27 | 56.8 | 27.8 | 55 | 0 | 0 | - | - | 28.6 | 51.7 | 0 | 0 | 0 | 0 | 28.7 | 27.6 | 26.9 | 1.53 | 1.9 | 3.2 | 0 | 26.1 | 27.2 | 26.5 | 1.55 | 1.1 | 0.7 | 26.8 | 26.9 | 25.9 | 1.56 | 1.57 | 1.55 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:45:00 | 2558.64 | 2254.96 | 827896.14 | 803388.68 | 32.52 | 3533.535 | 939.291 | -250.61 | 22 | 185 | 27 | 56.9 | 27.8 | 55 | 0 | 0 | - | - | 28.6 | 51.7 | 0 | 0 | 0 | 0 | 29 | 27.6 | 26.9 | 1.53 | 1.9 | 3.6 | 0 | 26.1 | 27.2 | 26.5 | 1.55 | 1 | 0.7 | 26.9 | 27 | 25.7 | 1.56 | 1.57 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:50:00 | 2558.64 | 2275.8 | 827896.14 | 803409.28 | 32.62 | 3548.445 | 924.381 | -162.439 | 22 | 185 | 27 | 56.9 | 27.8 | 55.1 | 0 | 0 | - | - | 28.6 | 51.7 | 0 | 0 | 0 | 0 | 29.6 | 27.7 | 27 | 1.53 | 1.8 | 4.1 | 0 | 26.1 | 27.2 | 26.5 | 1.55 | 1.1 | 0.8 | 26.9 | 27.1 | 25.7 | 1.56 | 1.58 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 19:55:00 | 2558.64 | 2300.46 | 827896.14 | 803434.02 | 32.72 | 3578.264 | 894.562 | -247.261 | 21 | 185 | 27 | 57 | 27.8 | 55.2 | 0 | 0 | - | - | 28.6 | 51.7 | 0 | 0 | 0 | 0 | 29.8 | 27.7 | 27 | 1.54 | 1.8 | 4.3 | 0 | 26.1 | 27.2 | 26.5 | 1.56 | 1 | 0.7 | 27 | 27.2 | 25.9 | 1.57 | 1.58 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:00:00 | 2558.64 | 2335.4 | 827896.14 | 803469.76 | 32.9 | 3600.627 | 872.199 | -364.829 | 21 | 185 | 27.1 | 57 | 27.7 | 55.5 | 0 | 0 | - | - | 28.6 | 51.7 | 120 | 120 | 0 | 0 | 29.9 | 27.7 | 26.9 | 1.57 | 2.5 | 3.9 | 0 | 26.3 | 27.2 | 26.5 | 1.58 | 1.4 | 0.5 | 25.2 | 27.2 | 26 | 2.21 | 0.93 | 2.11 | 0.85 | 232 | 211 | 2400 | 2400
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:05:00 | 2558.64 | 2355.18 | 827896.14 | 803488.4 | 33.51 | 3622.99 | 849.836 | 0.86 | 20 | 185 | 27 | 56.9 | 27.6 | 55.5 | 0 | 0 | - | - | 28.6 | 51.8 | 261 | 240 | 0 | 54.4 | 64.5 | 25.2 | 41.6 | 2.42 | 10.1 | 21.3 | 54.2 | 66 | 25.2 | 44.1 | 2.62 | 9.6 | 20.1 | 22.7 | 24.7 | 26.7 | 2.48 | 1.16 | 2.69 | 1.17 | 261 | 240 | 2400 | 2400
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:10:00 | 2559.22 | 2358.62 | 827896.72 | 803491.88 | 34.17 | 3622.99 | 849.836 | -50.668 | 20 | 185 | 26.9 | 56.9 | 27.5 | 55.5 | 0 | 0 | - | - | 28.6 | 51.9 | 261 | 230 | 49.6 | 49.4 | 62.7 | 23.7 | 39.2 | 2.26 | 8.5 | 22.1 | 49.4 | 67.1 | 23.7 | 42.9 | 2.5 | 8.4 | 23.1 | 21.3 | 23.5 | 26.7 | 2.32 | 1.15 | 2.54 | 1.15 | 259 | 227 | 2400 | 2400
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:15:00 | 2559.22 | 2366.82 | 827896.72 | 803500.32 | 34.83 | 3637.9 | 834.926 | -184.827 | 20 | 185 | 26.8 | 56.9 | 27.3 | 55.6 | 0 | 0 | - | - | 28.5 | 52 | 254 | 220 | 51.1 | 50.9 | 62.1 | 22.9 | 39.1 | 2.25 | 8.5 | 21.5 | 50.9 | 67.4 | 22.8 | 43.1 | 2.52 | 8.4 | 23.2 | 20.7 | 22.8 | 26.8 | 2.31 | 1.12 | 2.55 | 1.12 | 254 | 219 | 2400 | 2400
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:20:00 | 2559.22 | 2373.92 | 827896.72 | 803507.14 | 35.5 | 3652.809 | 820.017 | -2.861 | 20 | 185 | 26.8 | 56.9 | 27.2 | 55.6 | 0 | 0 | - | - | 28.5 | 52 | 247 | 215 | 51.5 | 51.3 | 61.8 | 22.4 | 38.8 | 2.24 | 8.4 | 21.7 | 51.4 | 67.8 | 22.5 | 43 | 2.51 | 8.5 | 23.7 | 20.3 | 22.3 | 26.6 | 2.31 | 1.11 | 2.54 | 1.11 | 246 | 214 | 2400 | 2400
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:25:00 | 2559.26 | 2377.22 | 827896.76 | 803510.48 | 36.16 | 3660.264 | 812.562 | -41.275 | 20 | 185 | 26.7 | 56.8 | 27.1 | 55.6 | 0 | 0 | - | - | 28.6 | 52 | 244 | 213 | 51 | 51.2 | 62 | 22.1 | 38.7 | 2.24 | 8.5 | 21.8 | 51.4 | 67.9 | 22.2 | 42.9 | 2.5 | 8.5 | 24 | 20 | 22.1 | 26.6 | 2.3 | 1.1 | 2.52 | 1.1 | 243 | 213 | 2400 | 2400
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:30:00 | 2559.32 | 2381.38 | 827896.82 | 803514.62 | 36.83 | 3660.264 | 812.562 | -37.74 | 20 | 185 | 26.6 | 56.7 | 27 | 55.6 | 0 | 0 | - | - | 28.5 | 52 | 239 | 212 | 51.5 | 51.7 | 62.1 | 21.7 | 38.6 | 2.22 | 8.5 | 22.1 | 51.4 | 67.8 | 21.8 | 42.8 | 2.5 | 8.5 | 23.9 | 19.7 | 21.7 | 26.7 | 2.29 | 1.08 | 2.53 | 1.09 | 239 | 212 | 2400 | 2400
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:35:00 | 2559.32 | 2385.02 | 827896.82 | 803518.24 | 37.49 | 3667.719 | 805.107 | -115.089 | 20 | 185 | 26.6 | 56.6 | 26.8 | 55.6 | 0 | 0 | - | - | 28.5 | 52 | 239 | 212 | 51 | 51.2 | 62 | 21.6 | 38.4 | 2.22 | 8.5 | 22.1 | 51.4 | 67.9 | 21.6 | 42.6 | 2.49 | 8.4 | 24.2 | 19.6 | 21.6 | 26.9 | 2.3 | 1.08 | 2.52 | 1.08 | 239 | 212 | 2400 | 2400
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:40:00 | 2559.32 | 2392.76 | 827896.82 | 803526 | 38.15 | 3667.719 | 805.107 | -103.918 | 20 | 185 | 26.5 | 56.4 | 26.8 | 55.5 | 0 | 0 | - | - | 28.5 | 52 | 239 | 210 | 51.5 | 51.7 | 61.9 | 21.2 | 38.3 | 2.21 | 8.5 | 22.3 | 51.4 | 68 | 21.3 | 42.6 | 2.49 | 8.4 | 24.3 | 19.3 | 21.2 | 26.4 | 2.26 | 1.07 | 2.53 | 1.08 | 239 | 209 | 2400 | 2400
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:45:00 | 2559.32 | 2399.26 | 827896.82 | 803532.5 | 38.81 | 3667.719 | 805.107 | -19.365 | 19 | 185 | 26.5 | 56.3 | 26.7 | 55.5 | 0 | 0 | - | - | 28.5 | 52.1 | 239 | 208 | 51.5 | 51.7 | 62 | 21.1 | 38.3 | 2.2 | 8.5 | 22.4 | 51.5 | 68.1 | 21.2 | 42.6 | 2.49 | 8.5 | 24.3 | 19.1 | 21.1 | 26.6 | 2.28 | 1.06 | 2.53 | 1.07 | 239 | 208 | 2400 | 2314
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:50:00 | 2559.36 | 2407.14 | 827896.86 | 803540.4 | 39.22 | 3667.719 | 805.107 | -125.609 | 19 | 185 | 26.5 | 56.2 | 26.6 | 55.5 | 0 | 0 | - | - | 28.5 | 52 | 217 | 0 | 45.6 | 45.6 | 63.5 | 21.6 | 40 | 2.32 | 8.3 | 22 | 45.1 | 42.8 | 31.1 | 32.1 | 1.69 | 9.6 | 14.8 | 20.6 | 21.9 | 26.7 | 2.4 | 1.09 | 1.67 | 1.42 | 217 | 0 | 2400 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 20:55:00 | 2559.36 | 2421.86 | 827896.86 | 803555.32 | 39.59 | 3690.084 | 782.742 | -199.477 | 19 | 185 | 26.4 | 56.2 | 26.6 | 55.4 | 0 | 0 | - | - | 28.5 | 51.9 | 217 | 0 | 45.5 | 45.7 | 64.6 | 22.4 | 40.4 | 2.33 | 8.7 | 22.8 | 45.6 | 32.9 | 45.1 | 29.7 | 1.44 | 22.1 | 10.2 | 21 | 22.4 | 26.6 | 2.39 | 1.11 | 1.43 | 1.45 | 217 | 0 | 2400 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:00:00 | 2559.36 | 2435.94 | 827896.86 | 803569.52 | 39.96 | 3704.994 | 767.832 | -127.858 | 19 | 185 | 26.4 | 56.2 | 26.6 | 55.3 | 0 | 0 | - | - | 28.5 | 51.8 | 217 | 0 | 44.5 | 44.7 | 64.3 | 22.4 | 40.1 | 2.32 | 8.6 | 22.7 | 44.7 | 32.6 | 43.2 | 28.4 | 1.43 | 20.2 | 10.1 | 21.1 | 22.4 | 26.2 | 2.39 | 1.11 | 1.43 | 1.46 | 217 | 0 | 2400 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:05:00 | 2559.36 | 2445.78 | 827896.86 | 803579.06 | 40.33 | 3712.449 | 760.377 | -107.359 | 18 | 185 | 26.3 | 56.2 | 26.5 | 55.3 | 0 | 0 | - | - | 28.6 | 51.8 | 217 | 0 | 45 | 44.7 | 64.2 | 22.4 | 40.1 | 2.32 | 8.6 | 22.7 | 44.7 | 32.1 | 41.1 | 27.7 | 1.43 | 18 | 9.7 | 21.1 | 22.4 | 26.3 | 2.39 | 1.11 | 1.43 | 1.46 | 217 | 0 | 2400 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:10:00 | 2559.36 | 2451.48 | 827896.86 | 803584.78 | 40.69 | 3712.449 | 760.377 | -88.491 | 18 | 185 | 26.3 | 56.1 | 26.4 | 55.4 | 0 | 0 | - | - | 28.6 | 51.7 | 217 | 0 | 44.9 | 45.2 | 64.4 | 22.4 | 40.2 | 2.33 | 8.6 | 22.6 | 45.3 | 32.1 | 39.9 | 27.2 | 1.43 | 16.8 | 9.6 | 21.1 | 22.4 | 26.4 | 2.4 | 1.11 | 1.43 | 1.46 | 217 | 0 | 2400 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:15:00 | 2559.4 | 2454.36 | 827896.9 | 803587.58 | 41.06 | 3712.449 | 760.377 | -24.592 | 18 | 185 | 26.3 | 56.1 | 26.4 | 55.4 | 0 | 0 | - | - | 28.6 | 51.6 | 217 | 0 | 45 | 45.2 | 64.5 | 22.3 | 40.2 | 2.33 | 8.6 | 22.8 | 45.3 | 32.1 | 38.9 | 26.9 | 1.42 | 15.9 | 9.8 | 20.9 | 22.3 | 26.4 | 2.39 | 1.1 | 1.43 | 1.45 | 217 | 0 | 2400 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:20:00 | 2559.4 | 2460.2 | 827896.9 | 803593.42 | 41.43 | 3719.904 | 752.922 | -55.901 | 18 | 185 | 26.2 | 56.1 | 26.3 | 55.4 | 0 | 0 | - | - | 28.6 | 51.6 | 217 | 0 | 45.5 | 45.7 | 64.7 | 22.2 | 40.4 | 2.33 | 8.6 | 23 | 45.9 | 32.1 | 38.1 | 26.9 | 1.42 | 15.1 | 9.9 | 20.9 | 22.2 | 26.8 | 2.4 | 1.1 | 1.42 | 1.45 | 217 | 0 | 2400 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:25:00 | 2559.4 | 2465.5 | 827896.9 | 803598.74 | 41.8 | 3734.813 | 738.013 | -41.845 | 18 | 185 | 26.1 | 56 | 26.2 | 55.4 | 0 | 0 | - | - | 28.6 | 51.6 | 216 | 0 | 45.1 | 45.2 | 64.4 | 22.2 | 40.2 | 2.32 | 8.4 | 22.8 | 44.9 | 31.9 | 36.9 | 27 | 1.41 | 14.3 | 9.9 | 20.7 | 22.2 | 26.3 | 2.39 | 1.1 | 1.41 | 1.44 | 216 | 0 | 2400 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:30:00 | 2559.4 | 2469.14 | 827896.9 | 803602.4 | 42.16 | 3742.268 | 730.558 | -27.06 | 18 | 185 | 26.1 | 56 | 26.1 | 55.4 | 0 | 0 | - | - | 28.6 | 51.5 | 216 | 0 | 44.6 | 44.7 | 64 | 22.1 | 39.9 | 2.31 | 8.5 | 22.7 | 44.4 | 31.3 | 34.9 | 27 | 1.41 | 12.3 | 9.5 | 20.7 | 22.1 | 26.3 | 2.38 | 1.09 | 1.41 | 1.43 | 215 | 0 | 2400 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:35:00 | 2564.24 | 2469.96 | 827901.88 | 803603.14 | 42.53 | 3734.813 | 738.013 | 65.719 | 18 | 185 | 26.1 | 56 | 26.1 | 55.5 | 0 | 0 | - | - | 28.6 | 51.5 | 215 | 0 | 44.6 | 44.7 | 64.1 | 21.8 | 39.9 | 2.31 | 8.5 | 22.8 | 44.4 | 30.8 | 32.9 | 27 | 1.4 | 10.5 | 9.1 | 20.6 | 21.9 | 26.3 | 2.38 | 1.09 | 1.4 | 1.43 | 215 | 0 | 2400 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:40:00 | 2565.42 | 2472.34 | 827902.92 | 803605.58 | 42.9 | 3742.268 | 730.558 | 10.203 | 18 | 185 | 26 | 56 | 26 | 55.4 | 0 | 0 | - | - | 28.6 | 51.5 | 215 | 0 | 44.7 | 44.7 | 64.1 | 21.7 | 39.9 | 2.31 | 8.5 | 22.8 | 44.9 | 30.8 | 31.7 | 27.1 | 1.4 | 9.4 | 9.1 | 20.4 | 21.8 | 26.2 | 2.38 | 1.09 | 1.4 | 1.43 | 215 | 0 | 2400 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:45:00 | 2568.58 | 2472.92 | 827906.24 | 803606.1 | 43.16 | 3734.813 | 738.013 | 103.885 | 18 | 185 | 25.9 | 55.9 | 25.9 | 55.5 | 0 | 0 | - | - | 28.6 | 51.4 | 0 | 0 | 32.2 | 32.4 | 62.3 | 21.2 | 36.1 | 1.73 | 28.1 | 32.6 | 36 | 30.7 | 30.9 | 27.2 | 1.39 | 8.7 | 9.2 | 21.7 | 21.9 | 26.4 | 1.71 | 0.8 | 1.4 | 1.43 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:50:00 | 2576.92 | 2472.92 | 827914.72 | 803606.1 | 43.25 | 3712.449 | 760.377 | 212.824 | 18 | 185 | 25.9 | 56.1 | 25.9 | 55.5 | 0 | 0 | - | - | 28.5 | 51.4 | 0 | 0 | 0 | 0 | 36.7 | 31.2 | 27.8 | 1.53 | 8.4 | 11.5 | 0 | 30.4 | 29.7 | 27.4 | 1.41 | 7.1 | 8.5 | 22.9 | 23 | 26.8 | 1.53 | 1.46 | 1.41 | 1.45 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 21:55:00 | 2582.12 | 2473.18 | 827919.64 | 803606.48 | 43.33 | 3712.449 | 760.377 | -87.466 | 18 | 185 | 25.8 | 56.2 | 25.9 | 55.5 | 0 | 0 | - | - | 28.5 | 51.3 | 0 | 0 | 0 | 0 | 29.6 | 35.8 | 28.6 | 1.47 | 12.1 | 5.6 | 0 | 30.2 | 28.9 | 27.5 | 1.42 | 5.8 | 7.8 | 23.3 | 23.4 | 26.9 | 1.49 | 1.49 | 1.43 | 1.46 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:00:00 | 2582.14 | 2484.78 | 827919.64 | 803618.2 | 43.42 | 3719.904 | 752.922 | -104.065 | 18 | 185 | 25.8 | 56.3 | 25.9 | 55.6 | 0 | 0 | - | - | 28.5 | 51.3 | 0 | 0 | 0 | 0 | 27.9 | 37.2 | 28.7 | 1.48 | 13.2 | 3.9 | 0 | 29.8 | 28.5 | 27.6 | 1.43 | 5.2 | 7.2 | 23.5 | 23.6 | 26.8 | 1.5 | 1.5 | 1.44 | 1.47 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:05:00 | 2582.14 | 2487.38 | 827919.64 | 803620.56 | 43.5 | 3690.084 | 782.742 | -8.696 | 18 | 185 | 25.7 | 56.3 | 25.9 | 55.6 | 0 | 0 | - | - | 28.5 | 51.3 | 0 | 0 | 0 | 0 | 27.7 | 36.9 | 28.4 | 1.48 | 12.8 | 3.4 | 0 | 29.5 | 28.2 | 27.7 | 1.44 | 4.7 | 6.7 | 23.6 | 23.8 | 26.7 | 1.5 | 1.51 | 1.45 | 1.48 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:10:00 | 2582.14 | 2488.04 | 827919.64 | 803621.22 | 43.58 | 3690.084 | 782.742 | -8.838 | 18 | 185 | 25.7 | 56.4 | 25.8 | 55.7 | 0 | 0 | - | - | 28.5 | 51.3 | 0 | 0 | 0 | 0 | 27.4 | 36.2 | 28.2 | 1.48 | 12 | 3.2 | 0 | 29.2 | 28.1 | 27.7 | 1.45 | 4.4 | 6.3 | 23.7 | 23.8 | 26.6 | 1.51 | 1.51 | 1.45 | 1.48 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:15:00 | 2582.14 | 2488.66 | 827919.64 | 803621.88 | 43.65 | 3690.084 | 782.742 | -8.831 | 18 | 185 | 25.7 | 56.4 | 25.8 | 55.7 | 0 | 0 | - | - | 28.4 | 51.3 | 0 | 0 | 0 | 0 | 27.2 | 35.4 | 27.8 | 1.48 | 11.1 | 3 | 0 | 28.7 | 27.8 | 27.7 | 1.45 | 4.2 | 5.8 | 23.7 | 23.8 | 26.6 | 1.51 | 1.51 | 1.45 | 1.48 | 0 | 0 | 0 | 0
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:20:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3682.629 | 790.197 | -0.623 | 18 | 185 | 25.7 | 56.5 | 25.7 | 55.8 | 0 | 0 | - | - | 28.4 | 51.4 | 0 | 0 | 0 | 0 | 27.3 | 35.4 | 27.9 | 1.49 | 11.1 | 3.1 | 0 | 28.6 | 27.7 | 27.6 | 1.45 | 4 | 5.6 | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:25:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3682.629 | 790.197 | -0.048 | 18 | 185 | 25.6 | 56.5 | 25.7 | 55.8 | 0 | 0 | - | - | 28.3 | 51.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:30:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3682.629 | 790.197 | -0.039 | 18 | 185 | 25.6 | 56.6 | 25.7 | 55.8 | 0 | 0 | - | - | 28.1 | 51.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:35:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3682.629 | 790.197 | -0.017 | 18 | 185 | 25.6 | 56.6 | 25.7 | 55.9 | 0 | 0 | - | - | 28 | 51.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:40:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3682.629 | 790.197 | -0.02 | 18 | 185 | 25.6 | 56.7 | 25.7 | 55.9 | 0 | 0 | - | - | 28 | 51.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:45:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3682.629 | 790.197 | -0.02 | 18 | 185 | 25.5 | 56.7 | 25.7 | 56 | 0 | 0 | - | - | 27.9 | 51.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:50:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.5 | 56.7 | 25.7 | 56 | 0 | 0 | - | - | 27.8 | 51.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 22:55:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.5 | 56.7 | 25.7 | 56 | 0 | 0 | - | - | 27.7 | 51.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:00:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.5 | 56.7 | 25.7 | 56 | 0 | 0 | - | - | 27.6 | 51.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:05:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.5 | 56.8 | 25.7 | 56 | 0 | 0 | - | - | 27.6 | 51.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:10:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.5 | 56.8 | 25.7 | 56 | 0 | 0 | - | - | 27.5 | 51.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:15:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.4 | 56.8 | 25.6 | 56 | 0 | 0 | - | - | 27.4 | 52 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:20:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.4 | 56.8 | 25.6 | 56.1 | 0 | 0 | - | - | 27.4 | 52 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:25:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.4 | 56.9 | 25.6 | 56.1 | 0 | 0 | - | - | 27.3 | 52.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:30:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.4 | 56.9 | 25.6 | 56.1 | 0 | 0 | - | - | 27.3 | 52.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:35:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.4 | 56.9 | 25.6 | 56.1 | 0 | 0 | - | - | 27.2 | 52.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:40:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.4 | 56.9 | 25.6 | 56.1 | 0 | 0 | - | - | 27.2 | 52.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:45:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.4 | 56.9 | 25.6 | 56.1 | 0 | 0 | - | - | 27.1 | 52.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:50:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.4 | 56.9 | 25.6 | 56.1 | 0 | 0 | - | - | 27.1 | 52.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-02 | / | SACU-34/B34-ESS04 | 2026-06-02 23:55:00 | 2582.14 | 2489.4 | 827919.64 | 803622.58 | 43.73 | 3675.174 | 797.652 | -0.02 | 18 | 185 | 25.4 | 56.9 | 25.6 | 56.1 | 0 | 0 | - | - | 27 | 52.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -