## 5 minutes
Time range: | 2026-06-02 00:00:00 - 2026-06-02 23:59:59
Export time: | 2026-06-03 01:22:53
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge energy(kWh) | Total discharge energy(kWh) | Daily auxiliary power consumption(kWh) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge power(kW) | SOC(%) | Equivalent number of cycles | Battery cabin temperature 1(℃) | Battery cabin humidity 1(%) | Battery cabin temperature 2(℃) | Battery cabin humidity 2(%) | CO concentration 1(ppm) | CO concentration 2(ppm) | H2 concentration 1(ppm) | H2 concentration 2(ppm) | Control unit cabin temperature 1(℃) | Control unit cabin humidity 1(%) | Control status of EEV 1(step) | Control status of EEV 2(step) | Running status of outdoor fan 1(%) | Running status of outdoor fan 2(%) | Discharge temperature of compressor 1(℃) | Suction temperature of refrigerant system 1(℃) | Condenser outlet temperature of refrigerant system 1(℃) | Condenser outlet pressure of refrigerant system 1(Mpa) | Suction superheat degree of refrigerant system 1(℃) | Discharge superheat degree of compressor 1(℃) | Running status of outdoor fan 3(%) | Discharge temperature of compressor 2(℃) | Suction temperature of refrigerant system 2(℃) | Condenser outlet temperature of refrigerant system 2(℃) | Condenser outlet pressure of refrigerant system 2(Mpa) | Suction superheat degree of refrigerant system 2(℃) | Discharge superheat degree of compressor 2(℃) | Battery-side supply water temperature(℃) | Battery-side return water temperature(℃) | Air intake temperature(℃) | Discharge pressure of refrigerant system 1(Mpa) | Suction pressure of refrigerant system 1(Mpa) | Discharge pressure of refrigerant system 2(Mpa) | Suction pressure of refrigerant system 2(Mpa) | Running status of EEV 1(step) | Running status of EEV 2(step) | Compressor 1 running status(rpm) | Compressor 2 running status(rpm)
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:00:00 | 0 | 1.16 | 823136.3 | 798281.52 | 0 | 3786.024 | 642.072 | -202.851 | 15 | 184 | 25.3 | 54 | 25.5 | 54.3 | 0 | 0 | - | - | 29.1 | 47.6 | 0 | 0 | 0 | 0 | 28.3 | 30.1 | 27.7 | 1.48 | 6.2 | 4.3 | 0 | 27.8 | 30.2 | 27.7 | 1.47 | 6.2 | 4.4 | 23.7 | 23.7 | 27.4 | 1.5 | 1.49 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:05:00 | 0 | 16.1 | 823136.3 | 798296.24 | 0.07 | 3808.166 | 619.932 | -186.048 | 15 | 184 | 25.3 | 54 | 25.5 | 54.3 | 0 | 0 | - | - | 29.1 | 47.6 | 0 | 0 | 0 | 0 | 28.2 | 30.1 | 27.7 | 1.48 | 6.1 | 4.2 | 0 | 27.8 | 30.1 | 27.8 | 1.47 | 6.1 | 4.3 | 23.7 | 23.7 | 27.5 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:10:00 | 0 | 33.18 | 823136.3 | 798313.08 | 0.14 | 3830.307 | 597.792 | -125.963 | 15 | 184 | 25.3 | 54.1 | 25.5 | 54.3 | 0 | 0 | - | - | 29 | 47.6 | 0 | 0 | 0 | 0 | 28.3 | 29.9 | 27.8 | 1.48 | 6 | 4.3 | 0 | 27.8 | 29.9 | 27.8 | 1.47 | 5.9 | 4.3 | 23.7 | 23.7 | 27.5 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:15:00 | 0.44 | 37.26 | 823136.8 | 798317.12 | 0.2 | 3830.307 | 597.792 | 22.718 | 14 | 184 | 25.3 | 54.1 | 25.5 | 54.3 | 0 | 0 | - | - | 29 | 47.7 | 0 | 0 | 0 | 0 | 28.3 | 29.8 | 27.8 | 1.48 | 5.9 | 4.2 | 0 | 27.8 | 29.8 | 27.9 | 1.48 | 5.8 | 4.3 | 23.8 | 23.7 | 27.6 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:20:00 | 6.36 | 37.5 | 823142.96 | 798317.34 | 0.26 | 3830.307 | 597.792 | 139.982 | 15 | 184 | 25.3 | 54.2 | 25.4 | 54.5 | 0 | 0 | - | - | 29 | 47.7 | 0 | 0 | 0 | 0 | 28.3 | 29.8 | 27.8 | 1.48 | 5.8 | 4.2 | 0 | 27.8 | 29.7 | 27.9 | 1.48 | 5.7 | 4.3 | 23.8 | 23.8 | 27.6 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:25:00 | 23.32 | 37.5 | 823159.88 | 798317.34 | 0.33 | 3808.166 | 619.932 | 209.757 | 15 | 184 | 25.3 | 54.2 | 25.3 | 54.7 | 0 | 0 | - | - | 29 | 47.8 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 27.8 | 1.48 | 5.7 | 4.1 | 0 | 27.7 | 29.7 | 27.9 | 1.48 | 5.6 | 4.2 | 23.8 | 23.7 | 27.6 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:30:00 | 44.08 | 37.5 | 823181.02 | 798317.34 | 0.39 | 3786.024 | 642.072 | 303.832 | 16 | 184 | 25.3 | 54.3 | 25.3 | 54.7 | 0 | 0 | - | - | 28.9 | 47.7 | 0 | 0 | 0 | 0 | 28.2 | 29.6 | 27.7 | 1.48 | 5.6 | 4 | 0 | 27.7 | 29.6 | 27.9 | 1.48 | 5.5 | 4.2 | 23.8 | 23.8 | 27.4 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:35:00 | 56.9 | 37.5 | 823193.4 | 798317.34 | 0.46 | 3771.264 | 656.832 | 83.371 | 16 | 184 | 25.2 | 54.3 | 25.4 | 54.6 | 0 | 0 | - | - | 28.9 | 47.8 | 0 | 0 | 0 | 0 | 28.1 | 29.6 | 27.7 | 1.48 | 5.5 | 3.9 | 0 | 27.7 | 29.4 | 27.9 | 1.48 | 5.4 | 4 | 23.8 | 23.8 | 27.4 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:40:00 | 61.66 | 37.56 | 823198.1 | 798317.4 | 0.52 | 3763.884 | 664.212 | 63.43 | 16 | 184 | 25.3 | 54.3 | 25.5 | 54.4 | 0 | 0 | - | - | 28.9 | 47.8 | 0 | 0 | 0 | 0 | 28.1 | 29.4 | 27.6 | 1.48 | 5.4 | 3.9 | 0 | 27.6 | 29.3 | 27.9 | 1.48 | 5.3 | 4 | 23.8 | 23.8 | 27.3 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:45:00 | 66.06 | 39.3 | 823202.36 | 798319.26 | 0.58 | 3763.884 | 664.212 | -71.45 | 16 | 184 | 25.2 | 54.3 | 25.4 | 54.4 | 0 | 0 | - | - | 28.9 | 47.9 | 0 | 0 | 0 | 0 | 28 | 29.3 | 27.6 | 1.48 | 5.4 | 3.9 | 0 | 27.6 | 29.3 | 27.8 | 1.48 | 5.2 | 4 | 23.8 | 23.8 | 27.3 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:50:00 | 67.44 | 41.2 | 823203.76 | 798321.04 | 0.64 | 3763.884 | 664.212 | 14.511 | 16 | 184 | 25.2 | 54.3 | 25.3 | 54.7 | 0 | 0 | - | - | 28.9 | 47.9 | 0 | 0 | 0 | 0 | 28 | 29.3 | 27.6 | 1.48 | 5.3 | 3.8 | 0 | 27.5 | 29.2 | 27.8 | 1.48 | 5.2 | 3.9 | 23.8 | 23.8 | 27.3 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 00:55:00 | 67.5 | 45.7 | 823203.82 | 798325.56 | 0.7 | 3771.264 | 656.832 | -5.932 | 16 | 184 | 25.2 | 54.4 | 25.2 | 54.9 | 0 | 0 | - | - | 28.8 | 47.9 | 0 | 0 | 0 | 0 | 28 | 29.2 | 27.6 | 1.48 | 5.2 | 3.9 | 0 | 27.5 | 29.2 | 27.8 | 1.48 | 5.1 | 3.9 | 23.8 | 23.8 | 27.3 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:00:00 | 67.88 | 49.66 | 823204.18 | 798329.5 | 0.77 | 3778.644 | 649.452 | -9.134 | 16 | 184 | 25.2 | 54.4 | 25.4 | 54.6 | 0 | 0 | - | - | 28.8 | 47.9 | 0 | 0 | 0 | 0 | 28 | 29.2 | 27.6 | 1.48 | 5.2 | 3.8 | 0 | 27.5 | 29.2 | 27.8 | 1.48 | 5.1 | 3.9 | 23.8 | 23.8 | 27.2 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:05:00 | 70.88 | 50.32 | 823207.22 | 798330.2 | 0.83 | 3771.264 | 656.832 | -28.249 | 16 | 184 | 25.2 | 54.4 | 25.5 | 54.5 | 0 | 0 | - | - | 28.8 | 47.9 | 0 | 0 | 0 | 0 | 27.9 | 29.2 | 27.6 | 1.48 | 5.1 | 3.8 | 0 | 27.5 | 29.1 | 27.8 | 1.48 | 5 | 3.9 | 23.9 | 23.9 | 27.1 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:10:00 | 71.36 | 54.38 | 823207.66 | 798334.42 | 0.89 | 3778.644 | 649.452 | -18.272 | 16 | 184 | 25.2 | 54.4 | 25.5 | 54.4 | 0 | 0 | - | - | 28.8 | 48 | 0 | 0 | 0 | 0 | 27.9 | 29.1 | 27.6 | 1.48 | 5 | 3.8 | 0 | 27.5 | 29.1 | 27.8 | 1.48 | 4.9 | 3.9 | 23.8 | 23.8 | 27.1 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:15:00 | 71.6 | 63.2 | 823207.9 | 798343.08 | 0.95 | 3786.024 | 642.072 | -48.416 | 16 | 184 | 25.3 | 54.4 | 25.5 | 54.4 | 0 | 0 | - | - | 28.8 | 48 | 0 | 0 | 0 | 0 | 27.9 | 29.1 | 27.6 | 1.48 | 4.9 | 3.8 | 0 | 27.4 | 28.9 | 27.8 | 1.48 | 4.9 | 3.8 | 23.9 | 23.9 | 27.2 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:20:00 | 73.24 | 64.04 | 823209.62 | 798343.88 | 1.01 | 3786.024 | 642.072 | 33.619 | 16 | 184 | 25.3 | 54.3 | 25.6 | 54.4 | 0 | 0 | - | - | 28.7 | 48 | 0 | 0 | 0 | 0 | 27.9 | 28.9 | 27.6 | 1.48 | 4.8 | 3.7 | 0 | 27.4 | 28.8 | 27.8 | 1.48 | 4.8 | 3.8 | 23.9 | 23.9 | 27.1 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:25:00 | 74.88 | 67.06 | 823211.22 | 798346.96 | 1.07 | 3786.024 | 642.072 | 8.728 | 16 | 184 | 25.3 | 54.3 | 25.6 | 54.3 | 0 | 0 | - | - | 28.7 | 48 | 0 | 0 | 0 | 0 | 27.9 | 28.9 | 27.6 | 1.48 | 4.8 | 3.7 | 0 | 27.4 | 28.8 | 27.8 | 1.48 | 4.7 | 3.7 | 23.9 | 23.9 | 27.1 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:30:00 | 75.1 | 70.28 | 823211.4 | 798350.2 | 1.13 | 3786.024 | 642.072 | -56.342 | 16 | 184 | 25.3 | 54.3 | 25.6 | 54.3 | 0 | 0 | - | - | 28.7 | 48.1 | 0 | 0 | 0 | 0 | 27.9 | 28.8 | 27.6 | 1.48 | 4.7 | 3.7 | 0 | 27.4 | 28.7 | 27.8 | 1.48 | 4.6 | 3.8 | 23.9 | 23.9 | 27.1 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:35:00 | 75.1 | 75.04 | 823211.4 | 798354.92 | 1.19 | 3786.024 | 642.072 | -60.1 | 16 | 184 | 25.3 | 54.3 | 25.6 | 54.3 | 0 | 0 | - | - | 28.7 | 48.1 | 0 | 0 | 0 | 0 | 27.9 | 28.8 | 27.6 | 1.49 | 4.7 | 3.7 | 0 | 27.4 | 28.7 | 27.8 | 1.48 | 4.5 | 3.8 | 23.9 | 23.9 | 27.1 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:40:00 | 75.1 | 78.68 | 823211.4 | 798358.58 | 1.26 | 3786.024 | 642.072 | -22.428 | 15 | 184 | 25.4 | 54.2 | 25.6 | 54.3 | 0 | 0 | - | - | 28.7 | 48.1 | 0 | 0 | 0 | 0 | 28 | 28.8 | 27.6 | 1.49 | 4.6 | 3.6 | 0 | 27.4 | 28.6 | 27.8 | 1.48 | 4.4 | 3.7 | 23.9 | 23.9 | 27.1 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:45:00 | 75.52 | 81.44 | 823211.82 | 798361.36 | 1.32 | 3786.024 | 642.072 | -39.776 | 15 | 184 | 25.4 | 54.2 | 25.6 | 54.3 | 0 | 0 | - | - | 28.7 | 48.2 | 0 | 0 | 0 | 0 | 27.9 | 28.7 | 27.6 | 1.49 | 4.6 | 3.7 | 0 | 27.4 | 28.6 | 27.7 | 1.48 | 4.4 | 3.7 | 23.9 | 23.9 | 27 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:50:00 | 76.1 | 84.9 | 823212.4 | 798364.82 | 1.38 | 3786.024 | 642.072 | -54.885 | 15 | 184 | 25.4 | 54.2 | 25.6 | 54.3 | 0 | 0 | - | - | 28.7 | 48.1 | 0 | 0 | 0 | 0 | 27.9 | 28.7 | 27.6 | 1.48 | 4.6 | 3.7 | 0 | 27.4 | 28.4 | 27.7 | 1.48 | 4.3 | 3.7 | 23.9 | 23.9 | 26.9 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 01:55:00 | 78.86 | 87.44 | 823215.46 | 798367.28 | 1.44 | 3786.024 | 642.072 | 228.354 | 15 | 184 | 25.4 | 54.2 | 25.7 | 54.3 | 0 | 0 | - | - | 28.7 | 48.1 | 0 | 0 | 0 | 0 | 27.9 | 28.7 | 27.5 | 1.48 | 4.5 | 3.7 | 0 | 27.4 | 28.4 | 27.7 | 1.48 | 4.3 | 3.7 | 23.9 | 23.9 | 26.9 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:00:00 | 87.26 | 90.7 | 823223.56 | 798370.62 | 1.5 | 3786.024 | 642.072 | -34.205 | 16 | 184 | 25.4 | 54.1 | 25.7 | 54.2 | 0 | 0 | - | - | 28.6 | 48.2 | 0 | 0 | 0 | 0 | 27.9 | 28.7 | 27.5 | 1.48 | 4.5 | 3.7 | 0 | 27.4 | 28.3 | 27.7 | 1.48 | 4.2 | 3.8 | 24 | 23.9 | 27 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:05:00 | 87.26 | 95.96 | 823223.56 | 798375.96 | 1.57 | 3786.024 | 642.072 | -14.736 | 15 | 184 | 25.4 | 54.2 | 25.7 | 54.2 | 0 | 0 | - | - | 28.6 | 48.2 | 0 | 0 | 0 | 0 | 28 | 28.6 | 27.5 | 1.48 | 4.6 | 3.8 | 0 | 27.4 | 28.2 | 27.7 | 1.48 | 4.2 | 3.7 | 24 | 24 | 27 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:10:00 | 87.54 | 98.26 | 823223.84 | 798378.26 | 1.63 | 3800.785 | 627.312 | -65.773 | 15 | 184 | 25.5 | 54.1 | 25.7 | 54.2 | 0 | 0 | - | - | 28.6 | 48.2 | 0 | 0 | 0 | 0 | 28 | 28.6 | 27.5 | 1.48 | 4.5 | 3.9 | 0 | 27.4 | 28.2 | 27.7 | 1.48 | 4.1 | 3.8 | 24 | 24 | 27 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:15:00 | 88.1 | 98.8 | 823224.4 | 798378.64 | 1.69 | 3800.785 | 627.312 | 2.843 | 15 | 184 | 25.5 | 54.1 | 25.7 | 54.2 | 0 | 0 | - | - | 28.6 | 48.2 | 0 | 0 | 0 | 0 | 28 | 28.6 | 27.5 | 1.48 | 4.5 | 3.9 | 0 | 27.4 | 28.2 | 27.7 | 1.48 | 4.1 | 3.8 | 24 | 24 | 26.9 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:20:00 | 89.42 | 99.74 | 823225.72 | 798379.62 | 1.75 | 3793.404 | 634.692 | -41.855 | 15 | 184 | 25.5 | 54.1 | 25.7 | 54.2 | 0 | 0 | - | - | 28.6 | 48.3 | 0 | 0 | 0 | 0 | 28 | 28.4 | 27.5 | 1.48 | 4.5 | 3.8 | 0 | 27.4 | 28.2 | 27.7 | 1.48 | 4.1 | 3.8 | 24 | 24 | 27 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:25:00 | 90.42 | 99.94 | 823226.82 | 798379.78 | 1.81 | 3756.504 | 671.592 | 52.843 | 15 | 184 | 25.5 | 54.1 | 25.7 | 54.2 | 0 | 0 | - | - | 28.6 | 48.3 | 0 | 0 | 0 | 0 | 28 | 28.4 | 27.5 | 1.48 | 4.5 | 3.9 | 0 | 27.4 | 28.2 | 27.7 | 1.48 | 4.1 | 3.8 | 24 | 24 | 27.1 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:30:00 | 97 | 100.08 | 823233.58 | 798379.92 | 1.87 | 3786.024 | 642.072 | 93.743 | 16 | 184 | 25.5 | 54.1 | 25.7 | 54.2 | 0 | 0 | - | - | 28.6 | 48.3 | 0 | 0 | 0 | 0 | 28 | 28.4 | 27.5 | 1.48 | 4.5 | 3.9 | 0 | 27.4 | 28.2 | 27.8 | 1.48 | 4.1 | 3.9 | 24 | 24 | 27.1 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:35:00 | 100.64 | 102.94 | 823236.94 | 798382.86 | 1.93 | 3786.024 | 642.072 | -53.785 | 16 | 184 | 25.5 | 54.1 | 25.7 | 54.2 | 0 | 0 | - | - | 28.6 | 48.3 | 0 | 0 | 0 | 0 | 28 | 28.4 | 27.5 | 1.48 | 4.4 | 3.9 | 0 | 27.4 | 28.1 | 27.7 | 1.48 | 4 | 3.9 | 24.1 | 24 | 27.1 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:40:00 | 101.34 | 105.22 | 823237.64 | 798385.08 | 1.99 | 3786.024 | 642.072 | 20.503 | 16 | 184 | 25.5 | 54.1 | 25.7 | 54.2 | 0 | 0 | - | - | 28.6 | 48.4 | 0 | 0 | 0 | 0 | 28 | 28.3 | 27.5 | 1.48 | 4.4 | 3.9 | 0 | 27.4 | 28.1 | 27.8 | 1.48 | 4 | 3.8 | 24.1 | 24 | 27.1 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:45:00 | 102.54 | 106.66 | 823238.86 | 798386.5 | 2.05 | 3786.024 | 642.072 | 11.649 | 16 | 184 | 25.5 | 54.1 | 25.7 | 54.2 | 0 | 0 | - | - | 28.6 | 48.3 | 0 | 0 | 0 | 0 | 28 | 28.2 | 27.5 | 1.48 | 4.3 | 3.9 | 0 | 27.4 | 28.1 | 27.8 | 1.48 | 4 | 3.8 | 24.1 | 24.1 | 26.9 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:50:00 | 105.64 | 106.66 | 823242.02 | 798386.54 | 2.12 | 3786.024 | 642.072 | -16.423 | 16 | 184 | 25.5 | 54.1 | 25.7 | 54.2 | 0 | 0 | - | - | 28.6 | 48.3 | 0 | 0 | 0 | 0 | 27.9 | 28.2 | 27.4 | 1.48 | 4.2 | 3.9 | 0 | 27.4 | 27.9 | 27.8 | 1.48 | 3.9 | 3.9 | 24.1 | 24.1 | 26.9 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 02:55:00 | 108.38 | 107.14 | 823244.68 | 798386.98 | 2.18 | 3786.024 | 642.072 | -70.647 | 16 | 184 | 25.5 | 54.1 | 25.8 | 54.2 | 0 | 0 | - | - | 28.6 | 48.4 | 0 | 0 | 0 | 0 | 27.9 | 28.1 | 27.4 | 1.48 | 4.2 | 3.9 | 0 | 27.4 | 27.8 | 27.7 | 1.48 | 3.9 | 3.9 | 24.1 | 24.1 | 26.8 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:00:00 | 108.6 | 110.88 | 823244.9 | 798390.74 | 2.24 | 3786.024 | 642.072 | -76.373 | 16 | 184 | 25.6 | 54.1 | 25.8 | 54.2 | 0 | 0 | - | - | 28.6 | 48.4 | 0 | 0 | 0 | 0 | 27.9 | 28.1 | 27.4 | 1.48 | 4.1 | 3.9 | 0 | 27.4 | 27.8 | 27.7 | 1.48 | 3.8 | 3.8 | 24.1 | 24.1 | 26.8 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:05:00 | 108.6 | 115.32 | 823244.9 | 798395.26 | 2.3 | 3786.024 | 642.072 | -16.008 | 15 | 184 | 25.5 | 54.1 | 25.7 | 54.2 | 0 | 0 | - | - | 28.5 | 48.4 | 0 | 0 | 0 | 0 | 27.9 | 28.1 | 27.4 | 1.48 | 4.1 | 3.9 | 0 | 27.3 | 27.7 | 27.7 | 1.48 | 3.7 | 3.8 | 24.1 | 24.1 | 26.8 | 1.5 | 1.49 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:10:00 | 109.82 | 118.18 | 823246.12 | 798398.28 | 2.36 | 3786.024 | 642.072 | -110.11 | 15 | 184 | 25.5 | 54.1 | 25.8 | 54.2 | 0 | 0 | - | - | 28.6 | 48.4 | 0 | 0 | 0 | 0 | 27.9 | 27.9 | 27.4 | 1.48 | 4 | 3.8 | 0 | 27.3 | 27.6 | 27.7 | 1.48 | 3.6 | 3.8 | 24.1 | 24.1 | 26.7 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:15:00 | 109.82 | 124.56 | 823246.12 | 798404.6 | 2.42 | 3800.785 | 627.312 | -108.105 | 15 | 184 | 25.5 | 54.1 | 25.8 | 54.2 | 0 | 0 | - | - | 28.5 | 48.5 | 0 | 0 | 0 | 0 | 27.8 | 27.9 | 27.3 | 1.48 | 4 | 3.8 | 0 | 27.3 | 27.6 | 27.7 | 1.48 | 3.6 | 3.8 | 24.1 | 24.1 | 26.7 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:20:00 | 109.82 | 135.72 | 823246.12 | 798415.7 | 2.49 | 3822.926 | 605.172 | -123.156 | 15 | 184 | 25.5 | 54.1 | 25.7 | 54.3 | 0 | 0 | - | - | 28.5 | 48.5 | 0 | 0 | 0 | 0 | 27.8 | 27.9 | 27.3 | 1.48 | 3.9 | 3.8 | 0 | 27.3 | 27.6 | 27.7 | 1.47 | 3.5 | 3.8 | 24.1 | 24.1 | 26.7 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:25:00 | 109.82 | 149.1 | 823246.12 | 798429.02 | 2.55 | 3830.307 | 597.792 | -63.417 | 15 | 184 | 25.5 | 54.1 | 25.7 | 54.3 | 0 | 0 | - | - | 28.5 | 48.5 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.3 | 1.48 | 3.8 | 3.7 | 0 | 27.2 | 27.4 | 27.7 | 1.48 | 3.4 | 3.7 | 24.1 | 24.1 | 26.7 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:30:00 | 110.52 | 152 | 823246.82 | 798431.98 | 2.62 | 3830.307 | 597.792 | -23.3 | 15 | 184 | 25.5 | 54.2 | 25.7 | 54.3 | 0 | 0 | - | - | 28.5 | 48.6 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.3 | 1.48 | 3.8 | 3.7 | 0 | 27.2 | 27.4 | 27.6 | 1.48 | 3.4 | 3.7 | 24.2 | 24.2 | 26.7 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:35:00 | 113.02 | 153.1 | 823249.46 | 798432.94 | 2.68 | 3830.307 | 597.792 | 60.672 | 15 | 184 | 25.5 | 54.2 | 25.7 | 54.3 | 0 | 0 | - | - | 28.5 | 48.6 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.3 | 1.48 | 3.8 | 3.7 | 0 | 27.2 | 27.4 | 27.6 | 1.48 | 3.4 | 3.7 | 24.2 | 24.2 | 26.7 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:40:00 | 114.9 | 155.84 | 823251.2 | 798435.74 | 2.74 | 3830.307 | 597.792 | -32.94 | 15 | 184 | 25.5 | 54.2 | 25.7 | 54.3 | 0 | 0 | - | - | 28.4 | 48.6 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.3 | 1.48 | 3.8 | 3.7 | 0 | 27.2 | 27.4 | 27.6 | 1.48 | 3.4 | 3.6 | 24.2 | 24.2 | 26.8 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:45:00 | 116.98 | 157.92 | 823253.52 | 798437.76 | 2.81 | 3830.307 | 597.792 | 137.96 | 15 | 184 | 25.5 | 54.2 | 25.7 | 54.3 | 0 | 0 | - | - | 28.4 | 48.6 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.4 | 1.48 | 3.8 | 3.7 | 0 | 27.2 | 27.4 | 27.7 | 1.48 | 3.4 | 3.7 | 24.2 | 24.2 | 26.8 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:50:00 | 119.56 | 158.54 | 823255.86 | 798438.38 | 2.87 | 3830.307 | 597.792 | -6.722 | 15 | 184 | 25.5 | 54.3 | 25.7 | 54.4 | 0 | 0 | - | - | 28.4 | 48.7 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.4 | 1.48 | 3.8 | 3.8 | 0 | 27.2 | 27.5 | 27.7 | 1.48 | 3.4 | 3.7 | 24.2 | 24.2 | 26.9 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 03:55:00 | 120.24 | 159.24 | 823256.54 | 798439.12 | 2.93 | 3830.307 | 597.792 | -16.998 | 15 | 184 | 25.4 | 54.3 | 25.7 | 54.4 | 0 | 0 | - | - | 28.4 | 48.7 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.5 | 1.48 | 3.8 | 3.7 | 0 | 27.2 | 27.5 | 27.7 | 1.48 | 3.4 | 3.7 | 24.2 | 24.2 | 26.9 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:00:00 | 120.42 | 160.52 | 823256.72 | 798440.36 | 2.99 | 3830.307 | 597.792 | -38.944 | 15 | 184 | 25.4 | 54.4 | 25.7 | 54.4 | 0 | 0 | - | - | 28.4 | 48.8 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.5 | 1.48 | 3.8 | 3.7 | 0 | 27.3 | 27.5 | 27.7 | 1.48 | 3.4 | 3.8 | 24.2 | 24.2 | 26.9 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:05:00 | 121.02 | 160.9 | 823257.32 | 798440.74 | 3.06 | 3830.307 | 597.792 | 4.555 | 15 | 184 | 25.4 | 54.4 | 25.7 | 54.5 | 0 | 0 | - | - | 28.3 | 48.8 | 0 | 0 | 0 | 0 | 27.8 | 27.9 | 27.5 | 1.48 | 3.8 | 3.7 | 0 | 27.2 | 27.5 | 27.7 | 1.48 | 3.4 | 3.7 | 24.2 | 24.2 | 26.9 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:10:00 | 123.1 | 161.08 | 823259.4 | 798440.96 | 3.12 | 3830.307 | 597.792 | -52.708 | 15 | 184 | 25.4 | 54.5 | 25.7 | 54.5 | 0 | 0 | - | - | 28.3 | 48.8 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.5 | 1.48 | 3.8 | 3.7 | 0 | 27.3 | 27.5 | 27.7 | 1.48 | 3.4 | 3.7 | 24.3 | 24.2 | 26.9 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:15:00 | 123.88 | 162.7 | 823260.24 | 798442.54 | 3.18 | 3830.307 | 597.792 | 29.141 | 15 | 184 | 25.4 | 54.5 | 25.6 | 54.5 | 0 | 0 | - | - | 28.3 | 48.8 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.5 | 1.48 | 3.8 | 3.7 | 0 | 27.3 | 27.5 | 27.7 | 1.48 | 3.4 | 3.7 | 24.2 | 24.2 | 27 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:20:00 | 125.64 | 164.84 | 823261.94 | 798444.72 | 3.25 | 3830.307 | 597.792 | -90.269 | 15 | 184 | 25.4 | 54.5 | 25.6 | 54.5 | 0 | 0 | - | - | 28.3 | 48.9 | 0 | 0 | 0 | 0 | 27.8 | 27.8 | 27.5 | 1.48 | 3.8 | 3.7 | 0 | 27.3 | 27.5 | 27.7 | 1.48 | 3.4 | 3.7 | 24.3 | 24.2 | 26.9 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:25:00 | 125.64 | 174.28 | 823261.94 | 798454.36 | 3.31 | 3837.688 | 590.412 | -83.344 | 14 | 184 | 25.3 | 54.5 | 25.6 | 54.6 | 0 | 0 | - | - | 28.3 | 48.9 | 0 | 0 | 0 | 0 | 27.7 | 27.8 | 27.4 | 1.48 | 3.7 | 3.6 | 0 | 27.2 | 27.4 | 27.8 | 1.48 | 3.3 | 3.7 | 24.3 | 24.3 | 27 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:30:00 | 125.64 | 181.06 | 823261.94 | 798461.12 | 3.37 | 3845.068 | 583.032 | -108.004 | 14 | 184 | 25.3 | 54.6 | 25.5 | 54.7 | 0 | 0 | - | - | 28.3 | 49 | 0 | 0 | 0 | 0 | 27.7 | 27.8 | 27.5 | 1.48 | 3.7 | 3.6 | 0 | 27.2 | 27.4 | 27.7 | 1.48 | 3.3 | 3.7 | 24.3 | 24.3 | 26.8 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:35:00 | 125.64 | 189.28 | 823261.94 | 798469.32 | 3.44 | 3859.83 | 568.272 | -75.53 | 14 | 184 | 25.3 | 54.7 | 25.4 | 55 | 0 | 0 | - | - | 28.2 | 49 | 0 | 0 | 0 | 0 | 27.7 | 27.7 | 27.4 | 1.48 | 3.6 | 3.6 | 0 | 27.2 | 27.4 | 27.7 | 1.48 | 3.2 | 3.6 | 24.3 | 24.3 | 26.8 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:40:00 | 127.26 | 193.42 | 823263.56 | 798473.44 | 3.5 | 3867.21 | 560.892 | -153.324 | 14 | 184 | 25.3 | 54.7 | 25.4 | 55 | 0 | 0 | - | - | 28.2 | 49 | 0 | 0 | 0 | 0 | 27.7 | 27.7 | 27.4 | 1.48 | 3.6 | 3.5 | 0 | 27.2 | 27.3 | 27.7 | 1.48 | 3.1 | 3.6 | 24.3 | 24.3 | 26.8 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:45:00 | 127.4 | 198.38 | 823263.7 | 798478.22 | 3.56 | 3874.59 | 553.512 | 41.421 | 14 | 184 | 25.3 | 54.7 | 25.5 | 54.8 | 0 | 0 | - | - | 28.2 | 49.1 | 0 | 0 | 0 | 0 | 27.7 | 27.7 | 27.4 | 1.48 | 3.6 | 3.4 | 0 | 27.2 | 27.3 | 27.7 | 1.48 | 3.1 | 3.5 | 24.3 | 24.3 | 26.8 | 1.5 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:50:00 | 132.96 | 198.4 | 823269.26 | 798478.24 | 3.62 | 3859.83 | 568.272 | 25.763 | 14 | 184 | 25.3 | 54.7 | 25.6 | 54.8 | 0 | 0 | - | - | 28.2 | 49.1 | 0 | 0 | 0 | 0 | 27.7 | 27.7 | 27.3 | 1.48 | 3.6 | 3.5 | 0 | 27.2 | 27.3 | 27.7 | 1.48 | 3.2 | 3.5 | 24.3 | 24.3 | 26.9 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 04:55:00 | 134.26 | 200.46 | 823270.56 | 798480.3 | 3.69 | 3867.21 | 560.892 | 16.372 | 14 | 184 | 25.3 | 54.8 | 25.6 | 54.7 | 0 | 0 | - | - | 28.2 | 49.1 | 0 | 0 | 0 | 0 | 27.7 | 27.7 | 27.3 | 1.48 | 3.6 | 3.5 | 0 | 27.1 | 27.3 | 27.7 | 1.48 | 3.2 | 3.5 | 24.3 | 24.3 | 26.8 | 1.51 | 1.5 | 1.48 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:00:00 | 135.2 | 203.74 | 823271.5 | 798483.64 | 3.75 | 3874.59 | 553.512 | -5.576 | 14 | 184 | 25.3 | 54.8 | 25.4 | 55 | 0 | 0 | - | - | 28.2 | 49.1 | 0 | 0 | 0 | 0 | 27.7 | 27.7 | 27.3 | 1.48 | 3.6 | 3.5 | 0 | 27.1 | 27.3 | 27.6 | 1.48 | 3.1 | 3.5 | 24.3 | 24.3 | 26.8 | 1.51 | 1.5 | 1.48 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:05:00 | 135.32 | 207.38 | 823271.62 | 798487.28 | 3.81 | 3874.59 | 553.512 | -137.59 | 14 | 184 | 25.2 | 54.8 | 25.3 | 55.2 | 0 | 0 | - | - | 28.2 | 49.1 | 0 | 0 | 0 | 0 | 27.7 | 27.7 | 27.3 | 1.48 | 3.6 | 3.4 | 0 | 27.1 | 27.3 | 27.6 | 1.48 | 3.1 | 3.5 | 24.4 | 24.4 | 26.8 | 1.51 | 1.5 | 1.48 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:10:00 | 135.32 | 216.04 | 823271.62 | 798496 | 3.88 | 3874.59 | 553.512 | -80.149 | 14 | 184 | 25.2 | 54.9 | 25.5 | 55 | 0 | 0 | - | - | 28.2 | 49.2 | 0 | 0 | 0 | 0 | 27.7 | 27.7 | 27.3 | 1.48 | 3.6 | 3.4 | 0 | 27.1 | 27.3 | 27.6 | 1.48 | 3.1 | 3.4 | 24.4 | 24.4 | 27 | 1.51 | 1.5 | 1.48 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:15:00 | 135.34 | 223.66 | 823271.64 | 798503.54 | 3.94 | 3881.97 | 546.132 | -0.756 | 14 | 184 | 25.2 | 54.9 | 25.5 | 54.8 | 0 | 0 | - | - | 28.2 | 49.1 | 0 | 0 | 0 | 0 | 27.7 | 27.7 | 27.3 | 1.48 | 3.6 | 3.4 | 0 | 27.1 | 27.3 | 27.6 | 1.48 | 3.1 | 3.4 | 24.4 | 24.4 | 27 | 1.51 | 1.51 | 1.48 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:20:00 | 135.34 | 231.56 | 823271.64 | 798511.48 | 4 | 3889.35 | 538.752 | -194.07 | 13 | 184 | 25.3 | 54.9 | 25.6 | 54.8 | 0 | 0 | - | - | 28.2 | 49.2 | 0 | 0 | 0 | 0 | 27.7 | 27.8 | 27.4 | 1.48 | 3.6 | 3.4 | 0 | 27.1 | 27.3 | 27.7 | 1.48 | 3.1 | 3.4 | 24.4 | 24.4 | 27 | 1.51 | 1.51 | 1.48 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:25:00 | 135.34 | 248.08 | 823271.64 | 798528.16 | 4.07 | 3926.25 | 501.848 | -126.969 | 12 | 184 | 25.3 | 54.8 | 25.6 | 54.8 | 0 | 0 | - | - | 28.1 | 49.2 | 0 | 0 | 0 | 0 | 27.7 | 27.8 | 27.4 | 1.48 | 3.6 | 3.4 | 0 | 27.1 | 27.4 | 27.7 | 1.48 | 3.1 | 3.4 | 24.4 | 24.4 | 27.1 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:30:00 | 135.34 | 261.28 | 823271.64 | 798541.48 | 4.13 | 3933.63 | 494.468 | -139.408 | 12 | 184 | 25.3 | 54.9 | 25.6 | 54.8 | 0 | 0 | - | - | 28.1 | 49.2 | 0 | 0 | 0 | 0 | 27.7 | 27.8 | 27.5 | 1.48 | 3.6 | 3.4 | 0 | 27.2 | 27.4 | 27.7 | 1.48 | 3.1 | 3.4 | 24.5 | 24.5 | 27 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:35:00 | 135.34 | 276.96 | 823271.64 | 798557.26 | 4.2 | 3970.53 | 457.567 | -255.422 | 11 | 184 | 25.3 | 54.8 | 25.6 | 54.8 | 0 | 0 | - | - | 28.2 | 49.2 | 0 | 0 | 0 | 0 | 27.7 | 27.8 | 27.5 | 1.49 | 3.6 | 3.5 | 0 | 27.2 | 27.4 | 27.7 | 1.49 | 3.1 | 3.5 | 24.5 | 24.5 | 27.1 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:40:00 | 147.58 | 284.5 | 823284.48 | 798564.34 | 4.27 | 3985.29 | 442.807 | 413.277 | 11 | 184 | 25.3 | 54.8 | 25.6 | 54.8 | 0 | 0 | - | - | 28.2 | 49.2 | 0 | 0 | 0 | 0 | 27.7 | 27.8 | 27.5 | 1.49 | 3.5 | 3.4 | 0 | 27.2 | 27.4 | 27.7 | 1.49 | 3.1 | 3.4 | 24.6 | 24.6 | 27.1 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:45:00 | 182.04 | 284.5 | 823318.72 | 798564.34 | 4.35 | 3955.77 | 472.327 | 439.669 | 12 | 184 | 25.3 | 54.8 | 25.7 | 54.8 | 0 | 0 | - | - | 28.2 | 49.2 | 0 | 0 | 0 | 0 | 27.7 | 27.8 | 27.6 | 1.49 | 3.5 | 3.4 | 0 | 27.2 | 27.4 | 27.8 | 1.49 | 3.1 | 3.4 | 24.6 | 24.6 | 27.1 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:50:00 | 207.16 | 284.5 | 823344.02 | 798564.34 | 4.42 | 3918.87 | 509.228 | 473.778 | 13 | 184 | 25.4 | 54.8 | 25.7 | 54.7 | 0 | 0 | - | - | 28.2 | 49.1 | 0 | 0 | 0 | 0 | 27.7 | 27.8 | 27.6 | 1.49 | 3.5 | 3.4 | 0 | 27.2 | 27.4 | 27.8 | 1.49 | 3.1 | 3.4 | 24.6 | 24.6 | 27.1 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 05:55:00 | 245.42 | 284.5 | 823382.14 | 798564.34 | 4.49 | 3874.589 | 553.512 | 246.323 | 14 | 184 | 25.4 | 54.8 | 25.8 | 54.7 | 0 | 0 | - | - | 28.2 | 49.2 | 0 | 0 | 0 | 0 | 27.8 | 27.9 | 27.7 | 1.49 | 3.6 | 3.5 | 0 | 27.2 | 27.4 | 27.8 | 1.49 | 3.1 | 3.4 | 24.6 | 24.6 | 27.2 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:00:00 | 256.96 | 287.94 | 823393.26 | 798568.32 | 4.56 | 3874.589 | 553.512 | -242.074 | 14 | 184 | 25.4 | 54.8 | 25.8 | 54.5 | 0 | 0 | - | - | 28.3 | 49.1 | 0 | 0 | 0 | 0 | 28 | 27.9 | 27.8 | 1.49 | 3.6 | 3.6 | 0 | 27.4 | 27.5 | 27.9 | 1.49 | 3.1 | 3.5 | 24.6 | 24.6 | 27.3 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:05:00 | 256.96 | 305.72 | 823393.26 | 798585.8 | 4.63 | 3896.73 | 531.37 | -115.314 | 13 | 184 | 25.5 | 54.7 | 25.9 | 54.5 | 0 | 0 | - | - | 28.3 | 49.1 | 0 | 0 | 0 | 0 | 28 | 28 | 27.8 | 1.49 | 3.6 | 3.6 | 0 | 27.4 | 27.5 | 27.9 | 1.49 | 3.1 | 3.5 | 24.6 | 24.6 | 27.3 | 1.51 | 1.51 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:10:00 | 257.36 | 311.92 | 823393.76 | 798591.76 | 4.69 | 3911.49 | 516.609 | 50.234 | 13 | 184 | 25.5 | 54.6 | 26 | 54.5 | 0 | 0 | - | - | 28.3 | 49.2 | 0 | 0 | 0 | 0 | 28.1 | 28 | 27.8 | 1.49 | 3.6 | 3.7 | 0 | 27.4 | 27.6 | 27.9 | 1.49 | 3.1 | 3.6 | 24.7 | 24.7 | 27.4 | 1.52 | 1.51 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:15:00 | 262.08 | 312.42 | 823398.38 | 798592.26 | 4.76 | 3904.11 | 523.989 | 18.421 | 13 | 184 | 25.7 | 54.5 | 26 | 54.3 | 0 | 0 | - | - | 28.4 | 49.1 | 0 | 0 | 0 | 0 | 28.1 | 28.1 | 27.9 | 1.49 | 3.6 | 3.7 | 0 | 27.4 | 27.6 | 28 | 1.49 | 3.1 | 3.6 | 24.7 | 24.7 | 27.6 | 1.52 | 1.52 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:20:00 | 270.04 | 312.42 | 823406.48 | 798592.26 | 4.82 | 3874.589 | 553.512 | 110.229 | 13 | 184 | 25.7 | 54.4 | 26.1 | 54.3 | 0 | 0 | - | - | 28.4 | 49.1 | 0 | 0 | 0 | 0 | 28.2 | 28.1 | 27.9 | 1.5 | 3.7 | 3.6 | 0 | 27.5 | 27.7 | 28.1 | 1.49 | 3.1 | 3.6 | 24.7 | 24.7 | 27.7 | 1.52 | 1.52 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:25:00 | 286.32 | 312.42 | 823422.86 | 798592.26 | 4.89 | 3867.209 | 560.892 | 245.093 | 14 | 184 | 25.8 | 54.3 | 26.2 | 54.2 | 0 | 0 | - | - | 28.5 | 49 | 0 | 0 | 0 | 0 | 28.2 | 28.1 | 27.9 | 1.5 | 3.7 | 3.6 | 0 | 27.5 | 27.7 | 28.1 | 1.49 | 3.2 | 3.5 | 24.7 | 24.7 | 27.6 | 1.52 | 1.52 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:30:00 | 302.8 | 312.42 | 823439.34 | 798592.26 | 4.96 | 3867.209 | 560.892 | 116.708 | 14 | 184 | 25.9 | 54.2 | 26.2 | 54.1 | 0 | 0 | - | - | 28.5 | 49 | 0 | 0 | 0 | 0 | 28.2 | 28.1 | 27.8 | 1.5 | 3.6 | 3.6 | 0 | 27.5 | 27.7 | 28.1 | 1.49 | 3.2 | 3.6 | 24.7 | 24.7 | 27.6 | 1.52 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:35:00 | 316.8 | 312.42 | 823453.26 | 798592.26 | 5.03 | 3830.308 | 597.792 | 221.715 | 15 | 184 | 26 | 54.1 | 26.3 | 54 | 0 | 0 | - | - | 28.6 | 48.9 | 0 | 0 | 0 | 0 | 28.2 | 28.1 | 27.9 | 1.5 | 3.7 | 3.7 | 0 | 27.5 | 27.7 | 28.2 | 1.49 | 3.2 | 3.6 | 24.7 | 24.7 | 27.8 | 1.52 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:40:00 | 337.7 | 312.42 | 823474.44 | 798592.26 | 5.1 | 3822.927 | 605.172 | 272.07 | 15 | 184 | 26 | 54 | 26.3 | 54 | 0 | 0 | - | - | 28.7 | 48.8 | 0 | 0 | 0 | 0 | 28.3 | 28.2 | 28.1 | 1.5 | 3.7 | 3.7 | 0 | 27.7 | 27.8 | 28.3 | 1.5 | 3.3 | 3.7 | 24.7 | 24.7 | 28.1 | 1.52 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:45:00 | 371.66 | 312.42 | 823508.86 | 798592.26 | 5.19 | 3778.644 | 649.452 | 425.574 | 16 | 184 | 26.1 | 53.9 | 26.4 | 53.9 | 0 | 0 | - | - | 28.8 | 48.8 | 0 | 0 | 0 | 0 | 28.5 | 28.4 | 28.3 | 1.5 | 3.8 | 3.9 | 0 | 27.7 | 27.9 | 28.4 | 1.5 | 3.3 | 3.7 | 24.7 | 24.7 | 28.5 | 1.52 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:50:00 | 408.52 | 312.42 | 823545.02 | 798592.26 | 5.27 | 3741.744 | 686.352 | 363.853 | 17 | 184 | 26.3 | 53.8 | 26.5 | 53.8 | 0 | 0 | - | - | 28.9 | 48.8 | 0 | 0 | 0 | 0 | 28.6 | 28.4 | 28.4 | 1.5 | 3.9 | 4 | 0 | 27.9 | 28 | 28.6 | 1.5 | 3.5 | 3.8 | 24.7 | 24.7 | 29 | 1.53 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 06:55:00 | 438.46 | 312.42 | 823575.08 | 798592.26 | 5.35 | 3712.224 | 715.872 | 248.929 | 17 | 184 | 26.4 | 53.5 | 26.7 | 53.5 | 0 | 0 | - | - | 29.1 | 48.7 | 0 | 0 | 0 | 0 | 28.8 | 28.5 | 28.6 | 1.5 | 3.9 | 4.1 | 0 | 28 | 28.1 | 28.7 | 1.5 | 3.5 | 3.9 | 24.8 | 24.7 | 29.5 | 1.53 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:00:00 | 446.84 | 312.84 | 823583.14 | 798592.9 | 5.42 | 3704.844 | 723.252 | -72.106 | 18 | 184 | 26.7 | 53.1 | 26.9 | 53.1 | 0 | 0 | - | - | 29.3 | 48.5 | 0 | 0 | 0 | 0 | 28.9 | 28.6 | 28.8 | 1.51 | 4 | 4.2 | 0 | 28.2 | 28.2 | 28.9 | 1.5 | 3.6 | 4 | 24.8 | 24.7 | 30.7 | 1.53 | 1.52 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:05:00 | 446.84 | 335.48 | 823583.14 | 798616.48 | 5.5 | 3734.364 | 693.732 | -438.655 | 17 | 184 | 27 | 52.7 | 27.1 | 52.9 | 0 | 0 | - | - | 29.5 | 48.3 | 0 | 0 | 0 | 0 | 29.1 | 28.7 | 29 | 1.51 | 4.1 | 4.4 | 0 | 28.3 | 28.4 | 29.2 | 1.5 | 3.7 | 4.1 | 24.8 | 24.8 | 31.9 | 1.53 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:10:00 | 446.84 | 393.86 | 823583.14 | 798674.62 | 5.59 | 3756.504 | 671.592 | -945.649 | 16 | 184 | 27.2 | 52.4 | 27.3 | 52.6 | 0 | 0 | - | - | 29.8 | 48.1 | 0 | 0 | 0 | 0 | 29.2 | 28.8 | 29.1 | 1.51 | 4.1 | 4.4 | 0 | 28.4 | 28.5 | 29.3 | 1.5 | 3.8 | 4.2 | 24.9 | 24.8 | 31.2 | 1.53 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:15:00 | 446.84 | 458.02 | 823583.14 | 798738.88 | 5.68 | 3778.644 | 649.452 | -735.368 | 16 | 184 | 27.4 | 52.1 | 27.4 | 52.5 | 0 | 0 | - | - | 30 | 47.9 | 0 | 0 | 0 | 0 | 29.3 | 28.9 | 29.2 | 1.51 | 4.1 | 4.5 | 0 | 28.5 | 28.6 | 29.5 | 1.51 | 3.8 | 4.3 | 25 | 25 | 30.7 | 1.53 | 1.53 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:20:00 | 448.6 | 480.58 | 823585.02 | 798760.42 | 5.76 | 3800.784 | 627.312 | 2.252 | 15 | 184 | 27.5 | 51.9 | 27.5 | 52.3 | 0 | 0 | - | - | 30.1 | 47.8 | 0 | 0 | 0 | 0 | 29.5 | 29 | 29.4 | 1.51 | 4.1 | 4.5 | 0 | 28.7 | 28.7 | 29.7 | 1.51 | 3.8 | 4.4 | 25.1 | 25.1 | 32.3 | 1.54 | 1.54 | 1.51 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:25:00 | 448.84 | 493.06 | 823585.14 | 798773.4 | 5.84 | 3815.545 | 612.552 | -560.165 | 15 | 184 | 27.7 | 51.7 | 27.7 | 52.2 | 0 | 0 | - | - | 30.3 | 47.7 | 0 | 0 | 0 | 0 | 29.6 | 29.1 | 29.5 | 1.52 | 4.1 | 4.6 | 0 | 28.8 | 28.7 | 29.8 | 1.51 | 3.8 | 4.4 | 25.2 | 25.2 | 31.4 | 1.54 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:30:00 | 448.84 | 527.68 | 823585.14 | 798807.9 | 5.93 | 3859.829 | 568.272 | -128.26 | 13 | 184 | 27.8 | 51.7 | 27.8 | 52.1 | 0 | 0 | - | - | 30.4 | 47.6 | 0 | 0 | 0 | 0 | 29.6 | 29.1 | 29.5 | 1.52 | 4.1 | 4.6 | 0 | 28.8 | 28.8 | 29.9 | 1.51 | 3.8 | 4.4 | 25.3 | 25.3 | 31.6 | 1.54 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:35:00 | 459.1 | 529.6 | 823595.9 | 798809.44 | 6 | 3859.829 | 568.272 | 239.43 | 14 | 184 | 27.9 | 51.5 | 27.9 | 52 | 0 | 0 | - | - | 30.5 | 47.5 | 0 | 0 | 0 | 0 | 29.7 | 29.2 | 29.7 | 1.52 | 4.1 | 4.6 | 0 | 28.9 | 28.9 | 30.1 | 1.52 | 3.8 | 4.4 | 25.4 | 25.3 | 33 | 1.55 | 1.55 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:40:00 | 474.98 | 529.6 | 823611.32 | 798809.44 | 6.08 | 3859.829 | 568.272 | 82.706 | 14 | 184 | 28.1 | 51.3 | 28 | 51.9 | 0 | 0 | - | - | 30.6 | 47.4 | 0 | 0 | 0 | 0 | 29.8 | 29.4 | 29.9 | 1.52 | 4.3 | 4.7 | 0 | 29.1 | 29 | 30.5 | 1.52 | 3.9 | 4.5 | 25.4 | 25.3 | 34.6 | 1.55 | 1.55 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:45:00 | 479.84 | 529.6 | 823616.32 | 798809.44 | 6.15 | 3859.829 | 568.272 | 265.308 | 14 | 184 | 28.3 | 51.1 | 28.1 | 51.8 | 0 | 0 | - | - | 30.7 | 47.3 | 0 | 0 | 0 | 0 | 30.1 | 29.7 | 30.2 | 1.53 | 4.5 | 4.8 | 0 | 29.3 | 29.3 | 30.9 | 1.52 | 4.1 | 4.7 | 25.4 | 25.4 | 35.5 | 1.55 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:50:00 | 507.26 | 529.6 | 823643.68 | 798809.44 | 6.23 | 3815.546 | 612.552 | 277.104 | 15 | 184 | 28.5 | 50.9 | 28.3 | 51.6 | 0 | 0 | - | - | 30.9 | 47.2 | 0 | 0 | 0 | 0 | 30.3 | 30 | 30.7 | 1.53 | 4.7 | 5 | 0 | 29.6 | 29.5 | 31.6 | 1.53 | 4.2 | 4.8 | 25.4 | 25.4 | 36.6 | 1.56 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 07:55:00 | 546.42 | 529.6 | 823683.58 | 798809.44 | 6.32 | 3771.264 | 656.832 | 312.287 | 16 | 184 | 28.7 | 50.6 | 28.4 | 51.4 | 0 | 0 | - | - | 31.1 | 47 | 0 | 0 | 0 | 0 | 30.6 | 30.3 | 31 | 1.53 | 5.1 | 5.3 | 0 | 29.8 | 29.8 | 32.1 | 1.53 | 4.5 | 5 | 25.4 | 25.4 | 37 | 1.56 | 1.55 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:00:00 | 559.58 | 534.72 | 823695.88 | 798814.56 | 6.39 | 3771.264 | 656.832 | -349.36 | 16 | 184 | 28.9 | 50.3 | 28.6 | 51.2 | 0 | 0 | - | - | 31.4 | 46.9 | 0 | 0 | 0 | 0 | 30.9 | 30.6 | 31.5 | 1.54 | 5.3 | 5.5 | 0 | 30.1 | 30 | 32.7 | 1.53 | 4.7 | 5.3 | 25.4 | 25.4 | 38.1 | 1.56 | 1.56 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:05:00 | 559.58 | 560.16 | 823695.88 | 798840.1 | 6.48 | 3800.785 | 627.312 | -230.222 | 15 | 184 | 29.2 | 50 | 28.9 | 50.9 | 0 | 0 | - | - | 31.8 | 46.5 | 0 | 0 | 0 | 0 | 31.2 | 30.8 | 31.7 | 1.54 | 5.4 | 5.8 | 0 | 30.3 | 30.2 | 33.1 | 1.53 | 4.9 | 5.5 | 25.5 | 25.5 | 37.7 | 1.56 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:10:00 | 559.58 | 577.16 | 823695.88 | 798857 | 6.55 | 3815.546 | 612.552 | -6.873 | 15 | 184 | 29.5 | 49.6 | 29.2 | 50.6 | 0 | 0 | - | - | 32.2 | 46.1 | 0 | 0 | 0 | 0 | 31.5 | 31 | 32.1 | 1.54 | 5.6 | 5.9 | 0 | 30.6 | 30.4 | 33.5 | 1.53 | 5 | 5.6 | 25.5 | 25.5 | 38.1 | 1.56 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:15:00 | 559.58 | 578.6 | 823695.88 | 798858.44 | 6.62 | 3815.546 | 612.552 | -1.731 | 15 | 184 | 29.8 | 49.3 | 29.3 | 50.4 | 0 | 0 | - | - | 32.7 | 45.6 | 0 | 0 | 0 | 0 | 31.7 | 31.1 | 32.2 | 1.54 | 5.7 | 6.2 | 0 | 30.8 | 30.6 | 33.8 | 1.54 | 5.1 | 5.8 | 25.6 | 25.6 | 37.4 | 1.56 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:20:00 | 559.58 | 585.96 | 823695.88 | 798866.12 | 6.69 | 3830.308 | 597.792 | -241.772 | 15 | 184 | 30.1 | 48.9 | 29.5 | 50.2 | 0 | 0 | - | - | 33.2 | 45.1 | 0 | 0 | 0 | 0 | 31.9 | 31.3 | 32.5 | 1.54 | 5.8 | 6.4 | 0 | 31 | 30.7 | 34 | 1.54 | 5.2 | 6 | 25.6 | 25.6 | 37.9 | 1.56 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:25:00 | 559.58 | 606.24 | 823695.88 | 798886.12 | 6.77 | 3859.829 | 568.272 | -106.55 | 14 | 184 | 30.3 | 48.6 | 29.8 | 49.8 | 0 | 0 | - | - | 33.6 | 44.7 | 0 | 0 | 0 | 0 | 32.1 | 31.4 | 32.7 | 1.54 | 5.8 | 6.5 | 0 | 31.2 | 30.9 | 34.2 | 1.54 | 5.3 | 6.1 | 25.6 | 25.6 | 37.2 | 1.57 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:30:00 | 561.36 | 611.64 | 823697.66 | 798891.78 | 6.85 | 3859.829 | 568.272 | -212.529 | 14 | 184 | 30.6 | 48.3 | 30 | 49.6 | 0 | 0 | - | - | 33.9 | 44.3 | 0 | 0 | 0 | 0 | 32.2 | 31.4 | 32.7 | 1.54 | 5.9 | 6.6 | 0 | 31.3 | 30.9 | 34.3 | 1.54 | 5.4 | 6.2 | 25.7 | 25.7 | 36.6 | 1.57 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:35:00 | 561.36 | 639.82 | 823697.66 | 798920.12 | 6.93 | 3881.97 | 546.132 | -226.105 | 13 | 184 | 30.7 | 48.1 | 30.1 | 49.5 | 0 | 0 | - | - | 34.1 | 44 | 0 | 0 | 0 | 0 | 32.2 | 31.4 | 32.7 | 1.55 | 5.8 | 6.6 | 0 | 31.3 | 30.9 | 34.3 | 1.54 | 5.3 | 6.2 | 25.7 | 25.7 | 35.4 | 1.57 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:40:00 | 561.36 | 651.28 | 823697.66 | 798931.3 | 7 | 3904.11 | 523.991 | -15.058 | 13 | 184 | 30.9 | 47.9 | 30.3 | 49.3 | 0 | 0 | - | - | 34.3 | 43.9 | 0 | 0 | 0 | 0 | 32.3 | 31.4 | 32.6 | 1.55 | 5.8 | 6.6 | 0 | 31.4 | 30.9 | 34.1 | 1.54 | 5.3 | 6.3 | 25.8 | 25.8 | 34.8 | 1.57 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:45:00 | 566.66 | 652.02 | 823703.08 | 798931.86 | 7.07 | 3904.11 | 523.991 | 255.868 | 13 | 184 | 31.1 | 47.8 | 30.5 | 49.2 | 0 | 0 | - | - | 34.4 | 43.8 | 0 | 0 | 0 | 0 | 32.3 | 31.4 | 32.6 | 1.55 | 5.8 | 6.7 | 0 | 31.5 | 31 | 33.9 | 1.54 | 5.4 | 6.3 | 25.8 | 25.8 | 34.8 | 1.57 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:50:00 | 592.16 | 652.02 | 823729.06 | 798931.86 | 7.15 | 3867.21 | 560.892 | 394.76 | 14 | 184 | 31.2 | 47.7 | 30.6 | 49.1 | 0 | 0 | - | - | 34.6 | 43.7 | 0 | 0 | 0 | 0 | 32.5 | 31.5 | 32.7 | 1.55 | 5.8 | 6.8 | 0 | 31.7 | 31.2 | 33.9 | 1.55 | 5.5 | 6.5 | 25.8 | 25.8 | 35.9 | 1.57 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 08:55:00 | 635.4 | 652.02 | 823772.78 | 798931.86 | 7.24 | 3822.926 | 605.172 | 599.948 | 15 | 184 | 31.4 | 47.6 | 30.7 | 49.1 | 0 | 0 | - | - | 34.7 | 43.6 | 0 | 0 | 0 | 0 | 32.7 | 31.6 | 33 | 1.55 | 5.9 | 7 | 0 | 31.9 | 31.3 | 34 | 1.55 | 5.6 | 6.7 | 25.9 | 25.8 | 36.5 | 1.57 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:00:00 | 685.16 | 652.02 | 823822.3 | 798931.86 | 7.32 | 3778.644 | 649.452 | 341.531 | 16 | 184 | 31.6 | 47.4 | 30.8 | 48.8 | 0 | 0 | - | - | 35 | 43.3 | 0 | 0 | 0 | 0 | 32.9 | 31.8 | 33.2 | 1.55 | 6.1 | 7.1 | 0 | 32.1 | 31.5 | 34.2 | 1.55 | 5.7 | 6.8 | 25.8 | 25.8 | 37.2 | 1.57 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:05:00 | 703.24 | 652.02 | 823839.6 | 798931.86 | 7.4 | 3771.264 | 656.832 | 26.873 | 16 | 184 | 31.9 | 47 | 31.1 | 48.6 | 0 | 0 | - | - | 35.3 | 43.1 | 0 | 0 | 0 | 0 | 33 | 31.9 | 33.3 | 1.55 | 6.1 | 7.2 | 0 | 32.2 | 31.5 | 34.5 | 1.55 | 5.8 | 6.9 | 25.9 | 25.8 | 37.4 | 1.58 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:10:00 | 704.74 | 656.64 | 823841.12 | 798936.48 | 7.47 | 3771.264 | 656.832 | 144.191 | 16 | 184 | 32.4 | 46.6 | 31.7 | 47.9 | 0 | 0 | - | - | 35.6 | 42.8 | 0 | 0 | 0 | 0 | 33.1 | 32 | 33.4 | 1.55 | 6.2 | 7.3 | 0 | 32.2 | 31.6 | 34.6 | 1.55 | 5.9 | 6.9 | 25.9 | 25.9 | 36.4 | 1.58 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:15:00 | 733.84 | 656.64 | 823870.44 | 798936.48 | 7.56 | 3734.364 | 693.732 | 653.768 | 17 | 184 | 32.8 | 46.1 | 32.1 | 47.5 | 0 | 0 | - | - | 35.8 | 42.6 | 0 | 0 | 0 | 0 | 33.2 | 32.1 | 33.5 | 1.56 | 6.3 | 7.3 | 0 | 32.4 | 31.7 | 34.6 | 1.55 | 5.9 | 7 | 25.9 | 25.9 | 37 | 1.58 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:20:00 | 789.84 | 656.64 | 823927.12 | 798936.48 | 7.65 | 3690.084 | 738.012 | 665.67 | 18 | 184 | 32.7 | 46.1 | 31.9 | 47.6 | 0 | 0 | - | - | 36.1 | 42.4 | 0 | 0 | 0 | 0 | 33.4 | 32.1 | 33.6 | 1.56 | 6.3 | 7.4 | 0 | 32.5 | 31.8 | 34.7 | 1.55 | 5.9 | 7.2 | 25.9 | 25.9 | 36.6 | 1.58 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:25:00 | 848.32 | 656.64 | 823985.9 | 798936.48 | 7.75 | 3616.282 | 811.818 | 506.178 | 20 | 184 | 32.7 | 46.2 | 31.8 | 47.8 | 0 | 0 | - | - | 36.2 | 42.2 | 0 | 0 | 0 | 0 | 33.4 | 32.2 | 33.6 | 1.56 | 6.3 | 7.4 | 0 | 32.5 | 31.8 | 34.8 | 1.55 | 5.9 | 7.1 | 26 | 25.9 | 36.4 | 1.58 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:30:00 | 883.28 | 656.64 | 824019.84 | 798936.48 | 7.84 | 3586.758 | 841.338 | 233.015 | 20 | 184 | 32.9 | 46 | 32 | 47.7 | 0 | 0 | - | - | 36.4 | 42.1 | 0 | 0 | 0 | 0 | 33.5 | 32.3 | 33.8 | 1.56 | 6.4 | 7.6 | 0 | 32.7 | 31.9 | 35 | 1.55 | 6 | 7.2 | 26 | 26 | 36.7 | 1.58 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:35:00 | 896.86 | 656.94 | 824033.18 | 798936.78 | 7.92 | 3571.998 | 856.098 | 14.029 | 21 | 184 | 33.1 | 45.8 | 32.2 | 47.5 | 0 | 0 | - | - | 36.5 | 42.1 | 0 | 0 | 0 | 0 | 33.7 | 32.4 | 33.9 | 1.56 | 6.5 | 7.7 | 0 | 32.8 | 32 | 35.1 | 1.56 | 6.1 | 7.3 | 26.1 | 26 | 37.1 | 1.58 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:40:00 | 897.02 | 670.46 | 824033.32 | 798950.46 | 8 | 3586.758 | 841.338 | -81.396 | 20 | 184 | 33.4 | 45.6 | 32.4 | 47.4 | 0 | 0 | - | - | 36.7 | 41.9 | 0 | 0 | 0 | 0 | 33.8 | 32.6 | 34.1 | 1.56 | 6.6 | 7.8 | 0 | 32.9 | 32.1 | 35.3 | 1.56 | 6.2 | 7.4 | 26.1 | 26.1 | 37.1 | 1.59 | 1.58 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:45:00 | 897.38 | 678.54 | 824033.68 | 798958.46 | 8.08 | 3594.139 | 833.958 | -73.083 | 20 | 184 | 33.5 | 45.4 | 32.5 | 47.2 | 0 | 0 | - | - | 36.8 | 41.7 | 0 | 0 | 0 | 0 | 33.8 | 32.6 | 34.1 | 1.56 | 6.6 | 7.8 | 0 | 32.9 | 32.1 | 35.3 | 1.56 | 6.1 | 7.4 | 26.2 | 26.1 | 36.4 | 1.59 | 1.58 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:50:00 | 897.38 | 695.92 | 824033.68 | 798976.26 | 8.15 | 3608.901 | 819.198 | -136.399 | 20 | 184 | 33.7 | 45.3 | 32.7 | 47.1 | 0 | 0 | - | - | 36.9 | 41.7 | 0 | 0 | 0 | 0 | 34 | 32.6 | 34.2 | 1.56 | 6.6 | 7.9 | 0 | 33.1 | 32.2 | 35.4 | 1.56 | 6.2 | 7.6 | 26.2 | 26.2 | 35.7 | 1.59 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 09:55:00 | 915.46 | 697.76 | 824052.34 | 798977.6 | 8.24 | 3594.139 | 833.958 | 559.691 | 20 | 184 | 33.8 | 45.2 | 32.8 | 47 | 0 | 0 | - | - | 36.9 | 41.7 | 0 | 0 | 0 | 0 | 33.9 | 32.6 | 34.2 | 1.57 | 6.6 | 7.8 | 0 | 33.1 | 32.2 | 35.4 | 1.56 | 6.1 | 7.5 | 26.2 | 26.2 | 35.3 | 1.59 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:00:00 | 943.68 | 697.76 | 824079.98 | 798977.6 | 8.32 | 3571.998 | 856.098 | 6.24 | 21 | 184 | 33.8 | 45.2 | 32.8 | 47 | 0 | 0 | - | - | 36.8 | 41.8 | 0 | 0 | 0 | 0 | 33.9 | 32.7 | 34.1 | 1.57 | 6.6 | 7.8 | 0 | 33.1 | 32.2 | 35.2 | 1.56 | 6.1 | 7.4 | 26.2 | 26.2 | 34.9 | 1.59 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:05:00 | 954.3 | 697.76 | 824091.2 | 798977.6 | 8.4 | 3549.859 | 878.238 | 386.466 | 21 | 184 | 33.8 | 45.2 | 32.8 | 47 | 0 | 0 | - | - | 36.8 | 41.9 | 0 | 0 | 0 | 0 | 33.9 | 32.7 | 34.1 | 1.57 | 6.6 | 7.9 | 0 | 33.1 | 32.2 | 35.2 | 1.56 | 6.1 | 7.5 | 26.3 | 26.2 | 34.9 | 1.59 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:10:00 | 985.18 | 697.76 | 824121.82 | 798977.6 | 8.48 | 3527.718 | 900.378 | 306.684 | 22 | 184 | 33.8 | 45.2 | 32.9 | 47 | 0 | 0 | - | - | 36.7 | 41.9 | 0 | 0 | 0 | 0 | 34 | 32.8 | 34.1 | 1.57 | 6.6 | 7.9 | 0 | 33.1 | 32.2 | 35.1 | 1.56 | 6.1 | 7.5 | 26.3 | 26.2 | 34.9 | 1.59 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:15:00 | 1018.6 | 697.76 | 824155.42 | 798977.6 | 8.57 | 3490.818 | 937.278 | 522.035 | 23 | 184 | 33.9 | 45.2 | 32.9 | 47 | 0 | 0 | - | - | 36.7 | 42 | 0 | 0 | -39.6 | -34.5 | 34 | 32.8 | 34 | 1.57 | 6.7 | 7.9 | -49.3 | 33.2 | 32.3 | 35 | 1.56 | 6.1 | 7.6 | 26.3 | 26.3 | 35.1 | 1.59 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:20:00 | 1066.74 | 697.76 | 824203.86 | 798977.6 | 8.72 | 3446.538 | 981.558 | 523.968 | 24 | 184 | 33.9 | 45.2 | 32.9 | 47.1 | 0 | 0 | - | - | 36.6 | 42 | 0 | 0 | 0 | 0 | 34.1 | 32.7 | 34.1 | 1.56 | 6.6 | 8.2 | 0 | 33.4 | 32.4 | 34.9 | 1.56 | 6.3 | 7.9 | 26.3 | 26.3 | 34.9 | 1.58 | 1.59 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:25:00 | 1102.44 | 697.76 | 824238.94 | 798977.6 | 8.81 | 3417.018 | 1011.078 | 370.653 | 25 | 184 | 34 | 45.2 | 33 | 47 | 0 | 0 | - | - | 36.7 | 42.1 | 0 | 0 | 0 | 0 | 34.2 | 32.7 | 34.3 | 1.56 | 6.6 | 8.2 | 0 | 33.5 | 32.4 | 35 | 1.56 | 6.3 | 7.9 | 26.3 | 26.3 | 35.5 | 1.58 | 1.59 | 1.56 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:30:00 | 1118.48 | 697.76 | 824254.82 | 798977.6 | 8.89 | 3380.118 | 1047.982 | 25.56 | 25 | 184 | 34.1 | 45.1 | 33.1 | 47 | 0 | 0 | - | - | 36.8 | 42 | 0 | 0 | 0 | 0 | 34.3 | 32.9 | 34.4 | 1.57 | 6.7 | 8.2 | 0 | 33.6 | 32.5 | 35.1 | 1.56 | 6.3 | 8 | 26.4 | 26.4 | 35.8 | 1.59 | 1.59 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:35:00 | 1129 | 697.76 | 824265.36 | 798977.6 | 8.97 | 3372.738 | 1055.363 | 79.774 | 25 | 184 | 34.2 | 45 | 33.2 | 46.8 | 0 | 0 | - | - | 36.9 | 41.9 | 0 | 0 | 0 | 0 | 34.6 | 33.1 | 34.7 | 1.57 | 6.8 | 8.4 | 0 | 33.8 | 32.6 | 35.3 | 1.57 | 6.4 | 8.1 | 26.4 | 26.4 | 36.6 | 1.59 | 1.59 | 1.57 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:40:00 | 1142.74 | 697.76 | 824279.22 | 798977.6 | 9.05 | 3372.738 | 1055.363 | 114.534 | 26 | 184 | 34.4 | 44.8 | 33.4 | 46.6 | 0 | 0 | - | - | 37 | 41.8 | 0 | 0 | 0 | 0 | 34.7 | 33.3 | 34.8 | 1.57 | 7 | 8.4 | 0 | 33.9 | 32.8 | 35.5 | 1.57 | 6.5 | 8.1 | 26.5 | 26.4 | 36.1 | 1.6 | 1.6 | 1.57 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:45:00 | 1145.08 | 704.74 | 824281.38 | 798984.96 | 9.14 | 3372.738 | 1055.363 | -180.535 | 26 | 184 | 34.5 | 44.7 | 33.5 | 46.5 | 0 | 0 | - | - | 37.1 | 41.7 | 0 | 0 | 0 | 0 | 34.8 | 33.4 | 34.9 | 1.57 | 7 | 8.5 | 0 | 34 | 32.8 | 35.6 | 1.57 | 6.5 | 8.2 | 26.5 | 26.5 | 35.6 | 1.6 | 1.6 | 1.57 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:50:00 | 1157.24 | 707.28 | 824293.76 | 798987.12 | 9.22 | 3357.977 | 1070.124 | 344.992 | 26 | 184 | 34.6 | 44.6 | 33.5 | 46.6 | 0 | 0 | - | - | 37.2 | 41.6 | 0 | 0 | 0 | 0 | 34.9 | 33.4 | 35 | 1.58 | 7.1 | 8.6 | 0 | 34.1 | 32.9 | 35.7 | 1.57 | 6.6 | 8.3 | 26.5 | 26.5 | 35.4 | 1.6 | 1.6 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 10:55:00 | 1192.86 | 707.28 | 824329.58 | 798987.12 | 9.31 | 3306.313 | 1121.784 | 271.625 | 27 | 184 | 34.6 | 44.6 | 33.6 | 46.5 | 0 | 0 | - | - | 37.2 | 41.5 | 0 | 0 | 0 | 0 | 34.9 | 33.5 | 34.9 | 1.58 | 7.1 | 8.5 | 0 | 34.2 | 33 | 35.6 | 1.57 | 6.6 | 8.3 | 26.6 | 26.5 | 35.2 | 1.6 | 1.6 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:00:00 | 1217.84 | 707.28 | 824355.1 | 798987.12 | 9.4 | 3284.172 | 1143.924 | 693.541 | 27 | 184 | 34.7 | 44.6 | 33.7 | 46.5 | 0 | 0 | - | - | 37.3 | 41.6 | 0 | 0 | 0 | 0 | 35 | 33.5 | 35 | 1.58 | 7.1 | 8.6 | 0 | 34.2 | 33 | 35.6 | 1.58 | 6.6 | 8.4 | 26.6 | 26.6 | 35.2 | 1.6 | 1.6 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:05:00 | 1282.62 | 707.28 | 824421.14 | 798987.12 | 9.5 | 3210.372 | 1217.724 | 936.109 | 29 | 184 | 34.7 | 44.7 | 33.6 | 46.6 | 0 | 0 | - | - | 37.3 | 41.6 | 0 | 0 | 0 | 0 | 35 | 33.6 | 34.9 | 1.58 | 7.1 | 8.5 | 0 | 34.2 | 33.1 | 35.6 | 1.58 | 6.6 | 8.3 | 26.6 | 26.6 | 35.2 | 1.61 | 1.6 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:10:00 | 1345.04 | 707.3 | 824481.34 | 798987.14 | 9.6 | 3151.332 | 1276.769 | -14.851 | 30 | 184 | 34.7 | 44.7 | 33.6 | 46.7 | 0 | 0 | - | - | 37.3 | 41.6 | 0 | 0 | 0 | 0 | 35 | 33.6 | 35 | 1.58 | 7.1 | 8.5 | 0 | 34.3 | 33.1 | 35.7 | 1.58 | 6.6 | 8.3 | 26.6 | 26.6 | 35.4 | 1.6 | 1.6 | 1.58 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:15:00 | 1356.14 | 707.64 | 824492.8 | 798987.48 | 9.69 | 3136.572 | 1291.53 | 223.61 | 30 | 184 | 34.7 | 44.7 | 33.6 | 46.7 | 0 | 0 | - | - | 37.3 | 41.6 | 0 | 0 | 0 | 0 | 35 | 33.6 | 35 | 1.58 | 7.1 | 8.5 | 0 | 34.3 | 33.1 | 35.7 | 1.58 | 6.6 | 8.3 | 26.7 | 26.7 | 35.4 | 1.61 | 1.61 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:20:00 | 1376.02 | 707.64 | 824512.36 | 798987.48 | 9.78 | 3121.812 | 1306.29 | -20.622 | 31 | 184 | 34.8 | 44.6 | 33.8 | 46.5 | 0 | 0 | - | - | 37.4 | 41.5 | 0 | 0 | 0 | 0 | 35.1 | 33.7 | 35.1 | 1.59 | 7.1 | 8.5 | 0 | 34.4 | 33.2 | 35.7 | 1.58 | 6.7 | 8.3 | 26.7 | 26.7 | 35.6 | 1.61 | 1.61 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:25:00 | 1380.78 | 708.9 | 824517.3 | 798988.74 | 9.87 | 3114.432 | 1313.67 | 201.549 | 31 | 184 | 34.9 | 44.5 | 33.8 | 46.5 | 0 | 0 | - | - | 37.5 | 41.5 | 0 | 0 | 0 | 0 | 35.2 | 33.8 | 35.3 | 1.59 | 7.2 | 8.6 | 0 | 34.5 | 33.3 | 35.8 | 1.59 | 6.7 | 8.4 | 26.8 | 26.8 | 35.7 | 1.61 | 1.61 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:30:00 | 1419.96 | 708.9 | 824557.2 | 798988.74 | 9.97 | 3070.148 | 1357.95 | 892.573 | 32 | 184 | 35.1 | 44.5 | 34 | 46.3 | 0 | 0 | - | - | 37.6 | 41.4 | 0 | 0 | 0 | 0 | 35.4 | 33.9 | 35.4 | 1.59 | 7.2 | 8.7 | 0 | 34.6 | 33.4 | 35.9 | 1.59 | 6.8 | 8.5 | 26.8 | 26.8 | 35.9 | 1.61 | 1.61 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:35:00 | 1501.14 | 708.9 | 824639.38 | 798988.74 | 10.07 | 2988.966 | 1439.13 | 950.757 | 34 | 184 | 35.2 | 44.3 | 34.1 | 46.2 | 0 | 0 | - | - | 37.7 | 41.3 | 0 | 0 | 20 | 17.5 | 35.5 | 34 | 35.5 | 1.59 | 7.3 | 8.9 | 20.9 | 34.7 | 33.4 | 36.1 | 1.59 | 6.7 | 8.6 | 26.9 | 26.9 | 35.7 | 1.61 | 1.62 | 1.59 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:40:00 | 1594.56 | 708.9 | 824733.02 | 798988.74 | 10.65 | 2893.026 | 1535.074 | 1386.914 | 36 | 184 | 35.5 | 44 | 34.3 | 46 | 0 | 0 | - | - | 37.8 | 41.2 | 231 | 186 | 65.9 | 65.6 | 68.7 | 25.7 | 45.2 | 2.65 | 11.5 | 22 | 65.6 | 70.6 | 25.7 | 47.8 | 2.86 | 11.4 | 21.1 | 23.1 | 25.2 | 35.1 | 2.71 | 1.12 | 2.9 | 1.12 | 231 | 186 | 2826 | 2817
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:45:00 | 1710.26 | 708.9 | 824848.76 | 798988.74 | 11.56 | 2760.18 | 1667.916 | 1436.718 | 39 | 184 | 35.7 | 43.6 | 34.5 | 45.7 | 0 | 0 | - | - | 37.9 | 41.1 | 230 | 186 | 65.7 | 65.3 | 71.5 | 23.7 | 44.5 | 2.6 | 10.6 | 25.6 | 65.4 | 75.2 | 23.8 | 47.9 | 2.83 | 10.1 | 26.2 | 21.6 | 23.4 | 35.1 | 2.65 | 1.08 | 2.86 | 1.1 | 230 | 186 | 2649 | 2649
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:50:00 | 1841.72 | 708.9 | 824978.78 | 798988.74 | 12.35 | 2627.34 | 1800.76 | 1458.179 | 42 | 184 | 36.1 | 43.2 | 34.7 | 45.4 | 0 | 0 | - | - | 38 | 41 | 230 | 186 | 63 | 62.9 | 70.6 | 23.4 | 44.1 | 2.55 | 9.7 | 25.4 | 62.8 | 74.8 | 23.6 | 47.3 | 2.78 | 9.9 | 26.6 | 21.6 | 23.3 | 35.9 | 2.61 | 1.11 | 2.81 | 1.11 | 230 | 186 | 2313 | 2313
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 11:55:00 | 1959.32 | 708.9 | 825097.92 | 798988.74 | 13.1 | 2516.635 | 1911.462 | 991.555 | 45 | 184 | 36.3 | 42.8 | 34.8 | 45.3 | 0 | 0 | - | - | 38.1 | 40.9 | 230 | 186 | 61.5 | 61.6 | 69.8 | 23.7 | 43.4 | 2.53 | 10 | 25 | 61.7 | 74.5 | 23.8 | 46.9 | 2.76 | 10.1 | 26.5 | 21.8 | 23.6 | 35.9 | 2.58 | 1.1 | 2.79 | 1.11 | 230 | 186 | 2310 | 2310
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:00:00 | 2013.36 | 708.9 | 825150.36 | 798988.74 | 13.84 | 2457.594 | 1970.502 | 436.27 | 46 | 184 | 36.5 | 42.6 | 34.9 | 45.1 | 0 | 0 | - | - | 38.2 | 40.9 | 230 | 186 | 61.5 | 61.5 | 69.6 | 23.8 | 43.5 | 2.54 | 10 | 24.8 | 61.2 | 74.4 | 23.9 | 46.9 | 2.76 | 10.1 | 26.4 | 21.9 | 23.7 | 36 | 2.59 | 1.1 | 2.79 | 1.11 | 230 | 186 | 2310 | 2310
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:05:00 | 2038.52 | 708.9 | 825175.12 | 798988.74 | 14.57 | 2435.454 | 1992.642 | 189.519 | 47 | 184 | 36.7 | 42.5 | 35 | 44.9 | 0 | 0 | - | - | 38.3 | 40.8 | 230 | 186 | 62 | 62.2 | 69.8 | 23.8 | 43.4 | 2.51 | 10.1 | 25.4 | 62.3 | 74.6 | 24 | 47.1 | 2.76 | 10.1 | 26.6 | 21.9 | 23.7 | 36.4 | 2.56 | 1.1 | 2.8 | 1.11 | 230 | 186 | 2310 | 2310
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:10:00 | 2043.84 | 710.3 | 825180.14 | 798990.48 | 15.28 | 2435.454 | 1992.642 | -154.071 | 47 | 184 | 36.7 | 42.3 | 35 | 44.8 | 0 | 0 | - | - | 38.3 | 40.7 | 230 | 186 | 60.4 | 60.5 | 68.8 | 23.7 | 43.1 | 2.49 | 10 | 24.5 | 59.9 | 73.5 | 23.8 | 46.3 | 2.73 | 10 | 26 | 21.7 | 23.6 | 34.4 | 2.55 | 1.1 | 2.76 | 1.11 | 230 | 186 | 2310 | 2310
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:15:00 | 2043.84 | 721.62 | 825180.14 | 799001.5 | 15.98 | 2435.454 | 1992.642 | -83.024 | 46 | 184 | 36.7 | 42.3 | 35 | 44.9 | 0 | 0 | - | - | 38.4 | 40.7 | 230 | 186 | 61.3 | 61.2 | 69 | 23.6 | 43.5 | 2.52 | 9.9 | 24.4 | 60.9 | 73.6 | 23.7 | 46.7 | 2.74 | 10 | 26 | 21.7 | 23.4 | 34.9 | 2.58 | 1.1 | 2.77 | 1.11 | 230 | 186 | 2268 | 2268
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:20:00 | 2051.64 | 722.9 | 825188.24 | 799002.74 | 16.68 | 2435.454 | 1992.642 | 137.24 | 47 | 184 | 36.6 | 42.4 | 34.9 | 44.9 | 0 | 0 | - | - | 38.3 | 40.7 | 230 | 186 | 60.8 | 60.6 | 69.2 | 23.5 | 43.4 | 2.51 | 9.6 | 24.7 | 60.9 | 73.7 | 23.7 | 46.6 | 2.73 | 9.8 | 26.3 | 21.7 | 23.3 | 35.6 | 2.57 | 1.11 | 2.76 | 1.11 | 230 | 186 | 2202 | 2202
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:25:00 | 2062.04 | 722.9 | 825198.58 | 799002.74 | 17.34 | 2428.074 | 2000.022 | 121.849 | 47 | 184 | 36.5 | 42.4 | 34.8 | 45 | 0 | 0 | - | - | 38.3 | 40.7 | 230 | 186 | 59.6 | 59.6 | 68.3 | 23.5 | 43.2 | 2.5 | 9.3 | 24 | 59.9 | 73.1 | 23.7 | 46.4 | 2.71 | 9.6 | 25.9 | 21.7 | 23.3 | 36.1 | 2.56 | 1.12 | 2.74 | 1.11 | 230 | 186 | 2127 | 2127
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:30:00 | 2063.82 | 729.9 | 825200.12 | 799010.26 | 17.98 | 2428.074 | 2000.022 | -345.382 | 47 | 184 | 36.3 | 42.5 | 34.6 | 45.1 | 0 | 0 | - | - | 38.2 | 40.8 | 230 | 186 | 59.1 | 59.1 | 67.8 | 23.4 | 42.9 | 2.48 | 9 | 23.8 | 58.9 | 72.5 | 23.7 | 46.2 | 2.7 | 9.3 | 25.5 | 21.7 | 23.3 | 35.9 | 2.54 | 1.13 | 2.73 | 1.13 | 230 | 186 | 2055 | 2055
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:35:00 | 2063.82 | 759.9 | 825200.12 | 799040.42 | 18.61 | 2442.834 | 1985.262 | -333.54 | 46 | 184 | 36.2 | 42.6 | 34.5 | 45.2 | 0 | 0 | - | - | 38.2 | 40.8 | 230 | 186 | 58.6 | 58.6 | 67.3 | 23.4 | 42.9 | 2.47 | 9.1 | 23.4 | 58.4 | 72.1 | 23.6 | 46.1 | 2.69 | 9.4 | 25.2 | 21.7 | 23.2 | 36.1 | 2.53 | 1.12 | 2.72 | 1.12 | 230 | 186 | 2041 | 2041
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:40:00 | 2063.82 | 800.82 | 825200.12 | 799080.86 | 19.25 | 2479.734 | 1948.362 | -397.48 | 45 | 184 | 36.1 | 42.7 | 34.3 | 45.4 | 0 | 0 | - | - | 38.2 | 40.8 | 230 | 186 | 58.6 | 58.6 | 67.2 | 23.3 | 42.9 | 2.47 | 8.9 | 23.5 | 58.4 | 71.9 | 23.4 | 45.9 | 2.69 | 9.3 | 25.1 | 21.6 | 23.1 | 36.1 | 2.52 | 1.13 | 2.72 | 1.12 | 230 | 186 | 2035 | 2035
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:45:00 | 2070.54 | 809.76 | 825207.84 | 799089.6 | 19.86 | 2501.874 | 1926.222 | 355.996 | 45 | 184 | 35.9 | 42.8 | 34.2 | 45.5 | 0 | 0 | - | - | 38.1 | 40.8 | 230 | 186 | 57.6 | 57.6 | 66.8 | 23.2 | 42.4 | 2.44 | 9 | 23.5 | 57.8 | 71.6 | 23.3 | 45.7 | 2.66 | 9.5 | 25.2 | 21.3 | 22.9 | 36 | 2.5 | 1.12 | 2.7 | 1.11 | 230 | 186 | 2040 | 2038
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:50:00 | 2080.92 | 822.6 | 825217.22 | 799103.12 | 20.48 | 2487.114 | 1940.982 | -431.449 | 45 | 184 | 35.7 | 42.9 | 34.1 | 45.6 | 0 | 0 | - | - | 38.1 | 40.8 | 230 | 186 | 57.6 | 57.6 | 66.6 | 22.9 | 42.4 | 2.46 | 9 | 23 | 57.8 | 71.5 | 23.2 | 45.7 | 2.67 | 9.4 | 25 | 21.2 | 22.8 | 35.8 | 2.52 | 1.11 | 2.7 | 1.1 | 230 | 186 | 2053 | 2053
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 12:55:00 | 2082.76 | 843.24 | 825219.42 | 799123.08 | 21.12 | 2524.015 | 1904.082 | 140.58 | 44 | 184 | 35.5 | 43 | 33.7 | 45.9 | 0 | 0 | - | - | 38 | 40.9 | 230 | 186 | 58.1 | 58.1 | 66.7 | 22.7 | 42.6 | 2.46 | 8.9 | 23 | 57.8 | 71.5 | 22.9 | 45.6 | 2.66 | 9.3 | 25 | 21.1 | 22.6 | 35.6 | 2.52 | 1.11 | 2.7 | 1.1 | 230 | 186 | 2067 | 2067
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:00:00 | 2085.38 | 854.9 | 825221.68 | 799134.88 | 21.74 | 2531.396 | 1896.702 | -343.382 | 44 | 184 | 35.3 | 43.2 | 33.5 | 46.1 | 0 | 0 | - | - | 37.9 | 40.9 | 230 | 186 | 58.7 | 58.6 | 67.2 | 22.7 | 42.9 | 2.47 | 8.8 | 23.3 | 58.8 | 71.9 | 22.8 | 45.9 | 2.68 | 9.3 | 25.2 | 20.8 | 22.4 | 35.9 | 2.53 | 1.11 | 2.71 | 1.1 | 230 | 186 | 2049 | 2052
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:05:00 | 2088.26 | 864.22 | 825225.04 | 799144.06 | 22.36 | 2538.776 | 1889.322 | 347.859 | 44 | 184 | 35.2 | 43.3 | 33.4 | 46.1 | 0 | 0 | - | - | 37.9 | 40.8 | 230 | 186 | 58.2 | 58.1 | 67.2 | 22.4 | 42.7 | 2.46 | 8.9 | 23.6 | 58.3 | 71.8 | 22.7 | 45.6 | 2.67 | 9.2 | 25.3 | 20.7 | 22.3 | 36.2 | 2.51 | 1.1 | 2.7 | 1.09 | 230 | 186 | 2028 | 2028
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:10:00 | 2123.08 | 864.22 | 825259.74 | 799144.06 | 22.99 | 2501.874 | 1926.222 | 365.513 | 45 | 184 | 35.1 | 43.3 | 33.2 | 46.2 | 0 | 0 | - | - | 37.8 | 40.8 | 230 | 186 | 58.2 | 58.1 | 66.9 | 22.3 | 42.2 | 2.43 | 8.9 | 23.8 | 58.2 | 71.7 | 22.6 | 45.6 | 2.66 | 9.2 | 25.3 | 20.7 | 22.2 | 35.9 | 2.48 | 1.09 | 2.69 | 1.09 | 230 | 186 | 2041 | 2041
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:15:00 | 2156.64 | 864.22 | 825293.14 | 799144.06 | 23.71 | 2479.734 | 1948.362 | -33.076 | 46 | 184 | 35 | 43.3 | 33.1 | 46.2 | 0 | 0 | - | - | 37.7 | 40.8 | 230 | 186 | 61.8 | 61.5 | 69.4 | 21.9 | 43.2 | 2.5 | 9.9 | 25 | 61.9 | 73.8 | 22.2 | 46.5 | 2.72 | 10 | 26.4 | 20 | 21.7 | 35.6 | 2.56 | 1.05 | 2.76 | 1.05 | 230 | 186 | 2400 | 2400
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:20:00 | 2156.94 | 876.84 | 825293.24 | 799157.42 | 24.37 | 2479.734 | 1948.362 | -537.568 | 45 | 184 | 35.1 | 43 | 33.4 | 45.8 | 0 | 0 | - | - | 37.7 | 40.8 | 230 | 186 | 57.7 | 58 | 67.2 | 21.8 | 42.1 | 2.44 | 8.8 | 23.9 | 57.5 | 72 | 21.9 | 45.4 | 2.65 | 9.1 | 25.7 | 20 | 21.6 | 35.2 | 2.5 | 1.08 | 2.68 | 1.08 | 230 | 186 | 2089 | 2089
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:25:00 | 2156.94 | 930.66 | 825293.24 | 799210.88 | 25.02 | 2524.015 | 1904.082 | -139.677 | 44 | 184 | 35.2 | 42.7 | 33.4 | 45.5 | 0 | 0 | - | - | 37.6 | 40.8 | 230 | 186 | 57.7 | 58 | 66.9 | 21.7 | 42.2 | 2.43 | 8.8 | 23.7 | 58 | 71.6 | 21.9 | 45.3 | 2.65 | 9.2 | 25.4 | 20 | 21.6 | 35.2 | 2.49 | 1.08 | 2.68 | 1.07 | 230 | 186 | 2088 | 2086
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:30:00 | 2159.48 | 931.92 | 825295.78 | 799211.78 | 25.64 | 2538.776 | 1889.322 | -22.455 | 44 | 184 | 34.9 | 42.9 | 33.2 | 45.6 | 0 | 0 | - | - | 37.5 | 40.8 | 230 | 186 | 56.7 | 56.9 | 66.8 | 21.7 | 42.1 | 2.43 | 8.8 | 23.6 | 57 | 71 | 21.8 | 44.9 | 2.62 | 9.2 | 25.4 | 19.8 | 21.4 | 34.7 | 2.48 | 1.07 | 2.65 | 1.06 | 230 | 186 | 2115 | 2116
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:35:00 | 2163.58 | 933.86 | 825299.88 | 799213.94 | 26.28 | 2538.776 | 1889.322 | -101.138 | 44 | 184 | 34.5 | 43.2 | 32.7 | 46.1 | 0 | 0 | - | - | 37.5 | 40.8 | 230 | 186 | 57.3 | 57.5 | 66.6 | 21.3 | 42 | 2.45 | 9.1 | 23.2 | 57.3 | 70.9 | 21.5 | 44.8 | 2.62 | 9.4 | 25.1 | 19.5 | 21.2 | 33.2 | 2.5 | 1.05 | 2.65 | 1.05 | 230 | 186 | 2208 | 2208
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:40:00 | 2163.58 | 959.24 | 825299.88 | 799240.36 | 26.94 | 2560.918 | 1867.182 | -632.701 | 43 | 184 | 34.2 | 43.4 | 32.3 | 46.5 | 0 | 0 | - | - | 37.4 | 40.9 | 230 | 186 | 57.8 | 58 | 67 | 21.1 | 41.9 | 2.41 | 8.9 | 24.2 | 58.3 | 71.8 | 21.2 | 45.1 | 2.63 | 9.3 | 25.9 | 19.3 | 20.9 | 33.2 | 2.47 | 1.05 | 2.66 | 1.04 | 230 | 186 | 2206 | 2206
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:45:00 | 2163.58 | 1023.72 | 825299.88 | 799304.5 | 27.6 | 2649.48 | 1778.618 | -927.555 | 42 | 184 | 34.1 | 43.4 | 32 | 46.7 | 0 | 0 | - | - | 37.2 | 40.9 | 230 | 0 | 56.2 | 53.3 | 66.5 | 20.8 | 41.1 | 2.38 | 8.8 | 24.1 | 58 | 70.9 | 21.1 | 44 | 2.41 | 32.5 | 28.8 | 19.1 | 20.7 | 32.2 | 2.44 | 1.05 | 2.42 | 0.45 | 230 | 0 | 2262 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:50:00 | 2163.58 | 1091.54 | 825299.88 | 799371.64 | 27.98 | 2701.14 | 1726.956 | -548.944 | 40 | 184 | 33.8 | 43.6 | 31.7 | 47 | 0 | 0 | - | - | 37.1 | 40.9 | 230 | 0 | 49.9 | 50.3 | 66.7 | 21.9 | 41.9 | 2.44 | 9.2 | 23.5 | 50.4 | 37.7 | 44.3 | 34.4 | 1.72 | 22.2 | 8.7 | 20.5 | 21.5 | 31.4 | 2.49 | 1.07 | 1.76 | 1.42 | 230 | 0 | 2316 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 13:55:00 | 2163.58 | 1111.06 | 825299.88 | 799390.94 | 28.36 | 2723.28 | 1704.816 | -137.19 | 40 | 184 | 33.5 | 44 | 31.6 | 47.2 | 0 | 0 | - | - | 36.9 | 41 | 230 | 0 | 50.5 | 50.8 | 67.2 | 21.8 | 42.4 | 2.44 | 9 | 23.8 | 50.9 | 36.6 | 47.7 | 30.7 | 1.41 | 25.7 | 14.6 | 20.6 | 21.7 | 31.5 | 2.5 | 1.07 | 1.42 | 1.41 | 230 | 0 | 2314 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:00:00 | 2163.58 | 1139.78 | 825299.88 | 799421.36 | 28.61 | 2745.42 | 1682.676 | -441.214 | 39 | 184 | 33.2 | 44.4 | 31.3 | 47.5 | 0 | 0 | - | - | 36.7 | 41.1 | 0 | 0 | 0 | 0 | 46.3 | 30.5 | 33.9 | 1.72 | 8.1 | 17.4 | 0 | 36.4 | 45.6 | 30.4 | 1.43 | 22.8 | 13.9 | 22.3 | 22.4 | 31.2 | 1.74 | 1.42 | 1.43 | 1.44 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:05:00 | 2163.58 | 1166.08 | 825299.88 | 799446.4 | 28.77 | 2774.94 | 1653.156 | -447.245 | 38 | 184 | 32.8 | 44.9 | 31 | 47.9 | 0 | 0 | - | - | 36.4 | 41.3 | 0 | 0 | 0 | 0 | 31.4 | 41.2 | 32.4 | 1.53 | 17.7 | 6.2 | 0 | 35.6 | 42 | 30.4 | 1.45 | 18.5 | 12.5 | 23.2 | 23.2 | 31.3 | 1.55 | 1.48 | 1.46 | 1.48 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:10:00 | 2163.58 | 1196.7 | 825299.88 | 799477.06 | 28.93 | 2811.843 | 1616.256 | -363.252 | 38 | 184 | 32.4 | 45.5 | 30.8 | 48.3 | 0 | 0 | - | - | 36.2 | 41.5 | 0 | 0 | 0 | 0 | 28.8 | 43.2 | 31.7 | 1.49 | 19.3 | 4.6 | 0 | 34.7 | 38.7 | 30.2 | 1.47 | 14.9 | 11.4 | 23.6 | 23.5 | 29.2 | 1.51 | 1.49 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:15:00 | 2173.62 | 1204.82 | 825310.2 | 799484.66 | 29.09 | 2811.843 | 1616.256 | 269.8 | 38 | 184 | 32 | 46 | 30.4 | 48.9 | 0 | 0 | - | - | 35.8 | 41.9 | 0 | 0 | 0 | 0 | 28.6 | 42.6 | 30.9 | 1.49 | 18.5 | 4.3 | 0 | 33.6 | 36.2 | 29.7 | 1.47 | 12.3 | 10 | 23.7 | 23.7 | 26.7 | 1.51 | 1.5 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:20:00 | 2192.76 | 1204.82 | 825329.14 | 799484.66 | 29.24 | 2804.463 | 1623.636 | 79.19 | 38 | 184 | 31.5 | 46.6 | 30 | 49.5 | 0 | 0 | - | - | 35.2 | 42.3 | 0 | 0 | 0 | 0 | 28.5 | 40.7 | 30.2 | 1.49 | 16.5 | 4.2 | 0 | 32.1 | 34.1 | 29.1 | 1.47 | 10.1 | 8.6 | 23.8 | 23.8 | 26.3 | 1.51 | 1.51 | 1.48 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:25:00 | 2200.52 | 1205.06 | 825337.3 | 799484.9 | 29.38 | 2797.082 | 1631.016 | 223.702 | 38 | 184 | 30.9 | 47.4 | 29.5 | 50 | 0 | 0 | - | - | 34.5 | 43 | 0 | 0 | 0 | 0 | 28.4 | 38.9 | 29.6 | 1.49 | 14.7 | 4 | 0 | 30.9 | 32.4 | 28.3 | 1.47 | 8.6 | 7.6 | 23.9 | 23.9 | 25.8 | 1.51 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:30:00 | 2246.52 | 1205.06 | 825384.8 | 799484.9 | 29.54 | 2730.66 | 1697.436 | 960.937 | 40 | 184 | 30.6 | 47.8 | 29.2 | 50.6 | 0 | 0 | - | - | 33.9 | 43.6 | 0 | 0 | 0 | 0 | 28.2 | 37.2 | 28.8 | 1.5 | 12.9 | 3.6 | 0 | 30.1 | 31.2 | 27.8 | 1.47 | 7.4 | 6.6 | 24 | 23.9 | 26.2 | 1.52 | 1.51 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:35:00 | 2328.82 | 1205.06 | 825466.54 | 799484.9 | 29.69 | 2656.86 | 1771.237 | 913.463 | 41 | 184 | 30.2 | 48.2 | 28.8 | 51.2 | 0 | 0 | - | - | 33.3 | 44.2 | 0 | 0 | 0 | 0 | 27.9 | 36.2 | 28.4 | 1.5 | 11.8 | 3.3 | 0 | 29.4 | 30.4 | 27.6 | 1.47 | 6.5 | 6 | 24.1 | 24.1 | 26.5 | 1.52 | 1.52 | 1.47 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:40:00 | 2399.54 | 1205.06 | 825536.7 | 799484.9 | 29.84 | 2583.06 | 1845.042 | 804.287 | 43 | 184 | 29.9 | 48.7 | 28.6 | 51.6 | 0 | 0 | - | - | 32.9 | 44.7 | 0 | 0 | 0 | 0 | 27.9 | 35.4 | 28.3 | 1.51 | 10.7 | 3.1 | 0 | 29.1 | 29.8 | 27.4 | 1.48 | 5.7 | 5.5 | 24.3 | 24.3 | 26.7 | 1.53 | 1.53 | 1.48 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:45:00 | 2454.54 | 1205.06 | 825591.2 | 799484.9 | 29.98 | 2524.015 | 1904.082 | 252.319 | 44 | 184 | 29.5 | 49.3 | 28.4 | 51.9 | 0 | 0 | - | - | 32.5 | 45.1 | 0 | 0 | 0 | 0 | 27.9 | 34.4 | 28.2 | 1.52 | 9.5 | 2.9 | 0 | 28.7 | 29.4 | 27.4 | 1.48 | 5.2 | 5.1 | 24.6 | 24.5 | 26.6 | 1.54 | 1.54 | 1.48 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:50:00 | 2477.88 | 1205.06 | 825614.58 | 799484.9 | 30.09 | 2494.494 | 1933.602 | 377.583 | 45 | 184 | 29.2 | 49.9 | 28.3 | 52.2 | 0 | 0 | - | - | 32.2 | 45.4 | 0 | 0 | 0 | 0 | 28 | 33.4 | 28.1 | 1.53 | 8.3 | 2.9 | 0 | 28.4 | 29.1 | 27.4 | 1.48 | 4.7 | 4.7 | 24.7 | 24.7 | 26.3 | 1.55 | 1.54 | 1.48 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 14:55:00 | 2516.3 | 1205.06 | 825652.78 | 799484.9 | 30.22 | 2457.594 | 1970.502 | 326.949 | 46 | 184 | 28.9 | 50.4 | 28.1 | 52.4 | 0 | 0 | - | - | 31.9 | 45.8 | 0 | 0 | 0 | 0 | 28.1 | 32.6 | 28.1 | 1.53 | 7.3 | 2.8 | 0 | 28.2 | 28.7 | 27.4 | 1.49 | 4.4 | 4.4 | 24.9 | 24.8 | 26.6 | 1.55 | 1.55 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:00:00 | 2522.2 | 1215.26 | 825658.5 | 799495.56 | 30.32 | 2450.214 | 1977.882 | -217.215 | 46 | 184 | 28.6 | 50.9 | 28.1 | 52.6 | 0 | 0 | - | - | 31.7 | 46.1 | 0 | 0 | 0 | 0 | 28.1 | 31.8 | 28.1 | 1.54 | 6.6 | 2.7 | 0 | 28.1 | 28.7 | 27.4 | 1.49 | 4.2 | 4.3 | 25 | 24.9 | 26.3 | 1.56 | 1.55 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:05:00 | 2529.48 | 1220.28 | 825666.46 | 799500.12 | 30.42 | 2457.594 | 1970.502 | 342.15 | 46 | 184 | 28.4 | 51.2 | 28 | 52.7 | 0 | 0 | - | - | 31.5 | 46.3 | 0 | 0 | 0 | 0 | 28.1 | 31.2 | 27.9 | 1.54 | 5.9 | 2.6 | 0 | 27.9 | 28.6 | 27.4 | 1.49 | 4 | 4 | 25 | 25 | 26.4 | 1.56 | 1.56 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:10:00 | 2537.44 | 1224.6 | 825673.9 | 799504.44 | 30.52 | 2450.214 | 1977.882 | 88.559 | 46 | 184 | 28.2 | 51.5 | 27.9 | 52.9 | 0 | 0 | - | - | 31.3 | 46.5 | 0 | 0 | 0 | 0 | 28.1 | 30.7 | 27.8 | 1.54 | 5.3 | 2.6 | 0 | 27.7 | 28.4 | 27.4 | 1.49 | 3.9 | 3.9 | 25.1 | 25.1 | 25.9 | 1.56 | 1.56 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:15:00 | 2555.78 | 1224.6 | 825692.9 | 799504.44 | 30.61 | 2435.454 | 1992.642 | 385.92 | 46 | 184 | 28.1 | 51.8 | 27.8 | 53.1 | 0 | 0 | - | - | 31.1 | 46.6 | 0 | 0 | 0 | 0 | 27.9 | 30.2 | 27.7 | 1.54 | 4.7 | 2.4 | 0 | 27.4 | 28.2 | 27.3 | 1.49 | 3.7 | 3.6 | 25.1 | 25.1 | 25.9 | 1.56 | 1.55 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:20:00 | 2571.24 | 1224.6 | 825707.82 | 799504.44 | 30.71 | 2428.074 | 2000.022 | 188.084 | 47 | 184 | 27.9 | 52 | 27.7 | 53.3 | 0 | 0 | - | - | 31 | 46.8 | 0 | 0 | 0 | 0 | 27.9 | 29.8 | 27.7 | 1.53 | 4.6 | 2.6 | 0 | 27.3 | 28.2 | 27.2 | 1.49 | 3.6 | 3.5 | 25.1 | 25.1 | 25.4 | 1.55 | 1.55 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:25:00 | 2585.32 | 1224.6 | 825721.98 | 799504.44 | 30.8 | 2405.934 | 2022.162 | 126.884 | 47 | 184 | 27.8 | 52.4 | 27.6 | 53.4 | 0 | 0 | - | - | 30.8 | 47 | 0 | 0 | 0 | 0 | 27.8 | 29.3 | 27.6 | 1.52 | 4.2 | 2.7 | 0 | 27.2 | 28.1 | 27.2 | 1.49 | 3.5 | 3.2 | 25.2 | 25.2 | 25.5 | 1.54 | 1.55 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:30:00 | 2602.04 | 1224.6 | 825738.7 | 799504.44 | 30.88 | 2391.174 | 2036.923 | 188.603 | 48 | 184 | 27.7 | 52.6 | 27.6 | 53.6 | 0 | 0 | - | - | 30.6 | 47.1 | 0 | 0 | 0 | 0 | 27.7 | 28.9 | 27.3 | 1.52 | 3.8 | 2.6 | 0 | 26.9 | 27.8 | 27.1 | 1.49 | 3.3 | 3 | 25.2 | 25.2 | 25.2 | 1.54 | 1.55 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:35:00 | 2606.4 | 1226.84 | 825742.7 | 799506.94 | 30.97 | 2391.174 | 2036.923 | -118.63 | 48 | 184 | 27.6 | 52.7 | 27.5 | 53.7 | 0 | 0 | - | - | 30.4 | 47.3 | 0 | 0 | 0 | 0 | 27.4 | 28.6 | 27.1 | 1.52 | 3.4 | 2.4 | 0 | 26.7 | 27.7 | 26.9 | 1.49 | 3.1 | 2.8 | 25.2 | 25.2 | 25.3 | 1.54 | 1.55 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:40:00 | 2606.4 | 1234.4 | 825742.7 | 799514.32 | 31.05 | 2391.174 | 2036.923 | -65.307 | 47 | 184 | 27.5 | 53 | 27.4 | 53.7 | 0 | 0 | - | - | 30.4 | 47.6 | 0 | 0 | 0 | 0 | 27.2 | 28.2 | 26.8 | 1.52 | 3.1 | 2.2 | 0 | 26.4 | 27.6 | 26.8 | 1.49 | 2.9 | 2.6 | 25.3 | 25.2 | 25.3 | 1.54 | 1.55 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:45:00 | 2606.58 | 1237.84 | 825742.88 | 799517.7 | 31.12 | 2398.554 | 2029.543 | -13.204 | 47 | 184 | 27.4 | 53.2 | 27.4 | 53.9 | 0 | 0 | - | - | 30.2 | 47.7 | 0 | 0 | 0 | 0 | 27.1 | 27.9 | 26.7 | 1.52 | 2.8 | 2 | 0 | 26.3 | 27.3 | 26.7 | 1.49 | 2.7 | 2.4 | 25.3 | 25.3 | 25.6 | 1.54 | 1.55 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:50:00 | 2607.08 | 1239.12 | 825743.38 | 799519.02 | 31.2 | 2398.554 | 2029.543 | 11.796 | 47 | 184 | 27.3 | 53.3 | 27.3 | 53.9 | 0 | 0 | - | - | 30.1 | 47.9 | 0 | 0 | 0 | 0 | 26.9 | 27.8 | 26.7 | 1.52 | 2.6 | 1.8 | 0 | 26.2 | 27.3 | 26.7 | 1.49 | 2.7 | 2.3 | 25.3 | 25.3 | 25.8 | 1.54 | 1.55 | 1.49 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 15:55:00 | 2608.2 | 1241.26 | 825744.5 | 799521.14 | 31.28 | 2398.554 | 2029.543 | -132.559 | 47 | 184 | 27.2 | 53.5 | 27.3 | 54 | 0 | 0 | - | - | 30 | 48 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.7 | 1.52 | 2.6 | 1.8 | 0 | 26.2 | 27.3 | 26.8 | 1.49 | 2.7 | 2.3 | 25.3 | 25.3 | 26 | 1.55 | 1.55 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:00:00 | 2608.32 | 1246.12 | 825744.72 | 799525.96 | 31.35 | 2405.934 | 2022.162 | 62.718 | 47 | 184 | 27.1 | 53.6 | 27.3 | 54.1 | 0 | 0 | - | - | 29.9 | 48.1 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.8 | 1.53 | 2.6 | 1.7 | 0 | 26.2 | 27.3 | 26.8 | 1.5 | 2.7 | 2.3 | 25.3 | 25.3 | 26.1 | 1.55 | 1.55 | 1.5 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:05:00 | 2614.96 | 1247.48 | 825752.02 | 799527.32 | 31.42 | 2398.554 | 2029.543 | 418.093 | 47 | 184 | 27.1 | 53.8 | 27.2 | 54.2 | 0 | 0 | - | - | 29.9 | 48.2 | 0 | 0 | 0 | 0 | 27 | 27.7 | 26.8 | 1.52 | 2.5 | 1.8 | 0 | 26.3 | 27.4 | 26.9 | 1.5 | 2.8 | 2.3 | 25.3 | 25.3 | 26.1 | 1.55 | 1.55 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:10:00 | 2652.58 | 1247.48 | 825789.5 | 799527.32 | 31.51 | 2354.273 | 2073.826 | 386.668 | 48 | 184 | 27 | 53.8 | 27.1 | 54.4 | 0 | 0 | - | - | 29.9 | 48.2 | 0 | 0 | 0 | 0 | 27 | 27.7 | 26.8 | 1.53 | 2.5 | 1.7 | 0 | 26.3 | 27.4 | 26.9 | 1.5 | 2.7 | 2.3 | 25.4 | 25.4 | 26.2 | 1.55 | 1.55 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:15:00 | 2683.84 | 1247.48 | 825820.82 | 799527.32 | 31.6 | 2324.751 | 2103.348 | 339.4 | 49 | 184 | 26.9 | 53.9 | 27 | 54.6 | 0 | 0 | - | - | 29.9 | 48.2 | 0 | 0 | 0 | 0 | 27 | 27.7 | 26.9 | 1.53 | 2.4 | 1.7 | 0 | 26.3 | 27.5 | 27 | 1.5 | 2.7 | 2.3 | 25.4 | 25.4 | 26.2 | 1.55 | 1.55 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:20:00 | 2708.96 | 1247.48 | 825845.56 | 799527.32 | 31.67 | 2302.609 | 2125.488 | 276.117 | 50 | 184 | 26.9 | 54.1 | 27 | 54.6 | 0 | 0 | - | - | 29.8 | 48.3 | 0 | 0 | 0 | 0 | 27 | 27.7 | 27 | 1.53 | 2.4 | 1.7 | 0 | 26.4 | 27.5 | 27 | 1.5 | 2.7 | 2.3 | 25.5 | 25.5 | 26.2 | 1.55 | 1.55 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:25:00 | 2733.38 | 1247.48 | 825870.04 | 799527.32 | 31.75 | 2273.088 | 2155.008 | 130.406 | 50 | 184 | 26.8 | 54.3 | 27 | 54.6 | 0 | 0 | - | - | 29.8 | 48.3 | 0 | 0 | 0 | 0 | 27 | 27.7 | 27 | 1.53 | 2.4 | 1.7 | 0 | 26.4 | 27.5 | 27.1 | 1.5 | 2.7 | 2.2 | 25.6 | 25.6 | 26.1 | 1.56 | 1.56 | 1.5 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:30:00 | 2747.1 | 1247.48 | 825883.82 | 799527.32 | 31.82 | 2258.328 | 2169.768 | 220.195 | 51 | 184 | 26.8 | 54.3 | 27 | 54.7 | 0 | 0 | - | - | 29.7 | 48.4 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 26.8 | 1.53 | 2.2 | 1.6 | 0 | 26.3 | 27.4 | 27.1 | 1.5 | 2.5 | 2.1 | 25.6 | 25.6 | 25.6 | 1.55 | 1.56 | 1.51 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:35:00 | 2766.72 | 1247.48 | 825903.26 | 799527.32 | 31.9 | 2236.188 | 2191.908 | 227.523 | 51 | 184 | 26.7 | 54.5 | 26.9 | 54.8 | 0 | 0 | - | - | 29.7 | 48.4 | 0 | 0 | 0 | 0 | 26.7 | 27.6 | 26.7 | 1.53 | 2.1 | 1.5 | 0 | 26.2 | 27.2 | 26.9 | 1.51 | 2.4 | 1.9 | 25.7 | 25.7 | 25.7 | 1.55 | 1.56 | 1.51 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:40:00 | 2786.52 | 1247.48 | 825923.18 | 799527.32 | 31.98 | 2214.048 | 2214.048 | 247.938 | 52 | 184 | 26.7 | 54.6 | 26.9 | 54.9 | 0 | 0 | - | - | 29.6 | 48.4 | 0 | 0 | 0 | 0 | 26.7 | 27.6 | 26.7 | 1.53 | 2 | 1.5 | 0 | 26.2 | 27.2 | 26.8 | 1.51 | 2.3 | 1.8 | 25.8 | 25.8 | 25.6 | 1.55 | 1.56 | 1.51 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:45:00 | 2807.52 | 1247.48 | 825944.34 | 799527.32 | 32.05 | 2177.148 | 2250.948 | 237.755 | 52 | 184 | 26.7 | 54.7 | 26.8 | 55 | 0 | 0 | - | - | 29.5 | 48.6 | 0 | 0 | 0 | 0 | 26.7 | 27.4 | 26.6 | 1.53 | 1.9 | 1.4 | 0 | 26.2 | 27.2 | 26.8 | 1.51 | 2.1 | 1.7 | 25.8 | 25.8 | 25.8 | 1.55 | 1.56 | 1.51 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:50:00 | 2821.76 | 1247.48 | 825958.14 | 799527.32 | 32.12 | 2169.768 | 2258.328 | 67.477 | 52 | 184 | 26.6 | 54.7 | 26.8 | 55.1 | 0 | 0 | - | - | 29.5 | 48.7 | 0 | 0 | 0 | 0 | 26.7 | 27.5 | 26.6 | 1.53 | 2 | 1.4 | 0 | 26.2 | 27.2 | 26.7 | 1.51 | 2.1 | 1.7 | 25.8 | 25.9 | 25.9 | 1.55 | 1.56 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 16:55:00 | 2823.66 | 1253.22 | 825959.96 | 799533.5 | 32.19 | 2169.768 | 2258.328 | -310.622 | 52 | 184 | 26.6 | 54.8 | 26.8 | 55.1 | 0 | 0 | - | - | 29.4 | 48.8 | 0 | 0 | 0 | 0 | 26.6 | 27.5 | 26.6 | 1.53 | 2 | 1.3 | 0 | 26.2 | 27.2 | 26.7 | 1.52 | 2.1 | 1.6 | 25.9 | 25.9 | 25.8 | 1.55 | 1.56 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:00:00 | 2823.66 | 1285.36 | 825959.96 | 799566.32 | 32.28 | 2191.908 | 2236.188 | -442.35 | 51 | 184 | 26.5 | 54.9 | 26.7 | 55.2 | 0 | 0 | - | - | 29.4 | 48.8 | 0 | 0 | 0 | 0 | 26.4 | 27.4 | 26.4 | 1.53 | 1.9 | 1.3 | 0 | 26.1 | 27.2 | 26.7 | 1.52 | 2 | 1.5 | 25.9 | 25.9 | 25.8 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:05:00 | 2823.66 | 1302.08 | 825959.96 | 799581.92 | 32.35 | 2236.188 | 2191.908 | -4.592 | 51 | 184 | 26.5 | 55.1 | 26.6 | 55.4 | 0 | 0 | - | - | 29.3 | 48.9 | 0 | 0 | 0 | 0 | 26.4 | 27.4 | 26.4 | 1.53 | 1.8 | 1.3 | 0 | 26 | 27.1 | 26.7 | 1.52 | 1.9 | 1.5 | 25.9 | 25.9 | 25.8 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:10:00 | 2824.3 | 1303.66 | 825960.6 | 799583.56 | 32.42 | 2236.188 | 2191.908 | -49.817 | 51 | 184 | 26.5 | 55.1 | 26.6 | 55.6 | 0 | 0 | - | - | 29.3 | 49 | 0 | 0 | 0 | 0 | 26.3 | 27.3 | 26.3 | 1.53 | 1.8 | 1.1 | 0 | 25.9 | 27.1 | 26.7 | 1.52 | 1.8 | 1.3 | 25.9 | 25.9 | 25.8 | 1.55 | 1.57 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:15:00 | 2824.34 | 1308.48 | 825960.64 | 799588.42 | 32.49 | 2236.188 | 2191.908 | -114.37 | 51 | 184 | 26.4 | 55.2 | 26.6 | 55.5 | 0 | 0 | - | - | 29.2 | 49.1 | 0 | 0 | 0 | 0 | 26.2 | 27.3 | 26.3 | 1.53 | 1.7 | 1 | 0 | 25.9 | 27 | 26.6 | 1.52 | 1.8 | 1.3 | 26 | 26 | 25.9 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:20:00 | 2824.34 | 1321.62 | 825960.64 | 799601.68 | 32.56 | 2250.948 | 2177.148 | -193.358 | 51 | 184 | 26.4 | 55.2 | 26.7 | 55.5 | 0 | 0 | - | - | 29.2 | 49.1 | 0 | 0 | 0 | 0 | 26.2 | 27.2 | 26.2 | 1.53 | 1.7 | 1 | 0 | 25.8 | 26.9 | 26.6 | 1.52 | 1.8 | 1.2 | 26 | 25.9 | 25.7 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:25:00 | 2824.34 | 1341.9 | 825960.64 | 799622.24 | 32.64 | 2258.328 | 2169.768 | -230.577 | 50 | 184 | 26.4 | 55.2 | 26.7 | 55.5 | 0 | 0 | - | - | 29.1 | 49.2 | 0 | 0 | 0 | 0 | 26.2 | 27.2 | 26.2 | 1.53 | 1.7 | 1 | 0 | 25.8 | 26.9 | 26.6 | 1.52 | 1.8 | 1.2 | 26 | 26 | 25.8 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:30:00 | 2824.34 | 1363.5 | 825960.64 | 799643.76 | 32.71 | 2295.229 | 2132.868 | -283.728 | 49 | 184 | 26.4 | 55.3 | 26.6 | 55.6 | 0 | 0 | - | - | 29.1 | 49.2 | 0 | 0 | 0 | 0 | 26.2 | 27.2 | 26.2 | 1.53 | 1.6 | 0.9 | 0 | 25.8 | 26.9 | 26.6 | 1.52 | 1.7 | 1.2 | 26 | 25.9 | 25.9 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:35:00 | 2824.34 | 1390.1 | 825960.64 | 799670.68 | 32.79 | 2309.99 | 2118.108 | -339.889 | 49 | 184 | 26.3 | 55.4 | 26.5 | 55.8 | 0 | 0 | - | - | 29.1 | 49.3 | 0 | 0 | 0 | 0 | 26.1 | 27.2 | 26.3 | 1.53 | 1.6 | 0.9 | 0 | 25.7 | 26.9 | 26.6 | 1.52 | 1.7 | 1.1 | 25.9 | 25.9 | 26 | 1.55 | 1.56 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:40:00 | 2824.34 | 1419.36 | 825960.64 | 799699.98 | 32.86 | 2346.893 | 2081.207 | -352.775 | 48 | 184 | 26.2 | 55.6 | 26.5 | 55.8 | 0 | 0 | - | - | 29 | 49.3 | 0 | 0 | 0 | 0 | 26.2 | 27.2 | 26.4 | 1.53 | 1.7 | 1 | 0 | 25.8 | 26.9 | 26.6 | 1.52 | 1.8 | 1.2 | 25.9 | 25.9 | 26.1 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:45:00 | 2824.34 | 1447.64 | 825960.64 | 799728.16 | 32.94 | 2383.794 | 2044.304 | -326.463 | 47 | 184 | 26.2 | 55.6 | 26.6 | 55.7 | 0 | 0 | - | - | 29 | 49.4 | 0 | 0 | 0 | 0 | 26.2 | 27.2 | 26.4 | 1.52 | 1.8 | 1.1 | 0 | 25.8 | 26.9 | 26.6 | 1.52 | 1.8 | 1.3 | 25.9 | 25.9 | 26 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:50:00 | 2824.34 | 1471.22 | 825960.64 | 799751.18 | 33.02 | 2405.934 | 2022.162 | -195.711 | 47 | 184 | 26.3 | 55.5 | 26.6 | 55.6 | 0 | 0 | - | - | 29 | 49.5 | 0 | 0 | 0 | 0 | 26.2 | 27.3 | 26.4 | 1.52 | 1.8 | 1.1 | 0 | 25.8 | 27 | 26.6 | 1.52 | 1.8 | 1.3 | 25.9 | 25.9 | 26 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 17:55:00 | 2824.34 | 1488.18 | 825960.64 | 799768.02 | 33.09 | 2428.074 | 2000.022 | -295.46 | 46 | 184 | 26.2 | 55.6 | 26.7 | 55.5 | 0 | 0 | - | - | 28.9 | 49.5 | 0 | 0 | 0 | 0 | 26.3 | 27.3 | 26.6 | 1.52 | 1.9 | 1.1 | 0 | 25.9 | 27 | 26.7 | 1.52 | 1.9 | 1.4 | 25.9 | 25.9 | 26.1 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:00:00 | 2824.34 | 1524.82 | 825960.64 | 799804.96 | 33.17 | 2450.214 | 1977.882 | -267.858 | 46 | 184 | 26.2 | 55.6 | 26.6 | 55.6 | 0 | 0 | - | - | 28.9 | 49.6 | 0 | 0 | 0 | 0 | 26.3 | 27.3 | 26.6 | 1.52 | 1.9 | 1.2 | 0 | 25.9 | 27 | 26.7 | 1.52 | 1.9 | 1.4 | 25.9 | 25.8 | 26 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:05:00 | 2824.34 | 1549.68 | 825960.64 | 799830.02 | 33.25 | 2487.114 | 1940.982 | -295.092 | 45 | 184 | 26.2 | 55.6 | 26.6 | 55.5 | 0 | 0 | - | - | 28.9 | 49.6 | 0 | 0 | 0 | 0 | 26.3 | 27.3 | 26.7 | 1.52 | 1.9 | 1.2 | 0 | 25.9 | 27.1 | 26.8 | 1.52 | 1.9 | 1.4 | 25.8 | 25.8 | 26.1 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:10:00 | 2824.34 | 1575.7 | 825960.64 | 799856.06 | 33.32 | 2524.015 | 1904.082 | -401.085 | 44 | 184 | 26.2 | 55.7 | 26.6 | 55.6 | 0 | 0 | - | - | 28.9 | 49.7 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.7 | 1.52 | 2 | 1.2 | 0 | 26 | 27.1 | 26.8 | 1.52 | 2 | 1.4 | 25.8 | 25.8 | 26.1 | 1.55 | 1.56 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:15:00 | 2824.34 | 1616.26 | 825960.64 | 799896.86 | 33.41 | 2568.299 | 1859.802 | -812.172 | 43 | 184 | 26.2 | 55.7 | 26.6 | 55.6 | 0 | 0 | - | - | 28.8 | 49.7 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.7 | 1.52 | 2 | 1.3 | 0 | 26 | 27.1 | 26.8 | 1.52 | 2 | 1.5 | 25.8 | 25.8 | 26.2 | 1.55 | 1.55 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:20:00 | 2824.34 | 1672.34 | 825960.64 | 799952.42 | 33.5 | 2619.96 | 1808.141 | -474.405 | 42 | 184 | 26.2 | 55.7 | 26.6 | 55.6 | 0 | 0 | - | - | 28.8 | 49.8 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.7 | 1.52 | 2.2 | 1.3 | 0 | 26 | 27.1 | 26.8 | 1.52 | 2 | 1.5 | 25.8 | 25.7 | 26.1 | 1.55 | 1.55 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:25:00 | 2824.34 | 1719.26 | 825960.64 | 800000.06 | 33.58 | 2671.62 | 1756.476 | -601.645 | 41 | 184 | 26.1 | 55.8 | 26.6 | 55.6 | 0 | 0 | - | - | 28.8 | 49.8 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.7 | 1.52 | 2.1 | 1.2 | 0 | 25.9 | 27.1 | 26.8 | 1.52 | 2 | 1.4 | 25.7 | 25.7 | 26.1 | 1.55 | 1.55 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:30:00 | 2824.34 | 1779.76 | 825960.64 | 800061.62 | 33.67 | 2745.42 | 1682.676 | -785.97 | 39 | 184 | 26.2 | 55.8 | 26.6 | 55.5 | 0 | 0 | - | - | 28.8 | 49.8 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.7 | 1.52 | 2.1 | 1.2 | 0 | 25.9 | 27.1 | 26.8 | 1.52 | 2 | 1.4 | 25.7 | 25.7 | 26.1 | 1.55 | 1.55 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:35:00 | 2824.34 | 1855.46 | 825960.64 | 800135.7 | 33.76 | 2848.745 | 1579.356 | -731.159 | 37 | 184 | 26.1 | 55.8 | 26.7 | 55.5 | 0 | 0 | - | - | 28.8 | 49.9 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.7 | 1.52 | 2.2 | 1.3 | 0 | 25.9 | 27.1 | 26.7 | 1.51 | 2.1 | 1.5 | 25.7 | 25.7 | 26.1 | 1.55 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:40:00 | 2824.34 | 1912.5 | 825960.64 | 800194.16 | 33.86 | 2893.026 | 1535.073 | -759.786 | 36 | 184 | 26.1 | 55.8 | 26.7 | 55.4 | 0 | 0 | - | - | 28.8 | 49.8 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.7 | 1.52 | 2.2 | 1.3 | 0 | 25.9 | 27.1 | 26.8 | 1.51 | 2.1 | 1.5 | 25.7 | 25.7 | 26.1 | 1.54 | 1.54 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:45:00 | 2824.34 | 1981.98 | 825960.64 | 800263.16 | 33.95 | 2974.206 | 1453.89 | -915.088 | 34 | 184 | 26.2 | 55.8 | 26.8 | 55.4 | 0 | 0 | - | - | 28.8 | 50 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.7 | 1.52 | 2.2 | 1.3 | 0 | 26 | 27.1 | 26.8 | 1.51 | 2.1 | 1.5 | 25.7 | 25.7 | 26.2 | 1.54 | 1.54 | 1.51 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:50:00 | 2824.34 | 2061.34 | 825960.64 | 800342.08 | 34.05 | 3048.007 | 1380.09 | -852.34 | 32 | 184 | 26.2 | 55.8 | 26.8 | 55.3 | 0 | 0 | - | - | 28.7 | 50 | 0 | 0 | 0 | 0 | 26.4 | 27.3 | 26.7 | 1.52 | 2.2 | 1.3 | 0 | 26 | 27.1 | 26.8 | 1.52 | 2.1 | 1.5 | 25.7 | 25.6 | 26.1 | 1.55 | 1.55 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 18:55:00 | 2824.34 | 2135.56 | 825960.64 | 800415.88 | 34.15 | 3129.192 | 1298.91 | -888.756 | 31 | 184 | 26.2 | 55.7 | 26.9 | 55.2 | 0 | 0 | - | - | 28.7 | 49.9 | 0 | 0 | 0 | 0 | 26.5 | 27.3 | 26.7 | 1.53 | 2.1 | 1.3 | 0 | 25.9 | 27.1 | 26.8 | 1.52 | 2 | 1.4 | 25.7 | 25.7 | 26.2 | 1.55 | 1.55 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:00:00 | 2824.34 | 2194.06 | 825960.64 | 800474.82 | 34.25 | 3166.092 | 1262.007 | -591.752 | 29 | 184 | 26.3 | 55.6 | 27 | 55.1 | 0 | 0 | - | - | 28.7 | 50 | 0 | 0 | 0 | 0 | 26.5 | 27.3 | 26.7 | 1.53 | 2.1 | 1.3 | 0 | 25.9 | 27.1 | 26.9 | 1.52 | 2 | 1.4 | 25.8 | 25.8 | 26.2 | 1.55 | 1.55 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:05:00 | 2824.34 | 2244.1 | 825960.64 | 800524.78 | 34.34 | 3225.132 | 1202.964 | -569.792 | 28 | 184 | 26.4 | 55.6 | 27 | 55 | 0 | 0 | - | - | 28.8 | 50 | 0 | 0 | 0 | 0 | 26.5 | 27.3 | 26.7 | 1.53 | 2.1 | 1.2 | 0 | 26 | 27.1 | 26.8 | 1.52 | 1.9 | 1.3 | 25.9 | 25.8 | 26.3 | 1.55 | 1.55 | 1.52 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:10:00 | 2824.34 | 2288.16 | 825960.64 | 800568.78 | 34.44 | 3262.032 | 1166.064 | -544.427 | 27 | 184 | 26.4 | 55.6 | 27.1 | 54.9 | 0 | 0 | - | - | 28.8 | 49.9 | 0 | 0 | 0 | 0 | 26.6 | 27.4 | 26.8 | 1.53 | 2.1 | 1.2 | 0 | 26 | 27.2 | 26.9 | 1.52 | 1.9 | 1.3 | 26 | 25.9 | 26.3 | 1.56 | 1.56 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:15:00 | 2824.34 | 2333.74 | 825960.64 | 800614.9 | 34.53 | 3328.455 | 1099.644 | -655.416 | 26 | 184 | 26.5 | 55.5 | 27.1 | 54.9 | 0 | 0 | - | - | 28.7 | 50 | 0 | 0 | 0 | 0 | 26.6 | 27.4 | 26.8 | 1.54 | 2.1 | 1.2 | 0 | 26 | 27.2 | 26.9 | 1.53 | 1.8 | 1.3 | 26.1 | 26.1 | 26.2 | 1.56 | 1.56 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:20:00 | 2824.34 | 2383.52 | 825960.64 | 800664.46 | 34.62 | 3394.878 | 1033.22 | -566.595 | 25 | 184 | 26.5 | 55.5 | 27.1 | 54.8 | 0 | 0 | - | - | 28.8 | 50 | 0 | 0 | 0 | 0 | 26.6 | 27.4 | 26.7 | 1.54 | 2 | 1.2 | 0 | 26 | 27.2 | 26.9 | 1.53 | 1.8 | 1.2 | 26.2 | 26.2 | 26.2 | 1.56 | 1.56 | 1.53 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:25:00 | 2824.34 | 2430.06 | 825960.64 | 800711.42 | 34.71 | 3439.158 | 988.938 | -580.656 | 24 | 184 | 26.5 | 55.5 | 27.2 | 54.8 | 0 | 0 | - | - | 28.8 | 50 | 0 | 0 | 0 | 0 | 26.6 | 27.4 | 26.7 | 1.54 | 1.9 | 1.1 | 0 | 26 | 27.2 | 26.9 | 1.54 | 1.6 | 1.1 | 26.3 | 26.4 | 26.1 | 1.56 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:30:00 | 2824.34 | 2479.02 | 825960.64 | 800760.24 | 34.8 | 3490.818 | 937.278 | -523.858 | 22 | 184 | 26.5 | 55.6 | 27.2 | 54.9 | 0 | 0 | - | - | 28.8 | 50 | 0 | 0 | 0 | 0 | 26.7 | 27.4 | 26.7 | 1.54 | 1.8 | 1.1 | 0 | 26 | 27.2 | 26.8 | 1.54 | 1.6 | 1.1 | 26.5 | 26.5 | 26.1 | 1.57 | 1.56 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:35:00 | 2824.34 | 2508.88 | 825960.64 | 800788.94 | 34.88 | 3520.339 | 907.758 | -199.246 | 22 | 184 | 26.5 | 55.6 | 27.3 | 54.9 | 0 | 0 | - | - | 28.8 | 50 | 0 | 0 | 0 | 0 | 26.8 | 27.4 | 26.7 | 1.55 | 1.8 | 1.2 | 0 | 26.1 | 27.2 | 26.9 | 1.54 | 1.5 | 1 | 26.7 | 26.6 | 26.1 | 1.57 | 1.57 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:40:00 | 2824.34 | 2526.62 | 825960.64 | 800806.64 | 34.96 | 3549.858 | 878.238 | -188.035 | 21 | 184 | 26.4 | 55.7 | 27.3 | 54.8 | 0 | 0 | - | - | 28.8 | 50.1 | 0 | 0 | 0 | 0 | 26.9 | 27.3 | 26.7 | 1.55 | 1.6 | 1.2 | 0 | 26.1 | 27.2 | 26.8 | 1.55 | 1.4 | 1 | 26.7 | 26.7 | 25.9 | 1.57 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:45:00 | 2824.34 | 2540.98 | 825960.64 | 800821.18 | 35.03 | 3557.238 | 870.858 | -279.527 | 21 | 184 | 26.4 | 55.8 | 27.4 | 54.7 | 0 | 0 | - | - | 28.8 | 50.1 | 0 | 0 | 0 | 0 | 27.1 | 27.4 | 26.7 | 1.55 | 1.6 | 1.3 | 0 | 26.2 | 27.2 | 26.8 | 1.55 | 1.3 | 0.9 | 26.8 | 26.8 | 26.1 | 1.58 | 1.58 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:50:00 | 2824.34 | 2560.46 | 825960.64 | 800840.46 | 35.25 | 3564.618 | 863.478 | -151.604 | 20 | 184 | 26.4 | 55.8 | 27.3 | 54.9 | 0 | 0 | - | - | 28.7 | 50.1 | 252 | 209 | 45.4 | 45 | 55.2 | 26.5 | 38.3 | 2.31 | 13.9 | 13.8 | 0 | 53 | 26.5 | 37.2 | 2.31 | 14 | 12.1 | 23.4 | 26.7 | 25.9 | 2.36 | 1.07 | 2.33 | 1.06 | 252 | 209 | 2400 | 2400
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 19:55:00 | 2824.34 | 2583.34 | 825960.64 | 800863.5 | 35.9 | 3601.521 | 826.578 | -237.031 | 20 | 184 | 26.3 | 55.8 | 27.2 | 54.9 | 0 | 0 | - | - | 28.7 | 50.2 | 247 | 202 | 51.9 | 51.9 | 64.9 | 23.9 | 40.7 | 2.28 | 9.7 | 24 | 49.9 | 68 | 24.1 | 44.1 | 2.5 | 9.4 | 24 | 22.1 | 23.9 | 26.4 | 2.36 | 1.12 | 2.55 | 1.14 | 247 | 202 | 2400 | 2400
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:00:00 | 2824.34 | 2616.02 | 825960.64 | 800896.38 | 36.54 | 3631.043 | 797.056 | -374.238 | 19 | 184 | 26.3 | 55.9 | 27 | 55.1 | 0 | 0 | - | - | 28.7 | 50.3 | 247 | 202 | 49.7 | 50 | 63.1 | 22.8 | 38.9 | 2.25 | 9.7 | 22.9 | 50 | 66.6 | 23.1 | 42.2 | 2.46 | 9.2 | 23.2 | 21.1 | 22.9 | 26.7 | 2.31 | 1.08 | 2.5 | 1.11 | 247 | 202 | 2400 | 2400
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:05:00 | 2824.34 | 2632.94 | 825960.64 | 800912.78 | 37.19 | 3660.563 | 767.534 | 26.452 | 19 | 184 | 26.2 | 55.8 | 26.8 | 55.1 | 0 | 0 | - | - | 28.7 | 50.4 | 247 | 202 | 50.2 | 50 | 62.9 | 22.4 | 38.9 | 2.25 | 9.5 | 22.7 | 50.5 | 66.5 | 22.6 | 42.2 | 2.46 | 9 | 23.2 | 20.6 | 22.4 | 26.7 | 2.31 | 1.07 | 2.49 | 1.1 | 247 | 202 | 2400 | 2400
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:10:00 | 2824.92 | 2636.3 | 825961.22 | 800916.26 | 37.84 | 3660.563 | 767.534 | -50.284 | 19 | 184 | 26.2 | 55.6 | 26.7 | 55.1 | 0 | 0 | - | - | 28.7 | 50.5 | 247 | 202 | 50.2 | 50.5 | 63.1 | 22.1 | 38.9 | 2.25 | 9.4 | 22.7 | 50.5 | 66.6 | 22.2 | 42.2 | 2.47 | 9 | 23.2 | 20.2 | 22.1 | 27 | 2.31 | 1.07 | 2.5 | 1.09 | 247 | 202 | 2400 | 2400
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:15:00 | 2824.92 | 2644.36 | 825961.22 | 800924.48 | 38.48 | 3660.563 | 767.534 | -150.16 | 18 | 184 | 26.1 | 55.5 | 26.6 | 55.1 | 0 | 0 | - | - | 28.6 | 50.5 | 247 | 202 | 50.7 | 50.5 | 62.7 | 21.7 | 38.7 | 2.24 | 9.3 | 22.7 | 50.5 | 66.6 | 21.9 | 42.2 | 2.46 | 8.9 | 23.3 | 19.9 | 21.7 | 26.8 | 2.3 | 1.06 | 2.5 | 1.08 | 247 | 202 | 2400 | 2400
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:20:00 | 2824.92 | 2650.48 | 825961.22 | 800930.4 | 39.1 | 3667.943 | 760.153 | -10.244 | 18 | 184 | 26.1 | 55.4 | 26.5 | 55 | 0 | 0 | - | - | 28.6 | 50.6 | 247 | 202 | 50.7 | 50.5 | 62.7 | 21.6 | 38.6 | 2.23 | 9.2 | 22.8 | 50.5 | 66.6 | 21.7 | 42.1 | 2.45 | 8.9 | 23.4 | 19.7 | 21.6 | 26.7 | 2.29 | 1.06 | 2.49 | 1.07 | 247 | 202 | 2400 | 2400
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:25:00 | 2824.94 | 2653.66 | 825961.24 | 800933.7 | 39.74 | 3675.323 | 752.773 | -58.079 | 18 | 184 | 26.1 | 55.2 | 26.5 | 55 | 0 | 0 | - | - | 28.6 | 50.6 | 247 | 202 | 50.7 | 51 | 62.7 | 21.2 | 38.6 | 2.24 | 9.1 | 22.7 | 51 | 66.6 | 21.4 | 42.1 | 2.46 | 8.8 | 23.4 | 19.4 | 21.3 | 26.8 | 2.3 | 1.05 | 2.49 | 1.07 | 247 | 202 | 2400 | 2400
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:30:00 | 2824.98 | 2657.58 | 825961.28 | 800937.48 | 40.39 | 3682.703 | 745.393 | -35.535 | 18 | 184 | 26 | 55.1 | 26.3 | 54.9 | 0 | 0 | - | - | 28.6 | 50.6 | 247 | 202 | 51.2 | 51 | 63.2 | 21.1 | 39 | 2.25 | 9.2 | 23 | 51 | 67 | 21.2 | 42.1 | 2.45 | 9 | 23.9 | 19.2 | 21.1 | 27.5 | 2.32 | 1.04 | 2.49 | 1.05 | 247 | 202 | 2400 | 2400
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:35:00 | 2824.98 | 2661.26 | 825961.28 | 800941.2 | 41.04 | 3682.703 | 745.393 | -86.381 | 18 | 184 | 26 | 54.9 | 26.3 | 54.8 | 0 | 0 | - | - | 28.6 | 50.6 | 247 | 0 | 51.3 | 51.2 | 63.3 | 20.8 | 39.1 | 2.26 | 8.5 | 22.8 | 51.2 | 65.8 | 20.7 | 40.4 | 2.02 | 27.7 | 30.3 | 19.3 | 20.8 | 27.6 | 2.33 | 1.06 | 2.12 | 0.46 | 247 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:40:00 | 2824.98 | 2668.34 | 825961.28 | 800948.24 | 41.4 | 3690.084 | 738.013 | -68.537 | 18 | 184 | 26 | 54.8 | 26.2 | 54.8 | 0 | 0 | - | - | 28.6 | 50.5 | 244 | 0 | 45.2 | 45.4 | 63.6 | 21.9 | 40.1 | 2.33 | 8.5 | 22.1 | 45.1 | 33.4 | 36.4 | 30.7 | 1.65 | 14.4 | 6.2 | 20.7 | 21.9 | 26.8 | 2.39 | 1.09 | 1.64 | 1.41 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:45:00 | 2825 | 2674.24 | 825961.3 | 800954.14 | 41.76 | 3704.844 | 723.253 | -16.797 | 18 | 184 | 26 | 54.8 | 26.1 | 54.9 | 0 | 0 | - | - | 28.5 | 50.5 | 244 | 0 | 45.6 | 45.4 | 63.9 | 22.3 | 40.4 | 2.34 | 8.6 | 22.2 | 45.6 | 32.4 | 44.2 | 27.8 | 1.43 | 21.7 | 10 | 21.1 | 22.3 | 27 | 2.4 | 1.1 | 1.43 | 1.44 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:50:00 | 2825.04 | 2681.66 | 825961.34 | 800961.5 | 42.12 | 3704.844 | 723.253 | -160.286 | 18 | 184 | 25.9 | 54.8 | 26.1 | 54.9 | 0 | 0 | - | - | 28.5 | 50.5 | 244 | 0 | 45.6 | 45.4 | 64 | 22.3 | 40.4 | 2.34 | 8.7 | 22.3 | 45.1 | 32.1 | 42.7 | 27.1 | 1.42 | 20.1 | 9.8 | 21.2 | 22.3 | 27.3 | 2.4 | 1.1 | 1.43 | 1.44 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 20:55:00 | 2825.04 | 2694.92 | 825961.34 | 800975.24 | 42.48 | 3712.224 | 715.873 | -169.751 | 17 | 184 | 25.9 | 54.8 | 26.1 | 54.9 | 0 | 0 | - | - | 28.5 | 50.5 | 244 | 0 | 45.1 | 44.9 | 63.6 | 22.2 | 40.2 | 2.33 | 8.6 | 22.1 | 45.2 | 31.7 | 41.1 | 26.8 | 1.42 | 18.5 | 9.5 | 21.1 | 22.3 | 27.3 | 2.39 | 1.1 | 1.43 | 1.44 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:00:00 | 2825.04 | 2707.86 | 825961.34 | 800987.8 | 42.85 | 3726.984 | 701.113 | -115.527 | 17 | 184 | 25.7 | 54.8 | 26 | 54.9 | 0 | 0 | - | - | 28.5 | 50.4 | 244 | 0 | 45.1 | 44.9 | 63.6 | 22.2 | 40.1 | 2.32 | 8.5 | 22.1 | 44.7 | 31.4 | 39.7 | 26.6 | 1.42 | 17.1 | 9.3 | 21.1 | 22.2 | 27.1 | 2.38 | 1.1 | 1.42 | 1.44 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:05:00 | 2825.04 | 2716.56 | 825961.34 | 800996.68 | 43.2 | 3741.744 | 686.352 | -94.385 | 17 | 184 | 25.7 | 54.8 | 25.9 | 54.9 | 0 | 0 | - | - | 28.5 | 50.4 | 244 | 0 | 44.6 | 44.9 | 63.5 | 22.2 | 40 | 2.32 | 8.6 | 22.1 | 44.7 | 31.2 | 38.7 | 26.3 | 1.42 | 16.2 | 9 | 21 | 22.2 | 26.6 | 2.38 | 1.1 | 1.42 | 1.43 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:10:00 | 2825.04 | 2721.7 | 825961.34 | 801001.7 | 43.56 | 3749.124 | 678.972 | -43.039 | 17 | 184 | 25.7 | 54.8 | 25.9 | 54.9 | 0 | 0 | - | - | 28.4 | 50.5 | 244 | 0 | 45.1 | 44.9 | 63.5 | 22.1 | 40.1 | 2.33 | 8.6 | 22.1 | 45.2 | 30.9 | 37.4 | 26.2 | 1.41 | 15.1 | 8.9 | 20.8 | 22.1 | 27.1 | 2.38 | 1.09 | 1.41 | 1.43 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:15:00 | 2825.06 | 2724.2 | 825961.36 | 801004.04 | 43.92 | 3749.124 | 678.972 | -39.351 | 17 | 184 | 25.6 | 54.8 | 25.7 | 55.1 | 0 | 0 | - | - | 28.4 | 50.5 | 244 | 0 | 45.6 | 45.9 | 63.8 | 21.9 | 40.3 | 2.34 | 8.7 | 22 | 45.7 | 30.6 | 35.8 | 26.2 | 1.4 | 13.6 | 8.8 | 20.8 | 21.9 | 27.8 | 2.4 | 1.09 | 1.41 | 1.42 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:20:00 | 2825.06 | 2729.62 | 825961.36 | 801009.62 | 44.28 | 3749.124 | 678.972 | -79.772 | 16 | 184 | 25.5 | 54.9 | 25.5 | 55.3 | 0 | 0 | - | - | 28.4 | 50.5 | 244 | 0 | 46.5 | 46.4 | 64.4 | 21.8 | 40.6 | 2.34 | 8.7 | 22.6 | 46.6 | 30.3 | 34.1 | 26.3 | 1.4 | 12 | 8.7 | 20.7 | 21.9 | 28.7 | 2.41 | 1.08 | 1.4 | 1.42 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:25:00 | 2825.06 | 2734.34 | 825961.36 | 801014.26 | 44.64 | 3756.504 | 671.592 | -38.871 | 16 | 184 | 25.4 | 54.8 | 25.5 | 55.3 | 0 | 0 | - | - | 28.4 | 50.5 | 244 | 0 | 45.9 | 45.4 | 64.1 | 21.7 | 40.2 | 2.33 | 8.7 | 22.5 | 45.6 | 30.2 | 32.7 | 26.4 | 1.39 | 10.7 | 8.6 | 20.6 | 21.8 | 28 | 2.39 | 1.08 | 1.4 | 1.42 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:30:00 | 2825.06 | 2737.64 | 825961.36 | 801017.52 | 45 | 3756.504 | 671.592 | 11.009 | 16 | 184 | 25.4 | 54.8 | 25.5 | 55.1 | 0 | 0 | - | - | 28.4 | 50.4 | 244 | 0 | 45.2 | 45.4 | 63.9 | 21.7 | 40.1 | 2.32 | 8.7 | 22.5 | 45 | 30.1 | 31.7 | 26.5 | 1.39 | 9.8 | 8.6 | 20.6 | 21.7 | 27.8 | 2.37 | 1.08 | 1.39 | 1.41 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:35:00 | 2830.06 | 2738.26 | 825966.44 | 801018.1 | 45.36 | 3756.504 | 671.592 | 30.199 | 16 | 184 | 25.4 | 54.7 | 25.5 | 55 | 0 | 0 | - | - | 28.3 | 50.4 | 244 | 0 | 45 | 44.9 | 63.7 | 21.6 | 40.1 | 2.31 | 8.5 | 22.4 | 44.9 | 29.9 | 31.2 | 26.6 | 1.38 | 9.3 | 8.6 | 20.4 | 21.6 | 27.6 | 2.37 | 1.08 | 1.39 | 1.41 | 244 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:40:00 | 2831.02 | 2740.48 | 825967.32 | 801020.36 | 45.52 | 3756.504 | 671.592 | -15.789 | 16 | 184 | 25.4 | 54.7 | 25.4 | 55 | 0 | 0 | - | - | 28.3 | 50.3 | 0 | 0 | 0 | 0 | 41.4 | 29.5 | 30.1 | 1.55 | 7.5 | 16 | 0 | 29.7 | 30.4 | 26.6 | 1.38 | 8.2 | 8.4 | 22.2 | 22.3 | 27.4 | 1.57 | 1.41 | 1.39 | 1.42 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:45:00 | 2834.42 | 2740.92 | 825970.88 | 801020.76 | 45.59 | 3749.124 | 678.972 | 102.231 | 16 | 184 | 25.4 | 54.7 | 25.3 | 55.3 | 0 | 0 | - | - | 28.3 | 50.3 | 0 | 0 | 0 | 0 | 29.9 | 35.8 | 28.7 | 1.46 | 12.7 | 6.5 | 0 | 29.5 | 29.6 | 26.8 | 1.4 | 6.9 | 7.9 | 23 | 22.9 | 27.7 | 1.48 | 1.46 | 1.4 | 1.44 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:50:00 | 2842.96 | 2740.92 | 825979.46 | 801020.76 | 45.66 | 3749.124 | 678.972 | 214.223 | 17 | 184 | 25.3 | 54.8 | 25.2 | 55.5 | 0 | 0 | - | - | 28.3 | 50.2 | 0 | 0 | 0 | 0 | 28.3 | 35.9 | 28.6 | 1.47 | 12.4 | 4.7 | 0 | 29.3 | 28.9 | 27 | 1.4 | 6.1 | 7.6 | 23.3 | 23.3 | 27.7 | 1.48 | 1.47 | 1.4 | 1.45 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 21:55:00 | 2847.76 | 2741.24 | 825984.06 | 801021.18 | 45.72 | 3741.744 | 686.352 | -109.98 | 17 | 184 | 25.3 | 54.9 | 25.4 | 55.2 | 0 | 0 | - | - | 28.3 | 50.2 | 0 | 0 | 0 | 0 | 27.7 | 35.9 | 28.2 | 1.47 | 12.3 | 3.8 | 0 | 29.1 | 28.7 | 27.2 | 1.41 | 5.7 | 7.2 | 23.4 | 23.4 | 27.6 | 1.49 | 1.48 | 1.41 | 1.45 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:00:00 | 2847.76 | 2751.96 | 825984.06 | 801032 | 45.79 | 3749.124 | 678.972 | -80.813 | 16 | 184 | 25.3 | 55 | 25.4 | 55.1 | 0 | 0 | - | - | 28.3 | 50.2 | 0 | 0 | 0 | 0 | 27.4 | 35.6 | 28.1 | 1.48 | 11.8 | 3.5 | 0 | 28.7 | 28.4 | 27.4 | 1.41 | 5.3 | 6.8 | 23.5 | 23.5 | 27.4 | 1.5 | 1.49 | 1.41 | 1.46 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:05:00 | 2847.76 | 2754.48 | 825984.06 | 801034.32 | 45.85 | 3712.224 | 715.873 | -8.607 | 16 | 184 | 25.3 | 55 | 25.4 | 55.1 | 0 | 0 | - | - | 28.3 | 50.1 | 0 | 0 | 0 | 0 | 27.4 | 35.6 | 28.1 | 1.48 | 11.8 | 3.5 | 0 | 28.7 | 28.4 | 27.4 | 1.41 | 5.3 | 6.8 | 23.6 | 23.5 | 27.2 | 1.5 | 1.49 | 1.42 | 1.46 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:10:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.037 | 16 | 184 | 25.2 | 55 | 25.4 | 55.1 | 0 | 0 | - | - | 28.2 | 50.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:15:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.035 | 16 | 184 | 25.2 | 55.1 | 25.4 | 55.2 | 0 | 0 | - | - | 28.1 | 50.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:20:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.027 | 16 | 184 | 25.2 | 55.1 | 25.4 | 55.1 | 0 | 0 | - | - | 27.9 | 50.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:25:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25.2 | 55.1 | 25.4 | 55.2 | 0 | 0 | - | - | 27.8 | 50.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:30:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25.2 | 55.2 | 25.4 | 55.2 | 0 | 0 | - | - | 27.7 | 50.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:35:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25.1 | 55.2 | 25.4 | 55.2 | 0 | 0 | - | - | 27.6 | 50.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:40:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25.1 | 55.2 | 25.4 | 55.2 | 0 | 0 | - | - | 27.5 | 51 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:45:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25.1 | 55.2 | 25.4 | 55.2 | 0 | 0 | - | - | 27.4 | 51.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:50:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25.1 | 55.3 | 25.4 | 55.3 | 0 | 0 | - | - | 27.3 | 51.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 22:55:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.3 | 25.3 | 55.2 | 0 | 0 | - | - | 27.3 | 51.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:00:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25.1 | 55.3 | 25.3 | 55.3 | 0 | 0 | - | - | 27.2 | 51.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:05:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.3 | 25.3 | 55.2 | 0 | 0 | - | - | 27.2 | 51.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:10:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.4 | 25.3 | 55.3 | 0 | 0 | - | - | 27.1 | 51.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:15:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.3 | 25.3 | 55.2 | 0 | 0 | - | - | 27.1 | 51.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:20:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.3 | 25.3 | 55.3 | 0 | 0 | - | - | 27 | 51.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:25:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.3 | 25.4 | 55.3 | 0 | 0 | - | - | 27 | 51.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:30:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.4 | 25.3 | 55.3 | 0 | 0 | - | - | 26.9 | 51.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:35:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.4 | 25.3 | 55.3 | 0 | 0 | - | - | 26.9 | 51.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:40:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.4 | 25.3 | 55.2 | 0 | 0 | - | - | 26.9 | 51.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:45:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.4 | 25.3 | 55.2 | 0 | 0 | - | - | 26.8 | 51.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:50:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.4 | 25.3 | 55.2 | 0 | 0 | - | - | 26.8 | 51.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-19/B19-ESS03 | 2026-06-02 23:55:00 | 2847.76 | 2754.88 | 825984.06 | 801034.72 | 45.9 | 3704.844 | 723.253 | -0.025 | 16 | 184 | 25 | 55.4 | 25.3 | 55.3 | 0 | 0 | - | - | 26.8 | 51.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -