## 5 minutes
Time range: | 2026-06-02 00:00:00 - 2026-06-02 23:59:59
Export time: | 2026-06-03 01:22:53
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge energy(kWh) | Total discharge energy(kWh) | Daily auxiliary power consumption(kWh) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge power(kW) | SOC(%) | Equivalent number of cycles | Battery cabin temperature 1(℃) | Battery cabin humidity 1(%) | Battery cabin temperature 2(℃) | Battery cabin humidity 2(%) | CO concentration 1(ppm) | CO concentration 2(ppm) | H2 concentration 1(ppm) | H2 concentration 2(ppm) | Control unit cabin temperature 1(℃) | Control unit cabin humidity 1(%) | Control status of EEV 1(step) | Control status of EEV 2(step) | Running status of outdoor fan 1(%) | Running status of outdoor fan 2(%) | Discharge temperature of compressor 1(℃) | Suction temperature of refrigerant system 1(℃) | Condenser outlet temperature of refrigerant system 1(℃) | Condenser outlet pressure of refrigerant system 1(Mpa) | Suction superheat degree of refrigerant system 1(℃) | Discharge superheat degree of compressor 1(℃) | Running status of outdoor fan 3(%) | Discharge temperature of compressor 2(℃) | Suction temperature of refrigerant system 2(℃) | Condenser outlet temperature of refrigerant system 2(℃) | Condenser outlet pressure of refrigerant system 2(Mpa) | Suction superheat degree of refrigerant system 2(℃) | Discharge superheat degree of compressor 2(℃) | Battery-side supply water temperature(℃) | Battery-side return water temperature(℃) | Air intake temperature(℃) | Discharge pressure of refrigerant system 1(Mpa) | Suction pressure of refrigerant system 1(Mpa) | Discharge pressure of refrigerant system 2(Mpa) | Suction pressure of refrigerant system 2(Mpa) | Running status of EEV 1(step) | Running status of EEV 2(step) | Compressor 1 running status(rpm) | Compressor 2 running status(rpm)
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:00:00 | 0 | 0 | 867661.56 | 841220.48 | 0 | 3801.906 | 670.92 | -217.237 | 16 | 193 | 25.6 | 54.7 | 25.9 | 54.7 | 0 | 0 | - | - | 29.3 | 50 | 0 | 0 | 0 | 0 | 28.1 | 30 | 27.8 | 1.49 | 5.6 | 3.7 | 0 | 27.7 | 29.7 | 27.7 | 1.51 | 5.2 | 3.4 | 24.3 | 24.2 | 27.2 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:05:00 | 0 | 17.12 | 867661.56 | 841236.38 | 0.1 | 3816.814 | 656.012 | -195.81 | 15 | 193 | 25.6 | 54.7 | 25.9 | 54.6 | 0 | 0 | - | - | 29.3 | 50 | 0 | 0 | 0 | 0 | 28.1 | 29.9 | 27.8 | 1.49 | 5.5 | 3.7 | 0 | 27.7 | 29.7 | 27.7 | 1.51 | 5.1 | 3.4 | 24.3 | 24.2 | 27.3 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:10:00 | 0 | 34.92 | 867661.56 | 841254.2 | 0.19 | 3846.63 | 626.196 | -127.826 | 15 | 193 | 25.6 | 54.8 | 25.9 | 54.7 | 0 | 0 | - | - | 29.3 | 50.1 | 0 | 0 | 0 | 0 | 28.1 | 29.8 | 27.9 | 1.49 | 5.5 | 3.8 | 0 | 27.7 | 29.7 | 27.8 | 1.51 | 5 | 3.3 | 24.4 | 24.2 | 27.3 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:15:00 | 0.48 | 39.52 | 867662.04 | 841258.7 | 0.27 | 3846.63 | 626.196 | 21.541 | 15 | 193 | 25.6 | 54.8 | 25.9 | 54.7 | 0 | 0 | - | - | 29.2 | 50 | 0 | 0 | 0 | 0 | 28.1 | 29.8 | 27.9 | 1.5 | 5.4 | 3.7 | 0 | 27.7 | 29.6 | 27.9 | 1.51 | 5 | 3.3 | 24.4 | 24.3 | 27.3 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:20:00 | 5.98 | 39.8 | 867667.8 | 841258.96 | 0.35 | 3846.63 | 626.196 | 164.914 | 15 | 193 | 25.6 | 54.8 | 25.9 | 54.7 | 0 | 0 | - | - | 29.2 | 50.1 | 0 | 0 | 0 | 0 | 28.2 | 29.8 | 27.9 | 1.49 | 5.3 | 3.8 | 0 | 27.7 | 29.5 | 27.9 | 1.51 | 4.9 | 3.4 | 24.4 | 24.3 | 27.3 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:25:00 | 22.62 | 39.8 | 867684.44 | 841258.96 | 0.44 | 3816.814 | 656.012 | 215.63 | 15 | 193 | 25.5 | 54.8 | 25.9 | 54.7 | 0 | 0 | - | - | 29.2 | 50.1 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 27.9 | 1.5 | 5.3 | 3.8 | 0 | 27.7 | 29.4 | 28 | 1.51 | 4.8 | 3.3 | 24.5 | 24.3 | 27.3 | 1.51 | 1.52 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:30:00 | 43.48 | 39.8 | 867705.48 | 841258.96 | 0.53 | 3801.906 | 670.92 | 230.58 | 16 | 193 | 25.5 | 54.9 | 25.9 | 54.7 | 0 | 0 | - | - | 29.2 | 50.1 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 27.9 | 1.49 | 5.2 | 3.8 | 0 | 27.7 | 29.3 | 28 | 1.51 | 4.7 | 3.3 | 24.5 | 24.3 | 27.3 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:35:00 | 56.78 | 39.8 | 867718.42 | 841258.96 | 0.61 | 3801.906 | 670.92 | 85.81 | 16 | 193 | 25.5 | 54.9 | 25.9 | 54.8 | 0 | 0 | - | - | 29.1 | 50.1 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 28 | 1.5 | 5.3 | 3.9 | 0 | 27.7 | 29.3 | 28 | 1.51 | 4.7 | 3.4 | 24.5 | 24.3 | 27.4 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:40:00 | 61.48 | 39.84 | 867723.16 | 841259 | 0.7 | 3801.906 | 670.92 | 62.578 | 16 | 193 | 25.5 | 54.9 | 25.9 | 54.7 | 0 | 0 | - | - | 29.1 | 50.2 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 27.9 | 1.49 | 5.3 | 3.8 | 0 | 27.7 | 29.3 | 28.1 | 1.52 | 4.7 | 3.3 | 24.5 | 24.3 | 27.3 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:45:00 | 65.88 | 41.28 | 867727.44 | 841260.62 | 0.78 | 3794.451 | 678.375 | -86.716 | 16 | 194 | 25.5 | 54.9 | 25.9 | 54.8 | 0 | 0 | - | - | 29.1 | 50.2 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 27.9 | 1.5 | 5.3 | 3.8 | 0 | 27.7 | 29.3 | 28.1 | 1.52 | 4.6 | 3.3 | 24.5 | 24.3 | 27.2 | 1.51 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:50:00 | 67.2 | 43.66 | 867728.78 | 841262.82 | 0.87 | 3794.451 | 678.375 | 10.267 | 16 | 194 | 25.5 | 54.9 | 25.9 | 54.8 | 0 | 0 | - | - | 29 | 50.3 | 0 | 0 | 0 | 0 | 28.2 | 29.7 | 27.8 | 1.5 | 5.2 | 3.7 | 0 | 27.7 | 29.2 | 28 | 1.52 | 4.5 | 3.2 | 24.5 | 24.4 | 27.2 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 00:55:00 | 67.28 | 48.4 | 867728.84 | 841267.58 | 0.95 | 3801.906 | 670.92 | -51.497 | 16 | 194 | 25.6 | 54.9 | 25.9 | 54.8 | 0 | 0 | - | - | 29 | 50.2 | 0 | 0 | 0 | 0 | 28.1 | 29.6 | 27.8 | 1.5 | 5.1 | 3.6 | 0 | 27.6 | 29.2 | 27.9 | 1.52 | 4.5 | 3.1 | 24.5 | 24.4 | 27.2 | 1.51 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:00:00 | 67.64 | 52.5 | 867729.2 | 841271.68 | 1.03 | 3801.906 | 670.92 | -12.335 | 16 | 194 | 25.5 | 54.9 | 25.9 | 54.7 | 0 | 0 | - | - | 29 | 50.2 | 0 | 0 | 0 | 0 | 27.9 | 29.4 | 27.7 | 1.5 | 5 | 3.5 | 0 | 27.4 | 29.1 | 27.8 | 1.52 | 4.3 | 3 | 24.5 | 24.4 | 27 | 1.52 | 1.52 | 1.51 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:05:00 | 70.48 | 53.26 | 867732.08 | 841272.42 | 1.12 | 3801.906 | 670.92 | -35.486 | 16 | 194 | 25.5 | 54.9 | 25.9 | 54.7 | 0 | 0 | - | - | 29 | 50.3 | 0 | 0 | 0 | 0 | 27.8 | 29.3 | 27.6 | 1.5 | 4.8 | 3.4 | 0 | 27.4 | 28.9 | 27.8 | 1.52 | 4.2 | 2.9 | 24.6 | 24.4 | 26.9 | 1.51 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:10:00 | 71.06 | 57.42 | 867732.62 | 841276.74 | 1.2 | 3801.906 | 670.92 | -50.087 | 16 | 194 | 25.6 | 54.9 | 25.9 | 54.8 | 0 | 0 | - | - | 29 | 50.3 | 0 | 0 | 0 | 0 | 27.8 | 29.2 | 27.6 | 1.5 | 4.7 | 3.3 | 0 | 27.3 | 28.9 | 27.7 | 1.52 | 4.1 | 2.8 | 24.6 | 24.4 | 26.9 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:15:00 | 71.24 | 66.72 | 867732.84 | 841285.88 | 1.29 | 3801.906 | 670.92 | -51.175 | 16 | 194 | 25.6 | 54.9 | 25.9 | 54.8 | 0 | 0 | - | - | 28.9 | 50.3 | 0 | 0 | 0 | 0 | 27.7 | 29.2 | 27.6 | 1.5 | 4.6 | 3.3 | 0 | 27.2 | 28.7 | 27.7 | 1.52 | 4 | 2.8 | 24.6 | 24.4 | 26.8 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:20:00 | 72.78 | 67.6 | 867734.44 | 841286.76 | 1.38 | 3801.906 | 670.92 | 29.253 | 16 | 194 | 25.6 | 54.9 | 25.9 | 54.7 | 0 | 0 | - | - | 28.9 | 50.3 | 0 | 0 | 0 | 0 | 27.7 | 29.1 | 27.6 | 1.5 | 4.5 | 3.2 | 0 | 27.2 | 28.7 | 27.7 | 1.52 | 4 | 2.8 | 24.6 | 24.4 | 26.9 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:25:00 | 74.5 | 70.66 | 867736.06 | 841289.92 | 1.46 | 3801.906 | 670.92 | -40.426 | 16 | 194 | 25.6 | 54.9 | 26 | 54.7 | 0 | 0 | - | - | 28.9 | 50.4 | 0 | 0 | 0 | 0 | 27.7 | 29.1 | 27.6 | 1.5 | 4.5 | 3.3 | 0 | 27.2 | 28.7 | 27.7 | 1.52 | 3.9 | 2.7 | 24.6 | 24.4 | 26.9 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:30:00 | 74.7 | 74 | 867736.26 | 841293.22 | 1.55 | 3801.906 | 670.92 | -59.532 | 16 | 194 | 25.6 | 54.9 | 26 | 54.7 | 0 | 0 | - | - | 28.9 | 50.4 | 0 | 0 | 0 | 0 | 27.7 | 28.9 | 27.6 | 1.5 | 4.4 | 3.2 | 0 | 27.2 | 28.7 | 27.7 | 1.52 | 3.9 | 2.7 | 24.6 | 24.5 | 26.9 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:35:00 | 74.7 | 79.12 | 867736.26 | 841298.32 | 1.64 | 3801.906 | 670.92 | -37.106 | 16 | 194 | 25.6 | 54.9 | 26 | 54.8 | 0 | 0 | - | - | 28.9 | 50.4 | 0 | 0 | 0 | 0 | 27.7 | 28.9 | 27.6 | 1.5 | 4.4 | 3.2 | 0 | 27.2 | 28.7 | 27.7 | 1.52 | 3.8 | 2.7 | 24.7 | 24.5 | 26.9 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:40:00 | 74.7 | 82.9 | 867736.26 | 841302.12 | 1.73 | 3801.906 | 670.92 | -24.503 | 16 | 194 | 25.7 | 54.9 | 26 | 54.7 | 0 | 0 | - | - | 28.8 | 50.5 | 0 | 0 | 0 | 0 | 27.8 | 28.9 | 27.7 | 1.5 | 4.4 | 3.3 | 0 | 27.2 | 28.7 | 27.7 | 1.52 | 3.8 | 2.7 | 24.7 | 24.5 | 26.9 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:45:00 | 75.14 | 85.8 | 867736.7 | 841305.02 | 1.81 | 3801.906 | 670.92 | -39.54 | 16 | 194 | 25.7 | 54.9 | 26 | 54.8 | 0 | 0 | - | - | 28.8 | 50.4 | 0 | 0 | 0 | 0 | 27.8 | 28.9 | 27.7 | 1.5 | 4.3 | 3.3 | 0 | 27.3 | 28.7 | 27.7 | 1.52 | 3.8 | 2.7 | 24.7 | 24.5 | 27 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:50:00 | 75.7 | 89.32 | 867737.26 | 841308.6 | 1.9 | 3816.814 | 656.012 | -58.093 | 16 | 194 | 25.7 | 54.8 | 26 | 54.8 | 0 | 0 | - | - | 28.8 | 50.5 | 0 | 0 | 0 | 0 | 27.9 | 29 | 27.8 | 1.5 | 4.4 | 3.4 | 0 | 27.3 | 28.7 | 27.8 | 1.52 | 3.8 | 2.8 | 24.7 | 24.5 | 27 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 01:55:00 | 77.92 | 92.16 | 867739.68 | 841311.32 | 1.98 | 3816.814 | 656.012 | 184.017 | 16 | 194 | 25.7 | 54.8 | 26 | 54.7 | 0 | 0 | - | - | 28.8 | 50.5 | 0 | 0 | 0 | 0 | 27.9 | 28.9 | 27.8 | 1.5 | 4.3 | 3.4 | 0 | 27.3 | 28.7 | 27.8 | 1.52 | 3.7 | 2.8 | 24.7 | 24.6 | 27 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:00:00 | 86.78 | 95.2 | 867748.34 | 841314.68 | 2.08 | 3801.906 | 670.92 | -37.885 | 16 | 194 | 25.7 | 54.8 | 26 | 54.7 | 0 | 0 | - | - | 28.8 | 50.5 | 0 | 0 | 0 | 0 | 27.9 | 28.9 | 27.8 | 1.5 | 4.3 | 3.3 | 0 | 27.3 | 28.7 | 27.8 | 1.53 | 3.7 | 2.7 | 24.7 | 24.6 | 27 | 1.52 | 1.52 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:05:00 | 86.78 | 100.86 | 867748.34 | 841320.26 | 2.16 | 3816.814 | 656.012 | -50.85 | 15 | 194 | 25.7 | 54.8 | 26 | 54.7 | 0 | 0 | - | - | 28.8 | 50.5 | 0 | 0 | 0 | 0 | 27.9 | 28.9 | 27.7 | 1.5 | 4.3 | 3.3 | 0 | 27.3 | 28.6 | 27.8 | 1.53 | 3.7 | 2.7 | 24.7 | 24.6 | 26.9 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:10:00 | 87.12 | 103.42 | 867748.68 | 841322.66 | 2.25 | 3816.814 | 656.012 | -72.388 | 15 | 194 | 25.7 | 54.8 | 26.1 | 54.7 | 0 | 0 | - | - | 28.8 | 50.6 | 0 | 0 | 0 | 0 | 27.9 | 28.9 | 27.7 | 1.5 | 4.2 | 3.3 | 0 | 27.3 | 28.6 | 27.8 | 1.53 | 3.6 | 2.6 | 24.7 | 24.6 | 26.9 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:15:00 | 87.62 | 104.12 | 867749.18 | 841323.28 | 2.33 | 3816.814 | 656.012 | 1.802 | 15 | 194 | 25.8 | 54.8 | 26.1 | 54.7 | 0 | 0 | - | - | 28.8 | 50.5 | 0 | 0 | 0 | 0 | 27.8 | 28.8 | 27.7 | 1.5 | 4.1 | 3.2 | 0 | 27.2 | 28.6 | 27.8 | 1.53 | 3.6 | 2.6 | 24.7 | 24.6 | 26.9 | 1.52 | 1.53 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:20:00 | 88.94 | 105.08 | 867750.5 | 841324.28 | 2.42 | 3816.814 | 656.012 | -38.855 | 15 | 194 | 25.8 | 54.8 | 26.1 | 54.7 | 0 | 0 | - | - | 28.8 | 50.5 | 0 | 0 | 0 | 0 | 27.8 | 28.8 | 27.7 | 1.5 | 4.1 | 3.3 | 0 | 27.2 | 28.5 | 27.8 | 1.52 | 3.6 | 2.6 | 24.7 | 24.6 | 27 | 1.52 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:25:00 | 89.84 | 105.3 | 867751.48 | 841324.46 | 2.5 | 3786.996 | 685.83 | 51.788 | 15 | 194 | 25.8 | 54.8 | 26.1 | 54.8 | 0 | 0 | - | - | 28.7 | 50.6 | 0 | 0 | 0 | 0 | 27.8 | 28.8 | 27.7 | 1.5 | 4.2 | 3.2 | 0 | 27.2 | 28.4 | 27.8 | 1.53 | 3.5 | 2.6 | 24.7 | 24.6 | 27 | 1.52 | 1.52 | 1.52 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:30:00 | 96.34 | 105.44 | 867758.04 | 841324.6 | 2.58 | 3801.906 | 670.92 | 93.449 | 16 | 194 | 25.8 | 54.8 | 26.1 | 54.8 | 0 | 0 | - | - | 28.7 | 50.6 | 0 | 0 | 0 | 0 | 27.8 | 28.8 | 27.7 | 1.5 | 4.2 | 3.2 | 0 | 27.2 | 28.5 | 27.8 | 1.53 | 3.5 | 2.6 | 24.7 | 24.6 | 27 | 1.52 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:35:00 | 100.1 | 108.14 | 867761.66 | 841327.4 | 2.67 | 3801.906 | 670.92 | -121.823 | 16 | 194 | 25.8 | 54.8 | 26.1 | 54.7 | 0 | 0 | - | - | 28.7 | 50.6 | 0 | 0 | 0 | 0 | 27.8 | 28.8 | 27.8 | 1.5 | 4.2 | 3.3 | 0 | 27.2 | 28.4 | 27.8 | 1.53 | 3.5 | 2.6 | 24.8 | 24.6 | 27.1 | 1.52 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:40:00 | 100.72 | 110.72 | 867762.28 | 841329.98 | 2.75 | 3801.906 | 670.92 | 22.857 | 16 | 194 | 25.8 | 54.8 | 26.1 | 54.7 | 0 | 0 | - | - | 28.7 | 50.6 | 0 | 0 | 0 | 0 | 27.9 | 28.8 | 27.7 | 1.5 | 4.2 | 3.3 | 0 | 27.2 | 28.5 | 27.8 | 1.53 | 3.6 | 2.6 | 24.8 | 24.7 | 27.1 | 1.52 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:45:00 | 101.92 | 112.36 | 867763.48 | 841331.52 | 2.84 | 3801.906 | 670.92 | 10.575 | 16 | 194 | 25.8 | 54.8 | 26.1 | 54.7 | 0 | 0 | - | - | 28.7 | 50.6 | 0 | 0 | 0 | 0 | 27.8 | 28.8 | 27.7 | 1.5 | 4.1 | 3.3 | 0 | 27.2 | 28.5 | 27.8 | 1.53 | 3.5 | 2.6 | 24.8 | 24.7 | 26.9 | 1.52 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:50:00 | 104.82 | 112.36 | 867766.52 | 841331.52 | 2.92 | 3801.906 | 670.92 | 25.242 | 16 | 194 | 25.8 | 54.8 | 26.1 | 54.7 | 0 | 0 | - | - | 28.7 | 50.6 | 0 | 0 | 0 | 0 | 27.9 | 28.8 | 27.7 | 1.5 | 4.2 | 3.3 | 0 | 27.2 | 28.4 | 27.8 | 1.53 | 3.5 | 2.6 | 24.8 | 24.7 | 27 | 1.52 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 02:55:00 | 107.72 | 112.9 | 867769.28 | 841332.06 | 3.01 | 3801.906 | 670.92 | -7.821 | 16 | 194 | 25.8 | 54.8 | 26.1 | 54.8 | 0 | 0 | - | - | 28.7 | 50.6 | 0 | 0 | 0 | 0 | 27.8 | 28.7 | 27.7 | 1.51 | 4.1 | 3.2 | 0 | 27.2 | 28.4 | 27.8 | 1.53 | 3.5 | 2.5 | 24.8 | 24.7 | 26.9 | 1.52 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:00:00 | 107.86 | 116.72 | 867769.48 | 841335.96 | 3.09 | 3801.906 | 670.92 | -21.709 | 16 | 194 | 25.8 | 54.8 | 26.1 | 54.8 | 0 | 0 | - | - | 28.7 | 50.7 | 0 | 0 | 0 | 0 | 27.8 | 28.7 | 27.7 | 1.51 | 4 | 3.1 | 0 | 27.2 | 28.3 | 27.8 | 1.53 | 3.4 | 2.5 | 24.8 | 24.7 | 27 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:05:00 | 107.92 | 121.4 | 867769.48 | 841340.68 | 3.18 | 3816.814 | 656.012 | -58.62 | 16 | 194 | 25.8 | 54.8 | 26.1 | 54.8 | 0 | 0 | - | - | 28.7 | 50.7 | 0 | 0 | 0 | 0 | 27.8 | 28.7 | 27.7 | 1.51 | 4 | 3.2 | 0 | 27.2 | 28.3 | 27.8 | 1.53 | 3.4 | 2.5 | 24.8 | 24.7 | 26.8 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:10:00 | 109.12 | 124.26 | 867770.68 | 841343.7 | 3.32 | 3816.814 | 656.012 | -163.407 | 15 | 194 | 25.8 | 54.8 | 26.1 | 54.7 | 0 | 0 | - | - | 28.7 | 50.7 | 0 | 0 | 0 | 0 | 27.6 | 28.6 | 27.6 | 1.51 | 3.7 | 2.7 | 0 | 27.1 | 28.3 | 27.7 | 1.53 | 3.2 | 2.2 | 24.8 | 24.7 | 26.6 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:15:00 | 109.12 | 130.7 | 867770.68 | 841350.12 | 3.4 | 3839.176 | 633.65 | -113.682 | 15 | 194 | 25.8 | 54.8 | 26.1 | 54.8 | 0 | 0 | - | - | 28.7 | 50.6 | 0 | 0 | 0 | 0 | 27.3 | 28.4 | 27.4 | 1.51 | 3.6 | 2.6 | 0 | 26.8 | 28.2 | 27.7 | 1.53 | 3.1 | 2.1 | 24.8 | 24.7 | 26.8 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:20:00 | 109.12 | 142.2 | 867770.68 | 841361.54 | 3.49 | 3846.63 | 626.196 | -123.048 | 15 | 194 | 25.8 | 54.9 | 26.1 | 54.8 | 0 | 0 | - | - | 28.6 | 50.7 | 0 | 0 | 0 | 0 | 27.3 | 28.3 | 27.4 | 1.51 | 3.5 | 2.6 | 0 | 26.8 | 28.2 | 27.6 | 1.53 | 3.1 | 2 | 24.9 | 24.7 | 26.8 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:25:00 | 109.12 | 156.48 | 867770.68 | 841375.86 | 3.57 | 3846.63 | 626.196 | -69.684 | 15 | 194 | 25.8 | 54.8 | 26.1 | 54.8 | 0 | 0 | - | - | 28.6 | 50.8 | 0 | 0 | 0 | 0 | 27.4 | 28.4 | 27.5 | 1.51 | 3.6 | 2.7 | 0 | 26.8 | 28.2 | 27.6 | 1.53 | 3 | 2.1 | 24.9 | 24.8 | 26.8 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:30:00 | 109.76 | 159.72 | 867771.32 | 841378.9 | 3.66 | 3846.63 | 626.196 | -77.131 | 15 | 194 | 25.8 | 54.9 | 26.1 | 54.8 | 0 | 0 | - | - | 28.6 | 50.8 | 0 | 0 | 0 | 0 | 27.5 | 28.4 | 27.6 | 1.51 | 3.6 | 2.8 | 0 | 26.9 | 28.2 | 27.6 | 1.53 | 3 | 2.1 | 24.9 | 24.8 | 26.9 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:35:00 | 111.92 | 160.86 | 867773.6 | 841380.02 | 3.74 | 3846.63 | 626.196 | 56.8 | 15 | 194 | 25.8 | 54.9 | 26.1 | 54.8 | 0 | 0 | - | - | 28.6 | 50.8 | 0 | 0 | 0 | 0 | 27.6 | 28.4 | 27.6 | 1.51 | 3.6 | 2.8 | 0 | 27 | 28.2 | 27.6 | 1.53 | 3 | 2.2 | 24.9 | 24.8 | 26.8 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:40:00 | 114.06 | 163.66 | 867775.62 | 841382.9 | 3.82 | 3846.63 | 626.196 | -34.946 | 15 | 194 | 25.8 | 54.9 | 26.1 | 54.9 | 0 | 0 | - | - | 28.5 | 50.8 | 0 | 0 | 0 | 0 | 27.6 | 28.5 | 27.6 | 1.51 | 3.7 | 2.9 | 0 | 26.9 | 28.2 | 27.6 | 1.54 | 3 | 2.2 | 24.9 | 24.8 | 26.9 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:45:00 | 115.86 | 165.98 | 867777.54 | 841385.14 | 3.91 | 3846.63 | 626.196 | 140.946 | 15 | 194 | 25.8 | 55 | 26 | 54.9 | 0 | 0 | - | - | 28.5 | 50.9 | 0 | 0 | 0 | 0 | 27.6 | 28.5 | 27.6 | 1.51 | 3.7 | 2.9 | 0 | 27 | 28.2 | 27.7 | 1.53 | 3 | 2.1 | 25 | 24.8 | 26.9 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:50:00 | 118.62 | 166.62 | 867780.18 | 841385.8 | 3.99 | 3846.63 | 626.196 | -10.628 | 15 | 194 | 25.8 | 55 | 25.8 | 55.3 | 0 | 0 | - | - | 28.5 | 50.9 | 0 | 0 | 0 | 0 | 27.6 | 28.5 | 27.6 | 1.51 | 3.7 | 2.9 | 0 | 27 | 28.2 | 27.7 | 1.53 | 3 | 2.2 | 25 | 24.8 | 26.9 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 03:55:00 | 119.3 | 167.38 | 867780.86 | 841386.62 | 4.07 | 3846.63 | 626.196 | -18.178 | 15 | 194 | 25.7 | 55.1 | 25.7 | 55.4 | 0 | 0 | - | - | 28.5 | 50.9 | 0 | 0 | 0 | 0 | 27.6 | 28.4 | 27.6 | 1.51 | 3.6 | 2.9 | 0 | 27 | 28.2 | 27.7 | 1.53 | 3 | 2.2 | 25 | 24.8 | 26.9 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:00:00 | 119.52 | 168.82 | 867781.08 | 841387.98 | 4.15 | 3846.63 | 626.196 | -3.18 | 15 | 194 | 25.7 | 55.1 | 25.9 | 55.2 | 0 | 0 | - | - | 28.5 | 50.9 | 0 | 0 | 0 | 0 | 27.6 | 28.5 | 27.6 | 1.51 | 3.7 | 2.9 | 0 | 27 | 28.1 | 27.7 | 1.53 | 3 | 2.2 | 25 | 24.8 | 26.9 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:05:00 | 120.12 | 169.3 | 867781.68 | 841388.46 | 4.23 | 3846.63 | 626.196 | 3.023 | 15 | 194 | 25.7 | 55.1 | 26 | 55 | 0 | 0 | - | - | 28.5 | 51 | 0 | 0 | 0 | 0 | 27.6 | 28.4 | 27.6 | 1.51 | 3.6 | 2.9 | 0 | 27 | 28.1 | 27.7 | 1.54 | 3 | 2.2 | 25 | 24.8 | 26.9 | 1.53 | 1.53 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:10:00 | 122 | 169.48 | 867783.56 | 841388.66 | 4.31 | 3846.63 | 626.196 | -12.122 | 15 | 194 | 25.7 | 55.2 | 26 | 55 | 0 | 0 | - | - | 28.4 | 51 | 0 | 0 | 0 | 0 | 27.6 | 28.4 | 27.6 | 1.51 | 3.6 | 2.9 | 0 | 27 | 28.1 | 27.7 | 1.54 | 3 | 2.2 | 25 | 24.9 | 26.9 | 1.53 | 1.53 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:15:00 | 122.7 | 171.24 | 867784.32 | 841390.4 | 4.39 | 3846.63 | 626.196 | 28.083 | 15 | 194 | 25.6 | 55.3 | 26 | 55.1 | 0 | 0 | - | - | 28.4 | 51 | 0 | 0 | 0 | 0 | 27.6 | 28.4 | 27.6 | 1.51 | 3.6 | 2.9 | 0 | 27 | 28.1 | 27.7 | 1.54 | 3 | 2.2 | 25 | 24.8 | 27.1 | 1.53 | 1.53 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:20:00 | 124.5 | 173.34 | 867786.06 | 841392.54 | 4.48 | 3846.63 | 626.196 | -93.985 | 15 | 194 | 25.6 | 55.4 | 26 | 55.1 | 0 | 0 | - | - | 28.4 | 51.1 | 0 | 0 | 0 | 0 | 27.7 | 28.4 | 27.6 | 1.51 | 3.6 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.9 | 2.2 | 25 | 24.9 | 27 | 1.53 | 1.53 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:25:00 | 124.5 | 183.12 | 867786.06 | 841402.48 | 4.56 | 3861.54 | 611.286 | -126.491 | 14 | 194 | 25.6 | 55.4 | 26 | 55.2 | 0 | 0 | - | - | 28.4 | 51.1 | 0 | 0 | 0 | 0 | 27.7 | 28.4 | 27.6 | 1.51 | 3.6 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.9 | 2.2 | 25 | 24.9 | 27.1 | 1.53 | 1.53 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:30:00 | 124.5 | 190.12 | 867786.06 | 841409.62 | 4.64 | 3876.45 | 596.376 | -112.043 | 14 | 194 | 25.6 | 55.4 | 26 | 55.1 | 0 | 0 | - | - | 28.4 | 51.1 | 0 | 0 | 0 | 0 | 27.7 | 28.5 | 27.6 | 1.51 | 3.6 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.2 | 25.1 | 24.9 | 26.9 | 1.53 | 1.53 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:35:00 | 124.5 | 198.88 | 867786.06 | 841418.12 | 4.73 | 3891.36 | 581.466 | -76.337 | 14 | 194 | 25.6 | 55.4 | 26 | 55.1 | 0 | 0 | - | - | 28.3 | 51.1 | 0 | 0 | 0 | 0 | 27.7 | 28.5 | 27.6 | 1.51 | 3.6 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.2 | 25.1 | 24.9 | 26.9 | 1.53 | 1.53 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:40:00 | 126.06 | 203.14 | 867787.62 | 841422.44 | 4.81 | 3891.36 | 581.466 | -97.37 | 14 | 194 | 25.6 | 55.4 | 26 | 55.2 | 0 | 0 | - | - | 28.3 | 51.2 | 0 | 0 | 0 | 0 | 27.7 | 28.5 | 27.6 | 1.51 | 3.6 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.1 | 25.1 | 25 | 26.9 | 1.53 | 1.53 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:45:00 | 126.24 | 208.66 | 867787.8 | 841427.84 | 4.89 | 3891.36 | 581.466 | 38.306 | 14 | 194 | 25.6 | 55.5 | 26 | 55.1 | 0 | 0 | - | - | 28.3 | 51.2 | 0 | 0 | 0 | 0 | 27.7 | 28.4 | 27.6 | 1.51 | 3.6 | 2.8 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.1 | 25.1 | 25 | 26.9 | 1.53 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:50:00 | 131.64 | 208.74 | 867793.22 | 841427.9 | 4.97 | 3891.36 | 581.466 | 25.391 | 14 | 194 | 25.6 | 55.4 | 26 | 55.2 | 0 | 0 | - | - | 28.3 | 51.2 | 0 | 0 | 0 | 0 | 27.7 | 28.5 | 27.7 | 1.51 | 3.6 | 3 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.2 | 25.1 | 25 | 26.9 | 1.53 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 04:55:00 | 132.9 | 210.88 | 867794.48 | 841430.04 | 5.05 | 3891.36 | 581.466 | 15.337 | 14 | 194 | 25.6 | 55.5 | 26 | 55.1 | 0 | 0 | - | - | 28.3 | 51.3 | 0 | 0 | 0 | 0 | 27.7 | 28.5 | 27.7 | 1.51 | 3.6 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.2 | 25.1 | 25 | 26.9 | 1.53 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:00:00 | 133.86 | 214.18 | 867795.42 | 841433.46 | 5.14 | 3891.36 | 581.466 | -44.387 | 14 | 194 | 25.6 | 55.5 | 26 | 55.2 | 0 | 0 | - | - | 28.3 | 51.3 | 0 | 0 | 0 | 0 | 27.8 | 28.5 | 27.7 | 1.51 | 3.6 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.1 | 25.2 | 25 | 27 | 1.53 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:05:00 | 133.98 | 218.02 | 867795.54 | 841437.26 | 5.21 | 3891.36 | 581.466 | -114.658 | 14 | 194 | 25.6 | 55.5 | 26 | 55.2 | 0 | 0 | - | - | 28.3 | 51.3 | 0 | 0 | 0 | 0 | 27.8 | 28.5 | 27.7 | 1.51 | 3.6 | 3 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.2 | 25.2 | 25 | 27.1 | 1.53 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:10:00 | 133.98 | 227.02 | 867795.54 | 841446.44 | 5.3 | 3891.36 | 581.466 | -128.401 | 14 | 194 | 25.6 | 55.5 | 26 | 55.2 | 0 | 0 | - | - | 28.3 | 51.4 | 0 | 0 | 0 | 0 | 27.8 | 28.5 | 27.7 | 1.51 | 3.6 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.1 | 25.2 | 25 | 27.1 | 1.53 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:15:00 | 133.98 | 235.18 | 867795.54 | 841454.46 | 5.38 | 3891.36 | 581.466 | -1.726 | 14 | 194 | 25.6 | 55.5 | 26 | 55.2 | 0 | 0 | - | - | 28.3 | 51.4 | 0 | 0 | 0 | 0 | 27.7 | 28.5 | 27.7 | 1.52 | 3.6 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.2 | 25.2 | 25.1 | 27.1 | 1.53 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:20:00 | 133.98 | 243.58 | 867795.54 | 841462.82 | 5.46 | 3913.725 | 559.101 | -197.486 | 13 | 194 | 25.6 | 55.5 | 26.1 | 55.2 | 0 | 0 | - | - | 28.3 | 51.4 | 0 | 0 | 0 | 0 | 27.7 | 28.5 | 27.7 | 1.51 | 3.6 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.1 | 25.2 | 25.1 | 27.1 | 1.53 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:25:00 | 133.98 | 261.14 | 867795.54 | 841480.42 | 5.55 | 3936.09 | 536.736 | -141.916 | 13 | 194 | 25.6 | 55.5 | 26 | 55.3 | 0 | 0 | - | - | 28.2 | 51.4 | 0 | 0 | 0 | 0 | 27.8 | 28.5 | 27.7 | 1.51 | 3.6 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.8 | 2.1 | 25.3 | 25.1 | 27.1 | 1.54 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:30:00 | 133.98 | 275.62 | 867795.54 | 841494.88 | 5.63 | 3936.09 | 536.736 | -210.42 | 13 | 194 | 25.6 | 55.5 | 26.1 | 55.3 | 0 | 0 | - | - | 28.2 | 51.4 | 0 | 0 | 0 | 0 | 27.8 | 28.5 | 27.7 | 1.52 | 3.5 | 2.9 | 0 | 27.1 | 28.1 | 27.7 | 1.54 | 2.7 | 2.1 | 25.3 | 25.2 | 27.1 | 1.54 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:35:00 | 133.98 | 292.94 | 867795.54 | 841512.66 | 5.71 | 3951 | 521.826 | -267.048 | 12 | 194 | 25.6 | 55.5 | 26 | 55.3 | 0 | 0 | - | - | 28.3 | 51.4 | 0 | 0 | 0 | 0 | 27.9 | 28.5 | 27.8 | 1.52 | 3.5 | 2.9 | 0 | 27.2 | 28.1 | 27.7 | 1.55 | 2.7 | 2.1 | 25.3 | 25.2 | 27.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:40:00 | 145.16 | 303.14 | 867807.12 | 841522.3 | 5.8 | 3936.09 | 536.736 | 405.272 | 12 | 194 | 25.6 | 55.5 | 26.1 | 55.2 | 0 | 0 | - | - | 28.3 | 51.3 | 0 | 0 | 0 | 0 | 28 | 28.5 | 27.9 | 1.52 | 3.5 | 3 | 0 | 27.3 | 28.1 | 27.8 | 1.55 | 2.8 | 2.2 | 25.4 | 25.2 | 27.2 | 1.54 | 1.54 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:45:00 | 179.32 | 303.14 | 867841.72 | 841522.3 | 5.89 | 3936.09 | 536.736 | 387.213 | 13 | 194 | 25.7 | 55.5 | 26.1 | 55.3 | 0 | 0 | - | - | 28.3 | 51.4 | 0 | 0 | 0 | 0 | 28 | 28.6 | 27.8 | 1.52 | 3.5 | 3 | 0 | 27.2 | 28.2 | 27.8 | 1.55 | 2.7 | 2.1 | 25.4 | 25.2 | 27.2 | 1.54 | 1.54 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:50:00 | 203.96 | 303.14 | 867866.22 | 841522.3 | 5.97 | 3891.36 | 581.466 | 368.853 | 14 | 194 | 25.7 | 55.5 | 26.1 | 55.3 | 0 | 0 | - | - | 28.3 | 51.4 | 0 | 0 | 0 | 0 | 27.9 | 28.6 | 27.9 | 1.52 | 3.4 | 2.9 | 0 | 27.3 | 28.2 | 27.9 | 1.55 | 2.7 | 2.2 | 25.4 | 25.2 | 27.3 | 1.54 | 1.55 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 05:55:00 | 241.9 | 303.14 | 867903.76 | 841522.3 | 6.06 | 3846.63 | 626.196 | 239.683 | 15 | 194 | 25.7 | 55.5 | 26.2 | 55.2 | 0 | 0 | - | - | 28.3 | 51.4 | 0 | 0 | 0 | 0 | 28 | 28.6 | 27.9 | 1.52 | 3.4 | 2.9 | 0 | 27.3 | 28.2 | 27.9 | 1.55 | 2.7 | 2.2 | 25.4 | 25.3 | 27.4 | 1.54 | 1.55 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:00:00 | 254.08 | 305.74 | 867915.64 | 841526.04 | 6.15 | 3846.63 | 626.196 | -287.224 | 15 | 194 | 25.8 | 55.4 | 26.3 | 55.1 | 0 | 0 | - | - | 28.4 | 51.4 | 0 | 0 | 0 | 0 | 28.1 | 28.6 | 28 | 1.53 | 3.4 | 2.9 | 0 | 27.3 | 28.2 | 27.9 | 1.55 | 2.7 | 2.1 | 25.4 | 25.3 | 27.6 | 1.54 | 1.55 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:05:00 | 254.08 | 327.3 | 867915.64 | 841546.74 | 6.23 | 3891.36 | 581.466 | -171.455 | 14 | 194 | 25.8 | 55.4 | 26.3 | 55.1 | 0 | 0 | - | - | 28.4 | 51.3 | 0 | 0 | 0 | 0 | 28.1 | 28.6 | 28 | 1.53 | 3.4 | 2.9 | 0 | 27.3 | 28.2 | 27.9 | 1.55 | 2.7 | 2.1 | 25.5 | 25.3 | 28.1 | 1.55 | 1.55 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:10:00 | 254.4 | 335.18 | 867916.02 | 841554.34 | 6.31 | 3891.36 | 581.466 | 48.691 | 14 | 194 | 25.9 | 55.2 | 26.4 | 55 | 0 | 0 | - | - | 28.4 | 51.3 | 0 | 0 | 0 | 0 | 28 | 28.6 | 28 | 1.53 | 3.4 | 2.8 | 0 | 27.3 | 28.2 | 28.1 | 1.55 | 2.7 | 2.1 | 25.5 | 25.3 | 29.5 | 1.55 | 1.55 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:15:00 | 259.1 | 335.7 | 867920.66 | 841554.86 | 6.39 | 3891.36 | 581.466 | 50.374 | 14 | 194 | 26 | 55.2 | 26.5 | 54.9 | 0 | 0 | - | - | 28.5 | 51.2 | 0 | 0 | 0 | 0 | 28.1 | 28.7 | 28.1 | 1.53 | 3.4 | 2.9 | 0 | 27.4 | 28.2 | 28.2 | 1.55 | 2.7 | 2.1 | 25.5 | 25.3 | 29.2 | 1.55 | 1.55 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:20:00 | 267.02 | 335.7 | 867928.8 | 841554.86 | 6.47 | 3861.54 | 611.286 | 105.574 | 14 | 194 | 26.1 | 55.1 | 26.5 | 54.8 | 0 | 0 | - | - | 28.5 | 51.2 | 0 | 0 | 0 | 0 | 28.2 | 28.8 | 28.2 | 1.53 | 3.5 | 3 | 0 | 27.5 | 28.3 | 28.4 | 1.55 | 2.7 | 2.2 | 25.6 | 25.3 | 28.9 | 1.55 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:25:00 | 283.12 | 335.7 | 867945.04 | 841554.86 | 6.55 | 3846.63 | 626.196 | 241.889 | 15 | 194 | 26.2 | 55 | 26.6 | 54.9 | 0 | 0 | - | - | 28.6 | 51.2 | 0 | 0 | 0 | 0 | 28.3 | 28.8 | 28.4 | 1.53 | 3.6 | 3.1 | 0 | 27.6 | 28.4 | 28.5 | 1.55 | 2.9 | 2.3 | 25.6 | 25.4 | 28.7 | 1.55 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:30:00 | 299.38 | 335.7 | 867961.06 | 841554.86 | 6.64 | 3846.63 | 626.196 | 109.535 | 15 | 194 | 26.3 | 55 | 26.6 | 54.8 | 0 | 0 | - | - | 28.7 | 51.1 | 0 | 0 | 0 | 0 | 28.4 | 28.9 | 28.5 | 1.53 | 3.6 | 3.1 | 0 | 27.6 | 28.5 | 28.6 | 1.56 | 2.8 | 2.2 | 25.6 | 25.4 | 28.7 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:35:00 | 312.72 | 335.7 | 867974.44 | 841554.86 | 6.72 | 3824.268 | 648.558 | 168.899 | 15 | 194 | 26.3 | 54.9 | 26.6 | 54.8 | 0 | 0 | - | - | 28.7 | 51.1 | 0 | 0 | 0 | 0 | 28.5 | 29.1 | 28.6 | 1.53 | 3.7 | 3.2 | 0 | 27.7 | 28.6 | 28.7 | 1.56 | 2.9 | 2.4 | 25.6 | 25.4 | 28.8 | 1.55 | 1.56 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:40:00 | 333.26 | 335.7 | 867995.36 | 841554.86 | 6.81 | 3801.906 | 670.92 | 271.321 | 16 | 194 | 26.4 | 54.9 | 26.7 | 54.7 | 0 | 0 | - | - | 28.8 | 51 | 0 | 0 | 0 | 0 | 28.6 | 29.1 | 28.7 | 1.54 | 3.8 | 3.3 | 0 | 27.8 | 28.7 | 28.7 | 1.56 | 3 | 2.4 | 25.6 | 25.4 | 29.1 | 1.55 | 1.56 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:45:00 | 366.82 | 335.7 | 868029.24 | 841554.86 | 6.9 | 3757.176 | 715.65 | 421.617 | 17 | 194 | 26.4 | 54.8 | 26.7 | 54.7 | 0 | 0 | - | - | 28.9 | 50.9 | 0 | 0 | 0 | 0 | 28.7 | 29.3 | 28.9 | 1.54 | 3.9 | 3.4 | 0 | 27.9 | 28.8 | 28.9 | 1.56 | 3.1 | 2.5 | 25.6 | 25.4 | 31.6 | 1.55 | 1.56 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:50:00 | 403.66 | 335.7 | 868065.6 | 841554.86 | 6.99 | 3749.721 | 723.105 | 362.878 | 17 | 194 | 26.5 | 54.7 | 26.8 | 54.7 | 0 | 0 | - | - | 29.1 | 50.8 | 0 | 0 | 0 | 0 | 29 | 29.5 | 29.2 | 1.54 | 4.1 | 3.6 | 0 | 28.2 | 29 | 29.4 | 1.56 | 3.3 | 2.8 | 25.6 | 25.4 | 34 | 1.56 | 1.56 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 06:55:00 | 433.44 | 335.7 | 868095.48 | 841554.86 | 7.08 | 3712.446 | 760.38 | 306.145 | 18 | 194 | 26.7 | 54.5 | 27 | 54.5 | 0 | 0 | - | - | 29.5 | 50.6 | 0 | 0 | 0 | 0 | 29.3 | 29.8 | 29.6 | 1.54 | 4.3 | 3.9 | 0 | 28.5 | 29.3 | 30 | 1.56 | 3.5 | 3 | 25.6 | 25.4 | 35.4 | 1.56 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:00:00 | 442.58 | 335.98 | 868104.14 | 841555.3 | 7.16 | 3712.446 | 760.38 | -80.584 | 18 | 194 | 27 | 54.3 | 27.2 | 54.3 | 0 | 0 | - | - | 29.9 | 50.2 | 0 | 0 | 0 | 0 | 29.6 | 30 | 29.9 | 1.54 | 4.4 | 4.1 | 0 | 28.7 | 29.5 | 30.6 | 1.57 | 3.7 | 3.2 | 25.6 | 25.5 | 34.6 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:05:00 | 442.58 | 359.96 | 868104.14 | 841579.56 | 7.25 | 3712.446 | 760.38 | -488.1 | 18 | 194 | 27.2 | 53.9 | 27.3 | 54 | 0 | 0 | - | - | 30.4 | 49.8 | 0 | 0 | 0 | 0 | 29.7 | 30.2 | 30 | 1.54 | 4.6 | 4.2 | 0 | 28.9 | 29.7 | 30.9 | 1.57 | 3.8 | 3.3 | 25.7 | 25.5 | 34.4 | 1.56 | 1.57 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:10:00 | 442.58 | 420.82 | 868104.14 | 841641.42 | 7.35 | 3801.906 | 670.92 | -960.014 | 16 | 194 | 27.4 | 53.7 | 27.5 | 53.8 | 0 | 0 | - | - | 30.8 | 49.4 | 0 | 0 | 0 | 0 | 29.9 | 30.3 | 30.2 | 1.55 | 4.7 | 4.3 | 0 | 29 | 29.8 | 31.2 | 1.57 | 3.9 | 3.4 | 25.8 | 25.6 | 33.1 | 1.57 | 1.57 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:15:00 | 442.58 | 487.22 | 868104.14 | 841707.72 | 7.45 | 3801.906 | 670.92 | -653.423 | 16 | 194 | 27.6 | 53.5 | 27.6 | 53.8 | 0 | 0 | - | - | 31.1 | 49.1 | 0 | 0 | 0 | 0 | 29.9 | 30.3 | 30.2 | 1.55 | 4.7 | 4.3 | 0 | 29.1 | 29.9 | 31.2 | 1.58 | 3.9 | 3.4 | 25.8 | 25.7 | 32.1 | 1.57 | 1.57 | 1.57 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:20:00 | 444.22 | 511.34 | 868105.86 | 841730.5 | 7.54 | 3846.63 | 626.196 | 81.845 | 15 | 194 | 27.7 | 53.3 | 27.8 | 53.6 | 0 | 0 | - | - | 31.3 | 48.9 | 0 | 0 | 0 | 0 | 30 | 30.3 | 30.3 | 1.55 | 4.6 | 4.4 | 0 | 29.2 | 29.9 | 31.2 | 1.58 | 3.8 | 3.4 | 26 | 25.8 | 33.3 | 1.57 | 1.57 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:25:00 | 444.58 | 523.32 | 868106.14 | 841742.94 | 7.62 | 3846.63 | 626.196 | -591.192 | 15 | 194 | 27.9 | 53.2 | 27.9 | 53.5 | 0 | 0 | - | - | 31.6 | 48.7 | 0 | 0 | 0 | 0 | 30.2 | 30.4 | 30.3 | 1.55 | 4.6 | 4.4 | 0 | 29.3 | 30.1 | 31.3 | 1.58 | 3.9 | 3.4 | 26 | 25.9 | 33.1 | 1.57 | 1.57 | 1.58 | 1.59 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:30:00 | 444.58 | 560.2 | 868106.14 | 841779.92 | 7.72 | 3883.905 | 588.921 | -215.276 | 14 | 194 | 28 | 53.1 | 28 | 53.4 | 0 | 0 | - | - | 31.8 | 48.5 | 0 | 0 | 0 | 0 | 30.2 | 30.4 | 30.4 | 1.56 | 4.5 | 4.4 | 0 | 29.3 | 30.1 | 31.4 | 1.59 | 3.9 | 3.4 | 26.1 | 26 | 32.7 | 1.58 | 1.58 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:35:00 | 454.52 | 562.84 | 868116.32 | 841782 | 7.8 | 3846.63 | 626.196 | 239.364 | 14 | 194 | 28.1 | 53 | 28.1 | 53.4 | 0 | 0 | - | - | 31.9 | 48.5 | 0 | 0 | 0 | 0 | 30.3 | 30.3 | 30.5 | 1.55 | 4.5 | 4.4 | 0 | 29.5 | 30.1 | 31.4 | 1.58 | 3.9 | 3.5 | 26.2 | 26 | 33.9 | 1.58 | 1.58 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:40:00 | 470.34 | 562.84 | 868131.98 | 841782 | 7.88 | 3846.63 | 626.196 | 78.592 | 15 | 194 | 28.2 | 52.9 | 28.2 | 53.3 | 0 | 0 | - | - | 32.1 | 48.4 | 0 | 0 | 0 | 0 | 30.4 | 30.4 | 30.6 | 1.56 | 4.5 | 4.5 | 0 | 29.6 | 30.2 | 31.7 | 1.59 | 3.9 | 3.6 | 26.2 | 26.1 | 35.9 | 1.58 | 1.58 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:45:00 | 475 | 562.84 | 868136.92 | 841782 | 7.96 | 3846.63 | 626.196 | 185.871 | 15 | 194 | 28.4 | 52.7 | 28.3 | 53.2 | 0 | 0 | - | - | 32.4 | 48.2 | 0 | 0 | 0 | 0 | 30.6 | 30.6 | 31 | 1.56 | 4.7 | 4.7 | 0 | 29.8 | 30.4 | 32.1 | 1.59 | 4.1 | 3.8 | 26.2 | 26.1 | 37 | 1.58 | 1.58 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:50:00 | 502.18 | 562.84 | 868164.06 | 841782 | 8.05 | 3801.906 | 670.92 | 192.967 | 15 | 194 | 28.6 | 52.6 | 28.5 | 53 | 0 | 0 | - | - | 32.7 | 47.9 | 0 | 0 | 0 | 0 | 30.9 | 30.9 | 31.5 | 1.56 | 4.8 | 4.9 | 0 | 30.1 | 30.7 | 32.7 | 1.59 | 4.4 | 4.1 | 26.2 | 26.1 | 37.9 | 1.58 | 1.59 | 1.58 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 07:55:00 | 541.3 | 562.84 | 868203.56 | 841782 | 8.14 | 3801.906 | 670.92 | 313.607 | 16 | 194 | 28.7 | 52.4 | 28.7 | 52.8 | 0 | 0 | - | - | 33.2 | 47.7 | 0 | 0 | 0 | 0 | 31.3 | 31.2 | 31.8 | 1.57 | 5.1 | 5.2 | 0 | 30.4 | 31 | 33.1 | 1.59 | 4.6 | 4.4 | 26.2 | 26.1 | 38.6 | 1.59 | 1.59 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:00:00 | 555.02 | 567.52 | 868216.58 | 841787 | 8.23 | 3757.176 | 715.65 | -366.724 | 16 | 194 | 28.9 | 52.3 | 28.6 | 53 | 0 | 0 | - | - | 33.6 | 47.3 | 0 | 0 | 0 | 0 | 31.6 | 31.5 | 32.2 | 1.57 | 5.3 | 5.5 | 0 | 30.7 | 31.2 | 33.7 | 1.59 | 4.9 | 4.6 | 26.3 | 26.1 | 38.9 | 1.59 | 1.59 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:05:00 | 555.02 | 593.94 | 868216.58 | 841813.34 | 8.32 | 3801.906 | 670.92 | -246.709 | 16 | 194 | 29.1 | 52.1 | 28.7 | 52.9 | 0 | 0 | - | - | 34.1 | 47 | 0 | 0 | 0 | 0 | 31.9 | 31.7 | 32.5 | 1.57 | 5.5 | 5.8 | 0 | 30.9 | 31.4 | 34.1 | 1.59 | 5.1 | 4.9 | 26.3 | 26.2 | 39.8 | 1.59 | 1.59 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:10:00 | 555.02 | 613.46 | 868216.58 | 841832.68 | 8.4 | 3801.906 | 670.92 | -7.287 | 15 | 194 | 29.4 | 51.7 | 29.2 | 52.4 | 0 | 0 | - | - | 34.6 | 46.6 | 0 | 0 | 0 | 0 | 32.2 | 31.9 | 32.9 | 1.57 | 5.7 | 6 | 0 | 31.2 | 31.7 | 34.6 | 1.59 | 5.3 | 5.1 | 26.4 | 26.2 | 39.9 | 1.59 | 1.59 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:15:00 | 555.02 | 614.94 | 868216.58 | 841834.1 | 8.48 | 3801.906 | 670.92 | -2.171 | 15 | 194 | 29.8 | 51.4 | 29.5 | 52.1 | 0 | 0 | - | - | 35 | 46.3 | 0 | 0 | 0 | 0 | 32.5 | 32.2 | 33.3 | 1.57 | 6 | 6.3 | 0 | 31.5 | 32 | 35 | 1.59 | 5.5 | 5.4 | 26.4 | 26.2 | 39.9 | 1.59 | 1.6 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:20:00 | 555.02 | 622.84 | 868216.58 | 841842.38 | 8.56 | 3846.63 | 626.196 | -256.386 | 15 | 194 | 30 | 51.1 | 29.7 | 51.8 | 0 | 0 | - | - | 35.4 | 46 | 0 | 0 | 0 | 0 | 32.9 | 32.5 | 33.8 | 1.57 | 6.2 | 6.7 | 0 | 31.8 | 32.2 | 35.4 | 1.59 | 5.8 | 5.7 | 26.5 | 26.3 | 39.9 | 1.59 | 1.6 | 1.59 | 1.6 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:25:00 | 555.02 | 644.56 | 868216.58 | 841863.9 | 8.64 | 3846.63 | 626.196 | -116.671 | 15 | 194 | 30.5 | 50.6 | 30 | 51.5 | 0 | 0 | - | - | 35.8 | 45.7 | 0 | 0 | 0 | 0 | 33.1 | 32.6 | 34.1 | 1.57 | 6.3 | 6.9 | 0 | 32.1 | 32.4 | 35.6 | 1.59 | 5.9 | 5.9 | 26.5 | 26.3 | 38.7 | 1.59 | 1.6 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:30:00 | 556.72 | 650.48 | 868218.28 | 841870.14 | 8.71 | 3846.63 | 626.196 | -239.404 | 15 | 194 | 30.9 | 50.1 | 30.1 | 51.4 | 0 | 0 | - | - | 36.1 | 45.4 | 0 | 0 | 0 | 0 | 33.3 | 32.6 | 34.2 | 1.57 | 6.3 | 7 | 0 | 32.2 | 32.5 | 35.7 | 1.59 | 6 | 6 | 26.6 | 26.3 | 37.6 | 1.6 | 1.6 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:35:00 | 556.72 | 681.48 | 868218.28 | 841900.64 | 8.8 | 3891.36 | 581.466 | -253.842 | 14 | 194 | 30.8 | 50.2 | 30.3 | 51.3 | 0 | 0 | - | - | 36.2 | 45.3 | 0 | 0 | 0 | 0 | 33.4 | 32.6 | 34.2 | 1.57 | 6.2 | 7.1 | 0 | 32.4 | 32.6 | 35.7 | 1.6 | 6 | 6.2 | 26.6 | 26.4 | 36.9 | 1.6 | 1.6 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:40:00 | 556.72 | 694.12 | 868218.28 | 841913.32 | 8.88 | 3891.36 | 581.466 | -15.983 | 14 | 194 | 30.9 | 50.2 | 30.4 | 51.1 | 0 | 0 | - | - | 36.3 | 45.3 | 0 | 0 | 0 | 0 | 33.4 | 32.4 | 34.3 | 1.58 | 6.1 | 7.2 | 0 | 32.5 | 32.4 | 35.6 | 1.6 | 5.9 | 6.3 | 26.7 | 26.5 | 36.6 | 1.6 | 1.6 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:45:00 | 562 | 694.76 | 868224.1 | 841913.92 | 8.96 | 3891.36 | 581.466 | 254.199 | 14 | 194 | 31 | 50.1 | 30.6 | 51 | 0 | 0 | - | - | 36.3 | 45.3 | 0 | 0 | 0 | 0 | 33.4 | 32.4 | 34.3 | 1.58 | 6.1 | 7.2 | 0 | 32.6 | 32.4 | 35.6 | 1.6 | 5.7 | 6.4 | 26.7 | 26.5 | 36.9 | 1.6 | 1.6 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:50:00 | 587.66 | 694.76 | 868250.02 | 841913.92 | 9.04 | 3846.63 | 626.196 | 397.467 | 14 | 194 | 31.2 | 50 | 30.6 | 50.9 | 0 | 0 | - | - | 36.4 | 45.3 | 0 | 0 | 0 | 0 | 33.6 | 32.4 | 34.4 | 1.58 | 6 | 7.3 | 0 | 32.7 | 32.4 | 35.6 | 1.6 | 5.7 | 6.5 | 26.7 | 26.5 | 37.2 | 1.6 | 1.6 | 1.59 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 08:55:00 | 630.24 | 694.76 | 868292.88 | 841913.92 | 9.13 | 3801.906 | 670.92 | 604.641 | 15 | 194 | 31.3 | 49.8 | 30.8 | 50.9 | 0 | 0 | - | - | 36.5 | 45.3 | 0 | 0 | 0 | 0 | 33.6 | 32.4 | 34.5 | 1.58 | 6.1 | 7.4 | 0 | 32.9 | 32.4 | 35.7 | 1.6 | 5.7 | 6.6 | 26.7 | 26.6 | 38.2 | 1.6 | 1.6 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:00:00 | 680.02 | 694.76 | 868342.8 | 841913.92 | 9.23 | 3757.176 | 715.65 | 343.938 | 17 | 194 | 31.5 | 49.7 | 31 | 50.7 | 0 | 0 | - | - | 36.6 | 45.3 | 0 | 0 | 0 | 0 | 33.8 | 32.5 | 34.7 | 1.58 | 6.1 | 7.4 | 0 | 33 | 32.4 | 35.8 | 1.6 | 5.8 | 6.7 | 26.7 | 26.6 | 38.9 | 1.6 | 1.6 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:05:00 | 698.42 | 694.76 | 868360.02 | 841913.92 | 9.31 | 3757.176 | 715.65 | 26.463 | 17 | 194 | 31.8 | 49.5 | 31.2 | 50.5 | 0 | 0 | - | - | 36.9 | 45.1 | 0 | 0 | 0 | 0 | 33.9 | 32.5 | 34.9 | 1.58 | 6.1 | 7.6 | 0 | 33.2 | 32.5 | 36 | 1.6 | 5.9 | 6.9 | 26.8 | 26.6 | 38.6 | 1.6 | 1.6 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:10:00 | 699.92 | 699.72 | 868361.62 | 841918.88 | 9.39 | 3757.176 | 715.65 | 137.085 | 17 | 194 | 32.1 | 49.2 | 31.4 | 50.3 | 0 | 0 | - | - | 37 | 44.9 | 0 | 0 | 0 | 0 | 33.9 | 32.5 | 34.9 | 1.58 | 6.1 | 7.6 | 0 | 33.2 | 32.5 | 36.1 | 1.6 | 5.8 | 7 | 26.8 | 26.6 | 37.9 | 1.6 | 1.6 | 1.6 | 1.61 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:15:00 | 729.04 | 699.72 | 868391.58 | 841918.88 | 9.48 | 3757.176 | 715.65 | 657.624 | 17 | 194 | 32.3 | 49 | 31.6 | 50.1 | 0 | 0 | - | - | 37.2 | 44.8 | 0 | 0 | 0 | 0 | 34 | 32.5 | 35 | 1.58 | 6.1 | 7.6 | 0 | 33.4 | 32.5 | 36.2 | 1.6 | 5.8 | 7 | 26.8 | 26.7 | 39.1 | 1.6 | 1.61 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:20:00 | 784.92 | 699.72 | 868448.16 | 841918.88 | 9.58 | 3667.722 | 805.104 | 664.245 | 19 | 194 | 32.5 | 48.8 | 31.8 | 50.1 | 0 | 0 | - | - | 37.4 | 44.7 | 0 | 0 | 0 | 0 | 34.2 | 32.6 | 35.2 | 1.58 | 6.1 | 7.8 | 0 | 33.5 | 32.6 | 36.4 | 1.6 | 5.9 | 7.2 | 26.9 | 26.7 | 38.1 | 1.6 | 1.61 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:25:00 | 844.4 | 699.72 | 868506.22 | 841918.88 | 9.67 | 3622.992 | 849.834 | 506.744 | 20 | 194 | 32.7 | 48.7 | 31.9 | 49.9 | 0 | 0 | - | - | 37.6 | 44.5 | 0 | 0 | 0 | 0 | 34.2 | 32.6 | 35.1 | 1.58 | 6.1 | 7.9 | 0 | 33.6 | 32.6 | 36.4 | 1.6 | 5.9 | 7.2 | 26.9 | 26.7 | 36.9 | 1.6 | 1.61 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:30:00 | 878.62 | 699.72 | 868540.5 | 841918.88 | 9.76 | 3622.992 | 849.834 | 234.594 | 21 | 194 | 32.9 | 48.5 | 32.1 | 49.7 | 0 | 0 | - | - | 37.7 | 44.5 | 0 | 0 | 0 | 0 | 34.1 | 32.6 | 35.1 | 1.58 | 6 | 7.8 | 0 | 33.5 | 32.5 | 36.2 | 1.6 | 5.8 | 7.3 | 26.9 | 26.7 | 36.9 | 1.6 | 1.61 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:35:00 | 892.16 | 700.04 | 868553.72 | 841919.2 | 9.85 | 3578.262 | 894.564 | 14.02 | 21 | 194 | 33.1 | 48.3 | 32.3 | 49.6 | 0 | 0 | - | - | 37.7 | 44.5 | 0 | 0 | 0 | 0 | 34.2 | 32.6 | 35.1 | 1.58 | 6 | 7.9 | 0 | 33.6 | 32.5 | 36.2 | 1.6 | 5.8 | 7.3 | 27 | 26.8 | 37.7 | 1.6 | 1.61 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:40:00 | 892.32 | 713.94 | 868553.88 | 841933.2 | 9.94 | 3600.627 | 872.199 | -85.351 | 21 | 194 | 33.4 | 48.1 | 32.5 | 49.5 | 0 | 0 | - | - | 37.8 | 44.4 | 0 | 0 | 0 | 0 | 34.4 | 32.6 | 35.2 | 1.58 | 6 | 7.9 | 0 | 33.7 | 32.6 | 36.3 | 1.6 | 5.8 | 7.3 | 27 | 26.8 | 37.5 | 1.6 | 1.61 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:45:00 | 892.68 | 722.42 | 868554.24 | 841941.72 | 10.02 | 3622.992 | 849.834 | -76.092 | 21 | 194 | 33.5 | 47.9 | 32.6 | 49.4 | 0 | 0 | - | - | 37.9 | 44.4 | 0 | 0 | 0 | 0 | 34.2 | 32.6 | 35.1 | 1.58 | 6 | 7.8 | 0 | 33.6 | 32.6 | 36.2 | 1.6 | 5.8 | 7.3 | 27.1 | 26.9 | 36.6 | 1.6 | 1.61 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:50:00 | 892.68 | 740 | 868554.24 | 841959.62 | 10.11 | 3622.992 | 849.834 | -161.74 | 20 | 194 | 33.7 | 47.9 | 32.8 | 49.2 | 0 | 0 | - | - | 37.9 | 44.3 | 0 | 0 | 0 | 0 | 34.2 | 32.5 | 35.1 | 1.58 | 5.9 | 7.8 | 0 | 33.6 | 32.6 | 36.1 | 1.6 | 5.7 | 7.3 | 27.1 | 26.9 | 35.6 | 1.6 | 1.61 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 09:55:00 | 909.84 | 742.36 | 868572.44 | 841961.52 | 10.21 | 3622.992 | 849.834 | 557.381 | 20 | 194 | 33.8 | 47.8 | 32.9 | 49.2 | 0 | 0 | - | - | 37.9 | 44.4 | 0 | 0 | 0 | 0 | 34.2 | 32.4 | 34.9 | 1.58 | 5.8 | 7.7 | 0 | 33.6 | 32.4 | 35.9 | 1.6 | 5.6 | 7.2 | 27.2 | 27 | 35.1 | 1.6 | 1.61 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:00:00 | 938.96 | 742.36 | 868600.7 | 841961.52 | 10.3 | 3578.262 | 894.564 | 5.33 | 21 | 194 | 33.8 | 47.8 | 32.9 | 49.2 | 0 | 0 | - | - | 37.8 | 44.5 | 0 | 0 | 0 | 0 | 34.2 | 32.4 | 34.9 | 1.58 | 5.8 | 7.8 | 0 | 33.6 | 32.4 | 35.7 | 1.6 | 5.6 | 7.3 | 27.2 | 27 | 34.9 | 1.6 | 1.61 | 1.6 | 1.62 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:05:00 | 948.78 | 742.36 | 868610.94 | 841961.52 | 10.79 | 3578.262 | 894.564 | 389.013 | 21 | 194 | 33.9 | 47.7 | 33 | 49.1 | 0 | 0 | - | - | 37.7 | 44.6 | 255 | 228 | 60.2 | 60.2 | 65.4 | 26.1 | 43.6 | 2.53 | 11.9 | 20.6 | 60 | 67.6 | 26.1 | 45.7 | 2.74 | 11.6 | 20 | 23.1 | 25.4 | 33.4 | 2.59 | 1.12 | 2.77 | 1.13 | 255 | 228 | 2775 | 2775
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:10:00 | 980.32 | 742.36 | 868642.36 | 841961.52 | 11.64 | 3533.532 | 939.294 | 308.357 | 22 | 194 | 34 | 47.5 | 32.9 | 49.1 | 0 | 0 | - | - | 37.6 | 44.7 | 255 | 228 | 61 | 61 | 69.7 | 23.7 | 44 | 2.53 | 10.2 | 24.8 | 61.2 | 73.6 | 23.8 | 46.4 | 2.74 | 9.9 | 26 | 21.7 | 23.4 | 33.6 | 2.59 | 1.1 | 2.77 | 1.11 | 255 | 228 | 2656 | 2656
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:15:00 | 1013.36 | 742.36 | 868675.58 | 841961.52 | 12.38 | 3533.532 | 939.294 | 455.896 | 23 | 194 | 34.1 | 47.4 | 32.8 | 49 | 0 | 0 | - | - | 37.5 | 44.8 | 255 | 227 | 56.4 | 56.3 | 67.8 | 23.3 | 42.8 | 2.46 | 8.8 | 24.1 | 56.1 | 71.3 | 23.4 | 45.2 | 2.65 | 8.4 | 25.1 | 21.5 | 23.1 | 35.6 | 2.52 | 1.13 | 2.68 | 1.15 | 255 | 227 | 2163 | 2179
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:20:00 | 1061.2 | 742.36 | 868723.8 | 841961.52 | 13.01 | 3488.808 | 984.018 | 527.717 | 24 | 194 | 34.1 | 47.2 | 32.7 | 49 | 0 | 0 | - | - | 37.4 | 44.8 | 255 | 222 | 55 | 55.2 | 65.9 | 23.3 | 41.9 | 2.41 | 9 | 23 | 55 | 69.7 | 23.4 | 44.6 | 2.62 | 8.8 | 24 | 21.6 | 23.1 | 34.2 | 2.47 | 1.12 | 2.65 | 1.13 | 255 | 222 | 2142 | 2145
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:25:00 | 1097.5 | 742.36 | 868759.82 | 841961.52 | 13.65 | 3444.078 | 1028.748 | 371.623 | 25 | 194 | 34 | 47.1 | 32.7 | 48.9 | 0 | 0 | - | - | 37.4 | 44.9 | 255 | 222 | 55.5 | 55.7 | 66 | 23.2 | 42.1 | 2.41 | 9 | 23.1 | 55.5 | 69.7 | 23.3 | 44.7 | 2.62 | 8.8 | 24 | 21.3 | 22.8 | 34.1 | 2.47 | 1.12 | 2.65 | 1.13 | 255 | 222 | 2160 | 2160
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:30:00 | 1115.1 | 742.36 | 868776.7 | 841961.52 | 14.28 | 3444.078 | 1028.748 | 25.347 | 25 | 194 | 34.1 | 47 | 32.8 | 48.8 | 0 | 0 | - | - | 37.3 | 44.9 | 255 | 222 | 55.5 | 55.7 | 66 | 23.1 | 42.1 | 2.42 | 9 | 22.9 | 55.5 | 69.8 | 23.2 | 44.7 | 2.63 | 8.7 | 23.9 | 21.2 | 22.7 | 34.3 | 2.48 | 1.12 | 2.66 | 1.13 | 255 | 222 | 2140 | 2140
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:35:00 | 1125.32 | 742.36 | 868787 | 841961.52 | 14.89 | 3399.348 | 1073.478 | 80.713 | 25 | 194 | 34.2 | 46.8 | 32.8 | 48.7 | 0 | 0 | - | - | 37.4 | 44.8 | 255 | 220 | 55.5 | 55.2 | 65.9 | 22.9 | 42.5 | 2.44 | 8.5 | 22.6 | 55.2 | 69.5 | 23.1 | 44.7 | 2.62 | 8.4 | 23.8 | 21.2 | 22.6 | 35.7 | 2.5 | 1.13 | 2.65 | 1.13 | 255 | 220 | 2062 | 2068
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:40:00 | 1139.16 | 742.36 | 868800.78 | 841961.52 | 15.5 | 3399.348 | 1073.478 | 112.774 | 25 | 194 | 34.3 | 46.6 | 32.9 | 48.5 | 0 | 0 | - | - | 37.4 | 44.8 | 255 | 220 | 55.5 | 55.3 | 65.7 | 22.8 | 42.1 | 2.42 | 8.6 | 22.6 | 55.2 | 69.5 | 22.9 | 44.6 | 2.62 | 8.5 | 23.8 | 20.9 | 22.5 | 35.1 | 2.49 | 1.12 | 2.65 | 1.13 | 255 | 220 | 2097 | 2095
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:45:00 | 1141.76 | 749 | 868803.32 | 841968.68 | 16.11 | 3399.348 | 1073.478 | -182.225 | 25 | 194 | 34.4 | 46.5 | 32.9 | 48.4 | 0 | 0 | - | - | 37.5 | 44.7 | 255 | 220 | 55.5 | 55.3 | 65.8 | 22.7 | 42.1 | 2.4 | 8.7 | 22.9 | 55.7 | 69.4 | 22.7 | 44.6 | 2.61 | 8.6 | 23.7 | 20.8 | 22.3 | 34.9 | 2.47 | 1.11 | 2.64 | 1.12 | 255 | 220 | 2116 | 2116
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:50:00 | 1153.52 | 751.88 | 868815.68 | 841971.04 | 16.72 | 3399.348 | 1073.478 | 420.279 | 26 | 194 | 34.5 | 46.2 | 32.9 | 48.3 | 0 | 0 | - | - | 37.5 | 44.6 | 255 | 218 | 55.5 | 55.3 | 66 | 22.6 | 42.4 | 2.44 | 8.5 | 22.4 | 55.3 | 69.5 | 22.6 | 44.6 | 2.62 | 8.5 | 23.9 | 20.7 | 22.2 | 35.4 | 2.51 | 1.12 | 2.64 | 1.12 | 255 | 218 | 2076 | 2076
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 10:55:00 | 1189.52 | 751.88 | 868851.66 | 841971.04 | 17.34 | 3354.624 | 1118.208 | 275.035 | 26 | 194 | 34.4 | 46.2 | 32.8 | 48.2 | 0 | 0 | - | - | 37.5 | 44.5 | 255 | 217 | 55.5 | 55.3 | 65.6 | 22.4 | 42.2 | 2.43 | 8.5 | 22.2 | 55.1 | 69.5 | 22.4 | 44.5 | 2.61 | 8.6 | 23.9 | 20.6 | 22.1 | 35.2 | 2.5 | 1.11 | 2.64 | 1.11 | 255 | 217 | 2089 | 2089
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:00:00 | 1212.82 | 751.88 | 868876.28 | 841971.04 | 17.95 | 3354.624 | 1118.208 | 451.086 | 27 | 194 | 34.4 | 46.2 | 32.8 | 48.2 | 0 | 0 | - | - | 37.5 | 44.5 | 255 | 217 | 55.5 | 55.3 | 65.9 | 22.2 | 42.3 | 2.43 | 8.5 | 22.6 | 56.4 | 69.6 | 22.2 | 44.6 | 2.61 | 8.6 | 24.1 | 20.3 | 21.8 | 35 | 2.49 | 1.1 | 2.64 | 1.1 | 255 | 217 | 2094 | 2094
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:05:00 | 1279.6 | 751.88 | 868943.4 | 841971.04 | 18.58 | 3272.619 | 1200.207 | 870.608 | 28 | 194 | 34.3 | 46.1 | 32.7 | 48.1 | 0 | 0 | - | - | 37.4 | 44.4 | 254 | 217 | 55 | 55.3 | 65.8 | 22.1 | 41.9 | 2.4 | 8.7 | 23 | 55.1 | 69.7 | 22.2 | 44.4 | 2.6 | 8.7 | 24.2 | 20.2 | 21.7 | 34.2 | 2.46 | 1.09 | 2.63 | 1.09 | 254 | 217 | 2143 | 2143
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:10:00 | 1343.78 | 751.9 | 869005.36 | 841971.1 | 19.21 | 3220.434 | 1252.392 | -14.829 | 30 | 194 | 34.2 | 46 | 32.6 | 48.1 | 0 | 0 | - | - | 37.4 | 44.5 | 254 | 217 | 55.5 | 55.3 | 66 | 21.8 | 42.1 | 2.42 | 8.4 | 22.9 | 55.4 | 69.7 | 22 | 44.4 | 2.61 | 8.5 | 24.2 | 20.1 | 21.6 | 35 | 2.48 | 1.09 | 2.63 | 1.1 | 254 | 217 | 2104 | 2104
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:15:00 | 1354.62 | 752.24 | 869016.3 | 841971.4 | 19.85 | 3220.434 | 1252.392 | 230.399 | 30 | 194 | 34.3 | 45.9 | 32.5 | 48.1 | 0 | 0 | - | - | 37.4 | 44.4 | 250 | 213 | 58.9 | 59.1 | 67.7 | 21.8 | 43 | 2.49 | 9.7 | 23.5 | 59 | 71.5 | 21.8 | 45.1 | 2.67 | 9.9 | 25.1 | 19.8 | 21.3 | 35.1 | 2.55 | 1.05 | 2.69 | 1.05 | 250 | 213 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:20:00 | 1375.1 | 752.24 | 869036.76 | 841971.4 | 20.55 | 3183.164 | 1289.662 | 64.583 | 30 | 194 | 34.2 | 45.7 | 32.5 | 48 | 0 | 0 | - | - | 37.4 | 44.4 | 249 | 211 | 56.1 | 56.3 | 67.4 | 21.4 | 42.1 | 2.42 | 8.5 | 24.4 | 56.5 | 71.4 | 21.6 | 44.7 | 2.62 | 8.4 | 25.7 | 19.6 | 21.1 | 34.9 | 2.47 | 1.08 | 2.64 | 1.08 | 249 | 211 | 2107 | 2109
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:25:00 | 1379.8 | 753.5 | 869041.52 | 841972.66 | 21.16 | 3175.71 | 1297.116 | 137.892 | 31 | 194 | 34.3 | 45.6 | 32.5 | 47.9 | 0 | 0 | - | - | 37.4 | 44.3 | 242 | 207 | 56.1 | 55.8 | 66.9 | 21.6 | 42.7 | 2.45 | 8.4 | 23.3 | 56 | 70.3 | 21.6 | 44.6 | 2.61 | 8.4 | 24.8 | 19.7 | 21.2 | 36.3 | 2.51 | 1.09 | 2.63 | 1.09 | 243 | 208 | 2026 | 2026
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:30:00 | 1417.94 | 753.5 | 869080.36 | 841972.66 | 21.78 | 3145.89 | 1326.936 | 906.347 | 31 | 194 | 34.4 | 45.4 | 32.5 | 47.8 | 0 | 0 | - | - | 37.4 | 44.2 | 242 | 207 | 56.1 | 56.3 | 66.2 | 21.4 | 41.9 | 2.43 | 8.9 | 23 | 56 | 70.3 | 21.6 | 44.5 | 2.61 | 8.9 | 24.8 | 19.6 | 21.1 | 34.9 | 2.49 | 1.06 | 2.63 | 1.07 | 242 | 207 | 2115 | 2112
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:35:00 | 1500.1 | 753.5 | 869163.66 | 841972.66 | 22.41 | 3078.795 | 1394.031 | 971.053 | 33 | 194 | 34.5 | 45.3 | 32.7 | 47.6 | 0 | 0 | - | - | 37.5 | 44 | 242 | 207 | 56.6 | 56.8 | 66.5 | 21.3 | 41.9 | 2.38 | 9 | 24 | 56.6 | 70.6 | 21.4 | 44.6 | 2.61 | 8.9 | 25.1 | 19.6 | 21 | 34.2 | 2.44 | 1.06 | 2.64 | 1.06 | 242 | 207 | 2148 | 2151
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:40:00 | 1593.44 | 753.5 | 869257.96 | 841972.66 | 23.05 | 2989.341 | 1483.485 | 1421.918 | 35 | 194 | 34.6 | 45.1 | 32.8 | 47.4 | 0 | 0 | - | - | 37.5 | 43.9 | 242 | 207 | 56.7 | 56.7 | 66.8 | 21.3 | 42.3 | 2.45 | 8.8 | 23.3 | 56.7 | 70.7 | 21.4 | 44.7 | 2.63 | 8.7 | 24.9 | 19.5 | 21 | 35 | 2.51 | 1.06 | 2.65 | 1.07 | 242 | 207 | 2095 | 2098
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:45:00 | 1715.62 | 753.5 | 869379.44 | 841972.66 | 23.68 | 2862.612 | 1610.214 | 1471.178 | 38 | 194 | 34.8 | 44.8 | 32.9 | 47.2 | 0 | 0 | - | - | 37.5 | 43.8 | 242 | 207 | 56.8 | 56.8 | 67 | 21.5 | 42.6 | 2.43 | 8.7 | 23.8 | 56.7 | 70.7 | 21.6 | 44.7 | 2.62 | 8.7 | 25 | 19.7 | 21.2 | 35.1 | 2.49 | 1.07 | 2.65 | 1.08 | 242 | 207 | 2094 | 2095
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:50:00 | 1846.46 | 753.5 | 869511.26 | 841972.66 | 24.32 | 2728.422 | 1744.404 | 1499.137 | 41 | 194 | 35 | 44.7 | 33 | 47.1 | 0 | 0 | - | - | 37.6 | 43.8 | 236 | 205 | 57.3 | 57.3 | 67.5 | 21.8 | 43.3 | 2.5 | 8.4 | 23.2 | 56.8 | 70.7 | 21.9 | 45.1 | 2.65 | 8.4 | 24.6 | 20.1 | 21.5 | 36.9 | 2.56 | 1.09 | 2.67 | 1.1 | 236 | 205 | 1984 | 1983
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 11:55:00 | 1970.66 | 753.5 | 869634.6 | 841972.66 | 24.93 | 2638.968 | 1833.858 | 1088.232 | 43 | 194 | 35.2 | 44.5 | 33.2 | 47 | 0 | 0 | - | - | 37.7 | 43.7 | 232 | 201 | 56.7 | 56.6 | 67.5 | 22.2 | 43.3 | 2.49 | 8.7 | 23.3 | 56.9 | 70.5 | 22.3 | 45.1 | 2.65 | 8.8 | 24.5 | 20.5 | 21.8 | 36.8 | 2.55 | 1.1 | 2.67 | 1.1 | 232 | 201 | 1995 | 1992
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:00:00 | 2027.3 | 753.5 | 869691 | 841972.66 | 25.54 | 2571.876 | 1900.95 | 454.01 | 45 | 194 | 35.4 | 44.4 | 33.3 | 47 | 0 | 0 | - | - | 37.7 | 43.5 | 232 | 201 | 57.2 | 57.1 | 67.5 | 22.4 | 42.8 | 2.48 | 9.2 | 23.4 | 56.9 | 70.8 | 22.4 | 45 | 2.65 | 9.1 | 24.7 | 20.6 | 22 | 35.9 | 2.54 | 1.09 | 2.67 | 1.09 | 232 | 201 | 2050 | 2052
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:05:00 | 2055.28 | 753.5 | 869717.32 | 841972.66 | 26.16 | 2549.514 | 1923.312 | 193.33 | 45 | 194 | 35.5 | 44.4 | 33.4 | 47 | 0 | 0 | - | - | 37.8 | 43.5 | 232 | 201 | 56.6 | 56.5 | 67.5 | 22.4 | 42.4 | 2.41 | 9.3 | 24.5 | 56.5 | 70.9 | 22.5 | 44.9 | 2.63 | 9.1 | 25 | 20.7 | 22.1 | 35.2 | 2.47 | 1.08 | 2.66 | 1.09 | 232 | 201 | 2095 | 2092
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:10:00 | 2061.46 | 754.7 | 869723.02 | 841974.3 | 26.79 | 2549.514 | 1923.312 | -166.602 | 45 | 194 | 35 | 44.8 | 33.5 | 46.8 | 0 | 0 | - | - | 37.8 | 43.5 | 232 | 201 | 57.6 | 57.5 | 67.6 | 22.3 | 42.8 | 2.49 | 9.4 | 23.5 | 57.5 | 71.2 | 22.4 | 45 | 2.65 | 9.3 | 25 | 20.5 | 21.9 | 35.1 | 2.54 | 1.08 | 2.68 | 1.08 | 232 | 201 | 2088 | 2088
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:15:00 | 2061.46 | 765.82 | 869723.02 | 841985.06 | 27.42 | 2549.514 | 1923.312 | -45.275 | 45 | 194 | 34.5 | 45.3 | 33.1 | 47.2 | 0 | 0 | - | - | 37.8 | 43.4 | 232 | 201 | 57 | 57 | 67.5 | 22.2 | 42.2 | 2.43 | 9.5 | 24.3 | 57.4 | 71.3 | 22.3 | 44.9 | 2.63 | 9.3 | 25.4 | 20.3 | 21.8 | 34.4 | 2.48 | 1.07 | 2.66 | 1.08 | 232 | 201 | 2136 | 2136
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:20:00 | 2069.24 | 767.22 | 869731.14 | 841986.38 | 28.07 | 2549.514 | 1923.312 | 145.651 | 45 | 194 | 34.9 | 45 | 33.2 | 47.1 | 0 | 0 | - | - | 37.8 | 43.4 | 232 | 201 | 60.6 | 60.7 | 69.1 | 22.1 | 43.4 | 2.51 | 10.4 | 24.6 | 60.7 | 72.6 | 22.2 | 45.6 | 2.69 | 10.4 | 25.8 | 20.2 | 21.7 | 35.1 | 2.57 | 1.03 | 2.72 | 1.03 | 232 | 201 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:25:00 | 2080.16 | 767.22 | 869741.9 | 841986.38 | 28.78 | 2549.514 | 1923.312 | 87.345 | 45 | 194 | 35 | 44.8 | 33.1 | 47.1 | 0 | 0 | - | - | 37.8 | 43.3 | 232 | 201 | 57.3 | 57.3 | 69.1 | 21.7 | 43.2 | 2.49 | 8.7 | 25 | 56.6 | 72.6 | 21.8 | 45.1 | 2.64 | 8.7 | 26.6 | 19.9 | 21.3 | 35.9 | 2.55 | 1.08 | 2.67 | 1.08 | 232 | 201 | 2046 | 2046
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:30:00 | 2082.22 | 773.6 | 869743.78 | 841993.06 | 29.39 | 2549.514 | 1923.312 | -335.063 | 45 | 194 | 35 | 44.8 | 33 | 47.1 | 0 | 0 | - | - | 37.8 | 43.4 | 232 | 201 | 57.3 | 57.2 | 67.5 | 21.8 | 42.1 | 2.42 | 9.3 | 24.5 | 57 | 71.2 | 21.9 | 44.9 | 2.63 | 9 | 25.4 | 20 | 21.4 | 35.1 | 2.48 | 1.06 | 2.65 | 1.08 | 232 | 201 | 2098 | 2098
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:35:00 | 2082.22 | 802.72 | 869743.78 | 842022.52 | 30.01 | 2549.514 | 1923.312 | -326.095 | 45 | 194 | 35.5 | 44.2 | 32.9 | 47.3 | 0 | 0 | - | - | 37.7 | 43.4 | 232 | 201 | 56.8 | 56.6 | 67.5 | 21.7 | 42.9 | 2.46 | 8.7 | 23.8 | 56.5 | 70.7 | 21.9 | 44.9 | 2.62 | 8.7 | 25 | 20 | 21.4 | 36.6 | 2.52 | 1.08 | 2.65 | 1.08 | 232 | 201 | 2004 | 2004
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:40:00 | 2082.22 | 842.26 | 869743.78 | 842062.04 | 30.62 | 2594.238 | 1878.588 | -389.331 | 44 | 194 | 35.9 | 43.8 | 32.7 | 47.4 | 0 | 0 | - | - | 37.6 | 43.4 | 232 | 201 | 56.3 | 56.6 | 67.2 | 21.7 | 42.7 | 2.45 | 8.7 | 23.6 | 56.5 | 70.5 | 21.8 | 44.7 | 2.62 | 8.7 | 24.7 | 19.9 | 21.3 | 36.8 | 2.51 | 1.08 | 2.65 | 1.08 | 232 | 201 | 1989 | 1987
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:45:00 | 2088.62 | 852.08 | 869750.66 | 842071.24 | 31.15 | 2594.238 | 1878.588 | 368.154 | 44 | 194 | 35.3 | 44.2 | 32.5 | 47.6 | 0 | 0 | - | - | 37.6 | 43.4 | 0 | 0 | 0 | 0 | 64.9 | 21.9 | 39.3 | 1.99 | 7.7 | 30.4 | 0 | 68.5 | 21.8 | 41.2 | 2.14 | 14.3 | 31.6 | 21.1 | 21.2 | 36.4 | 2.01 | 1.04 | 2.14 | 0.86 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:50:00 | 2099.9 | 863.56 | 869761.46 | 842083.54 | 31.36 | 2594.238 | 1878.588 | -425.312 | 44 | 194 | 34.8 | 44.7 | 32.4 | 47.7 | 0 | 0 | - | - | 37.6 | 43.3 | 0 | 0 | 0 | 0 | 33.4 | 44.1 | 35.7 | 1.47 | 20.6 | 9.6 | 0 | 34.7 | 44.6 | 35.2 | 1.63 | 20.8 | 7.7 | 23.4 | 23.2 | 35.7 | 1.49 | 1.48 | 1.63 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 12:55:00 | 2101.52 | 884.9 | 869763.24 | 842104.06 | 31.57 | 2638.968 | 1833.858 | 187.142 | 43 | 194 | 34.4 | 45.3 | 32.3 | 48 | 0 | 0 | - | - | 37.5 | 43.4 | 0 | 0 | 0 | 0 | 33.6 | 43.7 | 35.7 | 1.48 | 19.6 | 9.5 | 0 | 33.6 | 46.6 | 34.4 | 1.51 | 22.4 | 9.5 | 24 | 23.8 | 34.4 | 1.5 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:00:00 | 2104.46 | 894.64 | 869766.02 | 842114.92 | 31.79 | 2638.968 | 1833.858 | -334.194 | 43 | 194 | 34.2 | 45.8 | 32.3 | 48.2 | 0 | 0 | - | - | 37.5 | 43.4 | 0 | 0 | 0 | 0 | 34.4 | 42.6 | 35.4 | 1.49 | 18.3 | 10.1 | 0 | 34.8 | 44.9 | 34.1 | 1.51 | 20.4 | 10.5 | 24.3 | 24.1 | 33.6 | 1.51 | 1.51 | 1.51 | 1.52 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:05:00 | 2106.94 | 905.52 | 869768.76 | 842124.68 | 32 | 2638.968 | 1833.858 | 342.016 | 43 | 194 | 34 | 46.1 | 32.2 | 48.4 | 0 | 0 | - | - | 37.5 | 43.4 | 0 | 0 | 0 | 0 | 34.9 | 42 | 35.1 | 1.5 | 17.5 | 10.5 | 0 | 35.4 | 43.6 | 33.9 | 1.52 | 18.9 | 11 | 24.4 | 24.2 | 33.1 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:10:00 | 2142.98 | 905.52 | 869805.24 | 842124.68 | 32.2 | 2594.238 | 1878.588 | 335.074 | 44 | 194 | 33.8 | 46.3 | 32.1 | 48.6 | 0 | 0 | - | - | 37.5 | 43.3 | 0 | 0 | 0 | 0 | 35 | 41.6 | 34.9 | 1.5 | 17.1 | 10.5 | 0 | 35.5 | 42.6 | 33.7 | 1.52 | 17.8 | 11 | 24.5 | 24.3 | 32.6 | 1.52 | 1.52 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:15:00 | 2177.76 | 905.52 | 869839.62 | 842124.68 | 32.39 | 2586.784 | 1886.042 | 85.176 | 44 | 194 | 33.7 | 46.5 | 32.1 | 48.7 | 0 | 0 | - | - | 37.4 | 43.4 | 0 | 0 | 0 | 0 | 35 | 40.9 | 34.6 | 1.5 | 16.3 | 10.4 | 0 | 35.4 | 41.6 | 33.6 | 1.52 | 16.6 | 10.8 | 24.6 | 24.4 | 33.2 | 1.52 | 1.53 | 1.52 | 1.53 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:20:00 | 2178.36 | 917 | 869839.92 | 842136.56 | 32.57 | 2594.238 | 1878.588 | -508.481 | 44 | 194 | 33.6 | 46.7 | 32 | 48.8 | 0 | 0 | - | - | 37.4 | 43.4 | 0 | 0 | 0 | 0 | 35 | 40.1 | 34.4 | 1.51 | 15.4 | 10.3 | 0 | 35.4 | 40.6 | 33.4 | 1.53 | 15.5 | 10.7 | 24.7 | 24.5 | 32.6 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:25:00 | 2178.36 | 970.42 | 869839.92 | 842189.9 | 32.75 | 2638.968 | 1833.858 | -134.402 | 43 | 194 | 33.5 | 46.9 | 32 | 49 | 0 | 0 | - | - | 37.4 | 43.5 | 0 | 0 | 0 | 0 | 35 | 39.4 | 34.2 | 1.51 | 14.7 | 10.2 | 0 | 35.2 | 39.8 | 33.4 | 1.53 | 14.8 | 10.6 | 24.7 | 24.5 | 32.2 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:30:00 | 2180.96 | 971.92 | 869842.54 | 842191.08 | 32.91 | 2638.968 | 1833.858 | -25.948 | 43 | 194 | 33.4 | 47.1 | 31.9 | 49.1 | 0 | 0 | - | - | 37.3 | 43.5 | 0 | 0 | 0 | 0 | 34.9 | 38.7 | 34.1 | 1.51 | 13.9 | 10.1 | 0 | 35.1 | 39.4 | 33.3 | 1.53 | 14.3 | 10.3 | 24.7 | 24.5 | 32.1 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:35:00 | 2185.24 | 973.62 | 869846.8 | 842192.92 | 33.07 | 2638.968 | 1833.858 | -111.451 | 43 | 194 | 33.3 | 47.2 | 31.8 | 49.3 | 0 | 0 | - | - | 37.2 | 43.6 | 0 | 0 | 0 | 0 | 34.8 | 38.1 | 34.1 | 1.51 | 13.3 | 10 | 0 | 34.9 | 38.9 | 33.2 | 1.53 | 13.8 | 10 | 24.8 | 24.6 | 32.8 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:40:00 | 2185.24 | 1003.92 | 869846.8 | 842223.7 | 33.25 | 2653.878 | 1818.948 | -628.128 | 42 | 194 | 33.1 | 47.4 | 31.8 | 49.3 | 0 | 0 | - | - | 37.2 | 43.7 | 0 | 0 | 0 | 0 | 34.8 | 37.7 | 34.2 | 1.51 | 12.9 | 10 | 0 | 34.6 | 38.6 | 33.2 | 1.53 | 13.6 | 9.9 | 24.8 | 24.6 | 32.9 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:45:00 | 2185.24 | 1066.44 | 869846.8 | 842288 | 33.4 | 2728.422 | 1744.404 | -949.808 | 41 | 194 | 33 | 47.6 | 31.6 | 49.5 | 0 | 0 | - | - | 37.1 | 43.8 | 0 | 0 | 0 | 0 | 34.7 | 37.4 | 34.1 | 1.51 | 12.5 | 9.9 | 0 | 34.4 | 38.4 | 33.4 | 1.53 | 13.3 | 9.7 | 24.8 | 24.6 | 32.7 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:50:00 | 2185.24 | 1126.04 | 869846.8 | 842346.06 | 33.56 | 2773.152 | 1699.674 | -425.762 | 40 | 194 | 32.8 | 47.8 | 31.5 | 49.7 | 0 | 0 | - | - | 37 | 43.8 | 0 | 0 | 0 | 0 | 34.4 | 37.1 | 33.9 | 1.51 | 12.3 | 9.6 | 0 | 34.1 | 38.1 | 33.2 | 1.53 | 13 | 9.3 | 24.8 | 24.6 | 32.2 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 13:55:00 | 2185.24 | 1140.14 | 869846.8 | 842359.46 | 33.71 | 2795.517 | 1677.309 | -162.346 | 39 | 194 | 32.6 | 48 | 31.3 | 49.9 | 0 | 0 | - | - | 36.8 | 43.9 | 0 | 0 | 0 | 0 | 34.1 | 36.6 | 33.6 | 1.51 | 11.7 | 9.2 | 0 | 33.7 | 37.6 | 33.1 | 1.53 | 12.5 | 8.9 | 24.8 | 24.6 | 31.7 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:00:00 | 2185.24 | 1168.2 | 869846.8 | 842388.02 | 33.85 | 2817.882 | 1654.944 | -482.675 | 39 | 194 | 32.4 | 48.3 | 31.2 | 50.1 | 0 | 0 | - | - | 36.7 | 44.2 | 0 | 0 | 0 | 0 | 33.6 | 35.9 | 33.4 | 1.51 | 11.1 | 8.8 | 0 | 33.4 | 36.9 | 32.7 | 1.53 | 11.9 | 8.5 | 24.8 | 24.6 | 31.3 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:05:00 | 2185.24 | 1193.32 | 869846.8 | 842413.48 | 34.01 | 2855.157 | 1617.669 | -436.337 | 38 | 194 | 32.1 | 48.5 | 31 | 50.3 | 0 | 0 | - | - | 36.4 | 44.3 | 0 | 0 | 0 | 0 | 33.1 | 35.4 | 32.9 | 1.51 | 10.5 | 8.3 | 0 | 32.9 | 36.6 | 32.6 | 1.53 | 11.4 | 8 | 24.8 | 24.6 | 30.7 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:10:00 | 2185.24 | 1224.02 | 869846.8 | 842443.5 | 34.16 | 2862.612 | 1610.214 | -326.042 | 37 | 194 | 31.8 | 48.9 | 30.7 | 50.7 | 0 | 0 | - | - | 36.2 | 44.6 | 0 | 0 | 0 | 0 | 32.4 | 34.7 | 32.4 | 1.51 | 9.9 | 7.6 | 0 | 32.1 | 35.9 | 32.1 | 1.53 | 10.7 | 7.4 | 24.8 | 24.6 | 28.8 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:15:00 | 2196.54 | 1229.9 | 869858.34 | 842449.06 | 34.31 | 2862.612 | 1610.214 | 251.46 | 38 | 194 | 31.4 | 49.3 | 30.3 | 51.1 | 0 | 0 | - | - | 35.8 | 44.9 | 0 | 0 | 0 | 0 | 31.2 | 33.7 | 31.6 | 1.51 | 8.9 | 6.4 | 0 | 31.2 | 34.9 | 31.3 | 1.53 | 9.8 | 6.5 | 24.8 | 24.6 | 26.7 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:20:00 | 2214.94 | 1229.9 | 869876.58 | 842449.06 | 34.45 | 2862.612 | 1610.214 | -1.695 | 38 | 194 | 30.9 | 49.8 | 29.9 | 51.6 | 0 | 0 | - | - | 35.1 | 45.5 | 0 | 0 | 0 | 0 | 30.2 | 32.6 | 30.6 | 1.51 | 7.7 | 5.3 | 0 | 30.2 | 33.6 | 30.3 | 1.53 | 8.5 | 5.4 | 24.8 | 24.7 | 26.1 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:25:00 | 2223.84 | 1230.14 | 869885.96 | 842449.3 | 34.6 | 2862.612 | 1610.214 | 221.076 | 38 | 194 | 30.5 | 50.2 | 29.5 | 52.1 | 0 | 0 | - | - | 34.4 | 46.1 | 0 | 0 | 0 | 0 | 29.4 | 31.6 | 29.9 | 1.51 | 6.7 | 4.6 | 0 | 28.9 | 32.6 | 29.4 | 1.53 | 7.4 | 4.1 | 24.9 | 24.7 | 26.2 | 1.53 | 1.53 | 1.53 | 1.54 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:30:00 | 2273.36 | 1230.14 | 869936.42 | 842449.3 | 34.74 | 2802.972 | 1669.854 | 976.71 | 39 | 194 | 30 | 50.8 | 29.1 | 52.6 | 0 | 0 | - | - | 33.7 | 46.8 | 0 | 0 | 0 | 0 | 28.8 | 30.7 | 29.2 | 1.51 | 5.9 | 4 | 0 | 28.7 | 31.7 | 28.7 | 1.54 | 6.5 | 3.8 | 24.9 | 24.7 | 26.5 | 1.53 | 1.54 | 1.53 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:35:00 | 2356.66 | 1230.14 | 870020.64 | 842449.3 | 34.89 | 2728.422 | 1744.404 | 890.514 | 41 | 194 | 29.6 | 51.4 | 28.8 | 53 | 0 | 0 | - | - | 33 | 47.4 | 0 | 0 | 0 | 0 | 28.6 | 30.4 | 28.8 | 1.52 | 5.4 | 3.6 | 0 | 28.3 | 31.1 | 28.2 | 1.54 | 5.8 | 3.4 | 25 | 24.9 | 26.7 | 1.54 | 1.54 | 1.54 | 1.55 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:40:00 | 2428.3 | 1230.14 | 870090.72 | 842449.3 | 35.03 | 2638.968 | 1833.858 | 845.751 | 43 | 194 | 29.2 | 51.9 | 28.6 | 53.4 | 0 | 0 | - | - | 32.5 | 47.9 | 0 | 0 | 0 | 0 | 28.3 | 30.2 | 28.6 | 1.53 | 5 | 3.2 | 0 | 28.2 | 30.7 | 28.1 | 1.55 | 5.2 | 2.9 | 25.2 | 25.1 | 26.8 | 1.55 | 1.55 | 1.55 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:45:00 | 2481.74 | 1230.14 | 870143.72 | 842449.3 | 35.17 | 2594.238 | 1878.588 | 261.778 | 44 | 194 | 28.9 | 52.4 | 28.4 | 53.6 | 0 | 0 | - | - | 32.1 | 48.3 | 0 | 0 | 0 | 0 | 28.2 | 30.1 | 28.3 | 1.53 | 4.7 | 2.9 | 0 | 27.9 | 30.2 | 27.8 | 1.56 | 4.6 | 2.6 | 25.5 | 25.3 | 26.6 | 1.55 | 1.55 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:50:00 | 2506.26 | 1230.14 | 870168.44 | 842449.3 | 35.29 | 2586.784 | 1886.042 | 425.517 | 44 | 194 | 28.7 | 52.7 | 28.4 | 53.8 | 0 | 0 | - | - | 31.8 | 48.6 | 0 | 0 | 0 | 0 | 28.1 | 29.7 | 28.1 | 1.53 | 4.3 | 2.8 | 0 | 27.7 | 29.8 | 27.6 | 1.56 | 4.1 | 2.4 | 25.6 | 25.5 | 26.6 | 1.55 | 1.55 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 14:55:00 | 2545.14 | 1230.14 | 870207.5 | 842449.3 | 35.43 | 2549.514 | 1923.312 | 303.137 | 45 | 194 | 28.5 | 53 | 28.3 | 54 | 0 | 0 | - | - | 31.5 | 49 | 0 | 0 | 0 | 0 | 27.9 | 29.4 | 28.1 | 1.54 | 4 | 2.5 | 0 | 27.7 | 29.6 | 27.6 | 1.56 | 3.8 | 2.2 | 25.8 | 25.6 | 26.9 | 1.56 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:00:00 | 2550.34 | 1241.2 | 870211.9 | 842460.36 | 35.55 | 2549.514 | 1923.312 | -199.608 | 45 | 194 | 28.4 | 53.3 | 28.2 | 54.1 | 0 | 0 | - | - | 31.2 | 49.2 | 0 | 0 | 0 | 0 | 27.9 | 29.2 | 28.1 | 1.54 | 3.8 | 2.5 | 0 | 27.6 | 29.4 | 27.6 | 1.57 | 3.5 | 2 | 25.9 | 25.7 | 26.5 | 1.56 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:05:00 | 2558.68 | 1245.12 | 870220.94 | 842464.28 | 35.66 | 2549.514 | 1923.312 | 313.194 | 45 | 194 | 28.3 | 53.5 | 28.2 | 54.1 | 0 | 0 | - | - | 31 | 49.4 | 0 | 0 | 0 | 0 | 27.8 | 29.1 | 27.8 | 1.54 | 3.5 | 2.4 | 0 | 27.4 | 29.2 | 27.4 | 1.57 | 3.3 | 1.8 | 25.9 | 25.8 | 26.5 | 1.56 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:10:00 | 2566.48 | 1249.42 | 870228.22 | 842468.58 | 35.77 | 2549.514 | 1923.312 | 126.063 | 45 | 194 | 28.2 | 53.7 | 28.2 | 54.2 | 0 | 0 | - | - | 30.8 | 49.6 | 0 | 0 | 0 | 0 | 27.6 | 28.7 | 27.7 | 1.53 | 3.2 | 2.3 | 0 | 27.2 | 28.9 | 27.3 | 1.56 | 3 | 1.7 | 25.9 | 25.8 | 26.1 | 1.55 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:15:00 | 2586.32 | 1249.42 | 870248.48 | 842468.58 | 35.88 | 2512.239 | 1960.587 | 379.714 | 46 | 194 | 28.1 | 53.9 | 28.1 | 54.4 | 0 | 0 | - | - | 30.7 | 49.8 | 0 | 0 | 0 | 0 | 27.4 | 28.6 | 27.6 | 1.52 | 3.1 | 2.3 | 0 | 27 | 28.6 | 27.2 | 1.56 | 2.7 | 1.7 | 26 | 25.8 | 25.9 | 1.54 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:20:00 | 2601.36 | 1249.42 | 870263.12 | 842468.58 | 35.98 | 2504.784 | 1968.042 | 142.426 | 46 | 194 | 27.9 | 54.1 | 28 | 54.5 | 0 | 0 | - | - | 30.5 | 49.9 | 0 | 0 | 0 | 0 | 27.2 | 28.4 | 27.3 | 1.52 | 3 | 2.3 | 0 | 26.8 | 28.3 | 27.1 | 1.55 | 2.5 | 1.5 | 26 | 25.9 | 25.7 | 1.54 | 1.56 | 1.55 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:25:00 | 2615 | 1249.42 | 870276.8 | 842468.58 | 36.08 | 2504.784 | 1968.042 | 131.197 | 46 | 194 | 27.8 | 54.2 | 27.9 | 54.6 | 0 | 0 | - | - | 30.3 | 50 | 0 | 0 | 0 | 0 | 27.1 | 28.2 | 27.2 | 1.51 | 2.9 | 2.3 | 0 | 26.7 | 28.1 | 26.8 | 1.55 | 2.3 | 1.5 | 26.1 | 25.9 | 25.7 | 1.53 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:30:00 | 2632.36 | 1249.42 | 870294.32 | 842468.58 | 36.18 | 2489.874 | 1982.952 | 192.658 | 47 | 194 | 27.7 | 54.4 | 27.9 | 54.7 | 0 | 0 | - | - | 30.1 | 50.2 | 0 | 0 | 0 | 0 | 26.9 | 28.1 | 27.1 | 1.51 | 2.7 | 2.1 | 0 | 26.4 | 27.8 | 26.7 | 1.54 | 2.1 | 1.4 | 26.1 | 26 | 25.7 | 1.53 | 1.55 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:35:00 | 2636.64 | 1251.74 | 870298.2 | 842471.1 | 36.27 | 2474.964 | 1997.862 | -118.49 | 47 | 194 | 27.6 | 54.6 | 27.8 | 54.8 | 0 | 0 | - | - | 30 | 50.4 | 0 | 0 | 0 | 0 | 26.7 | 27.8 | 26.9 | 1.51 | 2.5 | 1.9 | 0 | 26.3 | 27.7 | 26.7 | 1.54 | 1.8 | 1.2 | 26.1 | 26 | 25.7 | 1.53 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:40:00 | 2636.64 | 1259.14 | 870298.2 | 842478.48 | 36.37 | 2489.874 | 1982.952 | -65.366 | 47 | 194 | 27.5 | 54.7 | 27.8 | 54.9 | 0 | 0 | - | - | 29.9 | 50.5 | 0 | 0 | 0 | 0 | 26.7 | 27.8 | 26.8 | 1.51 | 2.5 | 1.9 | 0 | 26.2 | 27.4 | 26.6 | 1.54 | 1.6 | 1.1 | 26.2 | 26 | 25.6 | 1.53 | 1.55 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:45:00 | 2636.8 | 1262.8 | 870298.36 | 842482 | 36.46 | 2489.874 | 1982.952 | 26.02 | 46 | 194 | 27.5 | 54.9 | 27.7 | 55 | 0 | 0 | - | - | 29.8 | 50.6 | 0 | 0 | 0 | 0 | 26.6 | 27.7 | 26.7 | 1.51 | 2.4 | 1.7 | 0 | 26.2 | 27.3 | 26.5 | 1.54 | 1.6 | 1 | 26.2 | 26.1 | 25.8 | 1.53 | 1.55 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:50:00 | 2637.34 | 1264.1 | 870298.9 | 842483.34 | 36.55 | 2489.874 | 1982.952 | 53.801 | 46 | 194 | 27.4 | 55 | 27.7 | 55 | 0 | 0 | - | - | 29.7 | 50.7 | 0 | 0 | 0 | 0 | 26.6 | 27.7 | 26.7 | 1.51 | 2.4 | 1.7 | 0 | 26.1 | 27.4 | 26.5 | 1.54 | 1.6 | 1.1 | 26.2 | 26.1 | 26.1 | 1.53 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 15:55:00 | 2638.46 | 1266.3 | 870300.02 | 842485.62 | 36.64 | 2489.874 | 1982.952 | -131.901 | 46 | 194 | 27.3 | 55.1 | 27.7 | 55.1 | 0 | 0 | - | - | 29.7 | 50.7 | 0 | 0 | 0 | 0 | 26.6 | 27.7 | 26.8 | 1.52 | 2.3 | 1.7 | 0 | 26.1 | 27.4 | 26.6 | 1.54 | 1.6 | 1.1 | 26.2 | 26.1 | 26.3 | 1.54 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:00:00 | 2638.66 | 1271.06 | 870300.3 | 842490.22 | 36.73 | 2504.784 | 1968.042 | 63.71 | 46 | 194 | 27.2 | 55.2 | 27.6 | 55.2 | 0 | 0 | - | - | 29.6 | 50.8 | 0 | 0 | 0 | 0 | 26.6 | 27.7 | 26.8 | 1.52 | 2.3 | 1.7 | 0 | 26.2 | 27.4 | 26.6 | 1.54 | 1.7 | 1.2 | 26.2 | 26.1 | 26.3 | 1.54 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:05:00 | 2645.98 | 1272.48 | 870307.92 | 842491.64 | 36.82 | 2489.874 | 1982.952 | 429.072 | 47 | 194 | 27.2 | 55.3 | 27.5 | 55.2 | 0 | 0 | - | - | 29.6 | 50.8 | 0 | 0 | 0 | 0 | 26.7 | 27.7 | 26.9 | 1.52 | 2.3 | 1.6 | 0 | 26.2 | 27.5 | 26.7 | 1.54 | 1.7 | 1.2 | 26.2 | 26.1 | 26.4 | 1.54 | 1.55 | 1.54 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:10:00 | 2684.66 | 1272.48 | 870346.46 | 842491.64 | 36.92 | 2460.054 | 2012.772 | 399.45 | 47 | 194 | 27.1 | 55.4 | 27.4 | 55.4 | 0 | 0 | - | - | 29.7 | 50.8 | 0 | 0 | 0 | 0 | 26.8 | 27.7 | 27 | 1.53 | 2.3 | 1.6 | 0 | 26.2 | 27.6 | 26.8 | 1.55 | 1.8 | 1.2 | 26.2 | 26.1 | 26.5 | 1.55 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:15:00 | 2716.62 | 1272.48 | 870378.54 | 842491.64 | 37.02 | 2415.324 | 2057.502 | 348.672 | 48 | 194 | 27.1 | 55.5 | 27.4 | 55.5 | 0 | 0 | - | - | 29.6 | 50.7 | 0 | 0 | 0 | 0 | 26.8 | 27.7 | 27.1 | 1.53 | 2.3 | 1.6 | 0 | 26.3 | 27.6 | 26.8 | 1.54 | 1.8 | 1.3 | 26.3 | 26.2 | 26.6 | 1.55 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:20:00 | 2742.12 | 1272.48 | 870404.1 | 842491.64 | 37.12 | 2400.416 | 2072.41 | 287.305 | 49 | 194 | 27 | 55.7 | 27.2 | 55.8 | 0 | 0 | - | - | 29.6 | 50.7 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 27.1 | 1.53 | 2.3 | 1.6 | 0 | 26.3 | 27.6 | 26.9 | 1.55 | 1.7 | 1.2 | 26.4 | 26.3 | 26.6 | 1.55 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:25:00 | 2767.48 | 1272.48 | 870429.44 | 842491.64 | 37.22 | 2370.6 | 2102.226 | 137.553 | 49 | 194 | 26.9 | 55.8 | 27.1 | 56 | 0 | 0 | - | - | 29.6 | 50.8 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 27.1 | 1.54 | 2.3 | 1.6 | 0 | 26.3 | 27.7 | 26.9 | 1.55 | 1.7 | 1.3 | 26.5 | 26.3 | 26.6 | 1.55 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:30:00 | 2783.04 | 1272.48 | 870444.7 | 842491.64 | 37.31 | 2370.6 | 2102.226 | 227.397 | 49 | 194 | 26.9 | 55.8 | 27.1 | 56.1 | 0 | 0 | - | - | 29.6 | 50.7 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 27.1 | 1.53 | 2.3 | 1.7 | 0 | 26.3 | 27.7 | 26.8 | 1.54 | 1.7 | 1.3 | 26.6 | 26.4 | 26.2 | 1.55 | 1.56 | 1.54 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:35:00 | 2802.28 | 1272.48 | 870463.96 | 842491.64 | 37.4 | 2355.69 | 2117.136 | 263.941 | 50 | 194 | 26.9 | 55.9 | 27.2 | 55.9 | 0 | 0 | - | - | 29.6 | 50.7 | 0 | 0 | 0 | 0 | 26.9 | 27.7 | 27.1 | 1.53 | 2.2 | 1.7 | 0 | 26.3 | 27.6 | 26.8 | 1.55 | 1.9 | 1.2 | 26.6 | 26.5 | 26.2 | 1.55 | 1.56 | 1.54 | 1.56 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:40:00 | 2822.78 | 1272.48 | 870484.88 | 842491.64 | 37.49 | 2325.87 | 2146.956 | 256.986 | 50 | 194 | 26.8 | 55.9 | 27.2 | 55.9 | 0 | 0 | - | - | 29.6 | 50.8 | 0 | 0 | 0 | 0 | 27 | 27.7 | 26.9 | 1.53 | 2.2 | 1.7 | 0 | 26.5 | 27.4 | 26.8 | 1.55 | 1.7 | 1.2 | 26.7 | 26.5 | 26.2 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:45:00 | 2844.7 | 1272.48 | 870506.26 | 842491.64 | 37.58 | 2310.96 | 2161.866 | 246.597 | 51 | 194 | 26.7 | 56.1 | 27.2 | 55.9 | 0 | 0 | - | - | 29.5 | 50.8 | 0 | 0 | 0 | 0 | 27 | 27.7 | 26.9 | 1.53 | 2.2 | 1.6 | 0 | 26.5 | 27.4 | 26.7 | 1.56 | 1.6 | 1.1 | 26.7 | 26.6 | 26.3 | 1.55 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:50:00 | 2858.74 | 1272.5 | 870520.5 | 842491.66 | 37.67 | 2288.595 | 2184.231 | 95.025 | 51 | 194 | 26.7 | 56.2 | 27.3 | 55.9 | 0 | 0 | - | - | 29.5 | 50.8 | 0 | 0 | 0 | 0 | 27 | 27.7 | 26.9 | 1.54 | 2.2 | 1.6 | 0 | 26.6 | 27.4 | 26.7 | 1.56 | 1.6 | 1.1 | 26.8 | 26.7 | 26.4 | 1.56 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 16:55:00 | 2860.5 | 1279.24 | 870522.06 | 842498.68 | 37.75 | 2288.595 | 2184.231 | -256.927 | 51 | 194 | 26.6 | 56.3 | 27.2 | 55.9 | 0 | 0 | - | - | 29.4 | 50.9 | 0 | 0 | 0 | 0 | 27 | 27.7 | 26.8 | 1.54 | 2 | 1.5 | 0 | 26.6 | 27.4 | 26.7 | 1.56 | 1.5 | 1.1 | 26.8 | 26.7 | 26.4 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:00:00 | 2860.5 | 1311.4 | 870522.06 | 842530.76 | 37.85 | 2310.96 | 2161.866 | -434.202 | 50 | 194 | 26.6 | 56.4 | 27.1 | 56.1 | 0 | 0 | - | - | 29.4 | 51 | 0 | 0 | 0 | 0 | 27 | 27.6 | 26.8 | 1.54 | 1.9 | 1.6 | 0 | 26.6 | 27.3 | 26.7 | 1.56 | 1.5 | 1.1 | 26.8 | 26.7 | 26.5 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:05:00 | 2860.5 | 1326.36 | 870522.06 | 842545.52 | 37.93 | 2348.235 | 2124.591 | 22.08 | 50 | 194 | 26.6 | 56.5 | 27.1 | 56.3 | 0 | 0 | - | - | 29.3 | 51 | 0 | 0 | 0 | 0 | 27 | 27.6 | 26.7 | 1.54 | 1.9 | 1.5 | 0 | 26.4 | 27.3 | 26.7 | 1.56 | 1.4 | 1 | 26.9 | 26.7 | 26.5 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:10:00 | 2861.18 | 1327.96 | 870522.74 | 842547.24 | 38.02 | 2355.69 | 2117.136 | -50.289 | 50 | 194 | 26.5 | 56.5 | 27.1 | 56.2 | 0 | 0 | - | - | 29.3 | 51.2 | 0 | 0 | 0 | 0 | 26.9 | 27.6 | 26.7 | 1.54 | 1.9 | 1.4 | 0 | 26.3 | 27.2 | 26.6 | 1.56 | 1.4 | 0.9 | 26.9 | 26.7 | 26.5 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:15:00 | 2861.2 | 1332.86 | 870522.76 | 842552.24 | 38.1 | 2355.69 | 2117.136 | -140.983 | 50 | 194 | 26.5 | 56.5 | 27.1 | 56.2 | 0 | 0 | - | - | 29.2 | 51.1 | 0 | 0 | 0 | 0 | 26.7 | 27.6 | 26.7 | 1.55 | 1.8 | 1.1 | 0 | 26.2 | 27.2 | 26.6 | 1.57 | 1.3 | 0.7 | 26.8 | 26.7 | 26.6 | 1.57 | 1.57 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:20:00 | 2861.2 | 1346 | 870522.76 | 842565.44 | 38.18 | 2355.69 | 2117.136 | -191.895 | 49 | 194 | 26.5 | 56.6 | 27 | 56.3 | 0 | 0 | - | - | 29.2 | 51.2 | 0 | 0 | 0 | 0 | 26.3 | 27.6 | 26.7 | 1.55 | 1.8 | 0.7 | 0 | 26.2 | 27.2 | 26.6 | 1.57 | 1.3 | 0.7 | 26.8 | 26.7 | 26.7 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:25:00 | 2861.2 | 1366.26 | 870522.76 | 842585.88 | 38.27 | 2370.6 | 2102.226 | -228.088 | 49 | 194 | 26.5 | 56.7 | 27 | 56.4 | 0 | 0 | - | - | 29.2 | 51.3 | 0 | 0 | 0 | 0 | 26.1 | 27.6 | 26.7 | 1.55 | 1.8 | 0.5 | 0 | 26.2 | 27.2 | 26.6 | 1.57 | 1.3 | 0.6 | 26.9 | 26.7 | 26.6 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:30:00 | 2861.2 | 1388.08 | 870522.76 | 842607.52 | 38.35 | 2385.508 | 2087.318 | -282.178 | 49 | 194 | 26.4 | 56.8 | 27 | 56.4 | 0 | 0 | - | - | 29.1 | 51.3 | 0 | 0 | 0 | 0 | 26.1 | 27.6 | 26.7 | 1.55 | 1.8 | 0.5 | 0 | 26.2 | 27.2 | 26.6 | 1.57 | 1.2 | 0.5 | 26.9 | 26.7 | 26.7 | 1.57 | 1.57 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:35:00 | 2861.2 | 1414.12 | 870522.76 | 842634.1 | 38.44 | 2415.324 | 2057.502 | -336.62 | 48 | 194 | 26.4 | 56.8 | 26.9 | 56.5 | 0 | 0 | - | - | 29.1 | 51.4 | 0 | 0 | 0 | 0 | 26.1 | 27.6 | 26.7 | 1.55 | 1.8 | 0.5 | 0 | 26.1 | 27.2 | 26.6 | 1.57 | 1.3 | 0.5 | 26.8 | 26.7 | 26.7 | 1.57 | 1.57 | 1.57 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:40:00 | 2861.2 | 1443 | 870522.76 | 842662.7 | 38.53 | 2445.144 | 2027.682 | -348.866 | 47 | 194 | 26.4 | 56.8 | 26.9 | 56.5 | 0 | 0 | - | - | 29 | 51.4 | 0 | 0 | 0 | 0 | 26.1 | 27.6 | 26.7 | 1.55 | 1.8 | 0.6 | 0 | 26.1 | 27.2 | 26.6 | 1.57 | 1.3 | 0.5 | 26.8 | 26.7 | 26.7 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:45:00 | 2861.2 | 1471.32 | 870522.76 | 842691.16 | 38.63 | 2460.054 | 2012.772 | -326.64 | 47 | 194 | 26.4 | 56.9 | 26.9 | 56.5 | 0 | 0 | - | - | 29 | 51.5 | 0 | 0 | 0 | 0 | 26.1 | 27.6 | 26.7 | 1.55 | 1.9 | 0.5 | 0 | 26.1 | 27.3 | 26.6 | 1.57 | 1.3 | 0.6 | 26.8 | 26.7 | 26.6 | 1.57 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:50:00 | 2861.2 | 1494.42 | 870522.76 | 842713.82 | 38.72 | 2489.874 | 1982.952 | -194.056 | 46 | 194 | 26.4 | 56.9 | 26.9 | 56.5 | 0 | 0 | - | - | 29 | 51.5 | 0 | 0 | 0 | 0 | 26.1 | 27.6 | 26.7 | 1.54 | 1.9 | 0.5 | 0 | 26.1 | 27.3 | 26.6 | 1.56 | 1.4 | 0.5 | 26.8 | 26.7 | 26.7 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 17:55:00 | 2861.2 | 1511.22 | 870522.76 | 842730.8 | 38.8 | 2504.784 | 1968.042 | -401.657 | 46 | 194 | 26.4 | 56.9 | 27 | 56.5 | 0 | 0 | - | - | 29 | 51.5 | 0 | 0 | 0 | 0 | 26.1 | 27.6 | 26.7 | 1.54 | 1.9 | 0.5 | 0 | 26.1 | 27.3 | 26.6 | 1.56 | 1.4 | 0.6 | 26.7 | 26.7 | 26.6 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:00:00 | 2861.2 | 1548.02 | 870522.76 | 842767.72 | 38.9 | 2542.059 | 1930.767 | -264.539 | 45 | 194 | 26.4 | 56.9 | 27 | 56.5 | 0 | 0 | - | - | 28.9 | 51.6 | 0 | 0 | 0 | 0 | 26.1 | 27.6 | 26.7 | 1.54 | 2 | 0.5 | 0 | 26.1 | 27.3 | 26.6 | 1.56 | 1.4 | 0.5 | 26.7 | 26.7 | 26.5 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:05:00 | 2861.2 | 1572.68 | 870522.76 | 842792.46 | 39 | 2556.968 | 1915.858 | -296.551 | 44 | 194 | 26.4 | 56.9 | 27 | 56.5 | 0 | 0 | - | - | 28.9 | 51.6 | 0 | 0 | 0 | 0 | 26.1 | 27.6 | 26.7 | 1.54 | 2 | 0.5 | 0 | 26.1 | 27.3 | 26.6 | 1.56 | 1.4 | 0.6 | 26.8 | 26.6 | 26.6 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:10:00 | 2861.2 | 1598.44 | 870522.76 | 842818.12 | 39.09 | 2594.238 | 1878.588 | -398.164 | 44 | 194 | 26.4 | 56.9 | 27 | 56.5 | 0 | 0 | - | - | 28.9 | 51.7 | 0 | 0 | 0 | 0 | 26 | 27.6 | 26.7 | 1.54 | 2 | 0.6 | 0 | 26.1 | 27.3 | 26.6 | 1.56 | 1.5 | 0.6 | 26.7 | 26.6 | 26.7 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:15:00 | 2861.2 | 1636.16 | 870522.76 | 842856.42 | 39.19 | 2638.968 | 1833.858 | -781.514 | 43 | 194 | 26.4 | 56.9 | 26.9 | 56.5 | 0 | 0 | - | - | 28.9 | 51.7 | 0 | 0 | 0 | 0 | 26 | 27.7 | 26.8 | 1.54 | 2 | 0.6 | 0 | 26.1 | 27.4 | 26.6 | 1.56 | 1.6 | 0.6 | 26.7 | 26.6 | 26.6 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:20:00 | 2861.2 | 1694.74 | 870522.76 | 842914.9 | 39.29 | 2683.698 | 1789.128 | -479.064 | 42 | 194 | 26.4 | 57 | 26.9 | 56.5 | 0 | 0 | - | - | 28.8 | 51.7 | 0 | 0 | 0 | 0 | 25.9 | 27.7 | 26.8 | 1.54 | 2.1 | 0.6 | 0 | 26.1 | 27.4 | 26.6 | 1.56 | 1.6 | 0.6 | 26.7 | 26.6 | 26.6 | 1.56 | 1.57 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:25:00 | 2861.2 | 1741.34 | 870522.76 | 842961.12 | 39.4 | 2728.422 | 1744.404 | -607.75 | 41 | 194 | 26.4 | 57 | 26.9 | 56.5 | 0 | 0 | - | - | 28.8 | 51.8 | 0 | 0 | 0 | 0 | 25.9 | 27.7 | 26.8 | 1.54 | 2.1 | 0.5 | 0 | 26.1 | 27.4 | 26.6 | 1.56 | 1.6 | 0.6 | 26.7 | 26.5 | 26.6 | 1.56 | 1.56 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:30:00 | 2861.2 | 1802.32 | 870522.76 | 843022.7 | 39.51 | 2773.152 | 1699.674 | -796.717 | 39 | 194 | 26.4 | 57 | 27 | 56.4 | 0 | 0 | - | - | 28.8 | 51.8 | 0 | 0 | 0 | 0 | 25.9 | 27.7 | 26.8 | 1.54 | 2.1 | 0.5 | 0 | 26.1 | 27.4 | 26.6 | 1.56 | 1.6 | 0.7 | 26.6 | 26.5 | 26.6 | 1.56 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:35:00 | 2861.2 | 1878 | 870522.76 | 843098.04 | 39.62 | 2862.612 | 1610.214 | -772.659 | 38 | 194 | 26.4 | 57 | 27.1 | 56.4 | 0 | 0 | - | - | 28.8 | 51.9 | 0 | 0 | 0 | 0 | 25.9 | 27.6 | 26.7 | 1.54 | 2.1 | 0.6 | 0 | 26 | 27.4 | 26.6 | 1.56 | 1.6 | 0.7 | 26.6 | 26.4 | 26.5 | 1.56 | 1.56 | 1.56 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:40:00 | 2861.2 | 1937.56 | 870522.76 | 843157.82 | 39.73 | 2907.336 | 1565.49 | -724.775 | 36 | 194 | 26.5 | 56.9 | 27.1 | 56.3 | 0 | 0 | - | - | 28.7 | 51.9 | 0 | 0 | 0 | 0 | 25.9 | 27.6 | 26.7 | 1.54 | 2.1 | 0.6 | 0 | 26 | 27.4 | 26.6 | 1.56 | 1.6 | 0.7 | 26.6 | 26.4 | 26.5 | 1.56 | 1.56 | 1.56 | 1.58 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:45:00 | 2861.2 | 2007.1 | 870522.76 | 843227.78 | 39.85 | 2996.796 | 1476.03 | -895.489 | 35 | 194 | 26.5 | 56.8 | 27.2 | 56.2 | 0 | 0 | - | - | 28.8 | 51.9 | 0 | 0 | 0 | 0 | 25.9 | 27.6 | 26.7 | 1.53 | 2.1 | 0.6 | 0 | 26 | 27.4 | 26.6 | 1.56 | 1.7 | 0.7 | 26.6 | 26.4 | 26.5 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:50:00 | 2861.2 | 2088.62 | 870522.76 | 843308.72 | 39.97 | 3086.25 | 1386.576 | -925.515 | 33 | 194 | 26.6 | 56.8 | 27.3 | 56.1 | 0 | 0 | - | - | 28.8 | 51.9 | 0 | 0 | 0 | 0 | 25.8 | 27.6 | 26.7 | 1.53 | 2.1 | 0.6 | 0 | 26 | 27.3 | 26.5 | 1.55 | 1.6 | 0.7 | 26.6 | 26.3 | 26.3 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 18:55:00 | 2861.2 | 2166.54 | 870522.76 | 843387.2 | 40.09 | 3175.71 | 1297.116 | -983.855 | 31 | 194 | 26.7 | 56.7 | 27.3 | 56 | 0 | 0 | - | - | 28.8 | 51.9 | 0 | 0 | 0 | 0 | 25.8 | 27.6 | 26.7 | 1.53 | 2.1 | 0.6 | 0 | 26 | 27.3 | 26.5 | 1.55 | 1.6 | 0.7 | 26.6 | 26.4 | 26.3 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:00:00 | 2861.2 | 2224.7 | 870522.76 | 843446.52 | 40.21 | 3220.434 | 1252.392 | -621.895 | 30 | 194 | 26.7 | 56.5 | 27.5 | 55.9 | 0 | 0 | - | - | 28.8 | 52 | 0 | 0 | 0 | 0 | 25.8 | 27.5 | 26.6 | 1.53 | 2 | 0.5 | 0 | 25.9 | 27.2 | 26.4 | 1.55 | 1.6 | 0.7 | 26.6 | 26.4 | 26.2 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:05:00 | 2861.2 | 2279.02 | 870522.76 | 843498.78 | 40.34 | 3265.164 | 1207.662 | -595.02 | 29 | 194 | 26.8 | 56.5 | 27.5 | 55.7 | 0 | 0 | - | - | 28.8 | 52 | 0 | 0 | 0 | 0 | 25.8 | 27.4 | 26.6 | 1.53 | 2 | 0.6 | 0 | 25.9 | 27.2 | 26.4 | 1.55 | 1.5 | 0.7 | 26.7 | 26.5 | 26.2 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:10:00 | 2861.2 | 2325.62 | 870522.76 | 843545.34 | 40.46 | 3309.894 | 1162.932 | -567.768 | 28 | 194 | 26.9 | 56.4 | 27.6 | 55.7 | 0 | 0 | - | - | 28.8 | 52 | 0 | 0 | 0 | 0 | 25.8 | 27.4 | 26.6 | 1.54 | 1.9 | 0.5 | 0 | 25.9 | 27.2 | 26.4 | 1.56 | 1.4 | 0.6 | 26.7 | 26.6 | 26.2 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:15:00 | 2861.2 | 2372.4 | 870522.76 | 843592.88 | 40.58 | 3354.624 | 1118.208 | -647.437 | 27 | 194 | 26.9 | 56.4 | 27.6 | 55.7 | 0 | 0 | - | - | 28.8 | 52 | 0 | 0 | 0 | 0 | 25.9 | 27.3 | 26.5 | 1.53 | 1.8 | 0.6 | 0 | 25.9 | 27.2 | 26.3 | 1.55 | 1.4 | 0.6 | 26.8 | 26.7 | 26.2 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:20:00 | 2861.2 | 2424.8 | 870522.76 | 843644.22 | 40.7 | 3399.348 | 1073.478 | -542.706 | 25 | 194 | 26.9 | 56.4 | 27.6 | 55.7 | 0 | 0 | - | - | 28.8 | 52 | 0 | 0 | 0 | 0 | 25.9 | 27.3 | 26.5 | 1.54 | 1.7 | 0.6 | 0 | 26 | 27.2 | 26.3 | 1.55 | 1.4 | 0.7 | 26.9 | 26.8 | 26.2 | 1.56 | 1.57 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:25:00 | 2861.2 | 2473.22 | 870522.76 | 843693.3 | 40.82 | 3444.078 | 1028.748 | -608.71 | 24 | 194 | 26.9 | 56.4 | 27.6 | 55.7 | 0 | 0 | - | - | 28.8 | 52.1 | 120 | 120 | 0 | 0 | 25.9 | 27.3 | 26.4 | 1.54 | 1.8 | 0.6 | 0 | 26.1 | 27.2 | 26.3 | 1.56 | 1.5 | 0.8 | 27 | 26.9 | 26.1 | 1.55 | 1.56 | 1.55 | 1.57 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:30:00 | 2861.2 | 2524.1 | 870522.76 | 843744.74 | 41.31 | 3488.808 | 984.018 | -582.26 | 23 | 194 | 26.9 | 56.3 | 27.6 | 55.7 | 0 | 0 | - | - | 28.7 | 52.1 | 254 | 243 | 52 | 52 | 65.5 | 25.3 | 43 | 2.51 | 10.1 | 20.9 | 0 | 65.2 | 25.3 | 42.3 | 2.57 | 9.9 | 20.2 | 23.1 | 25.2 | 26.7 | 2.58 | 1.15 | 2.59 | 1.16 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:35:00 | 2861.2 | 2556.36 | 870522.76 | 843775.84 | 41.99 | 3533.532 | 939.294 | -209.03 | 22 | 194 | 26.8 | 56.3 | 27.5 | 55.7 | 0 | 0 | - | - | 28.7 | 52.2 | 254 | 243 | 48.9 | 48.6 | 65 | 23.9 | 40.6 | 2.28 | 9.6 | 24.3 | 48.6 | 67.6 | 23.9 | 43.1 | 2.46 | 9 | 24.4 | 21.9 | 23.7 | 26.8 | 2.35 | 1.13 | 2.51 | 1.15 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:40:00 | 2861.2 | 2574.92 | 870522.76 | 843794.5 | 42.63 | 3533.532 | 939.294 | -198.685 | 22 | 194 | 26.7 | 56.3 | 27.3 | 55.7 | 0 | 0 | - | - | 28.7 | 52.2 | 254 | 243 | 48.9 | 49.2 | 63.4 | 23.2 | 39.4 | 2.26 | 9.6 | 22.9 | 49 | 66.4 | 23.3 | 41.7 | 2.46 | 8.9 | 23.1 | 21.3 | 23.2 | 27 | 2.33 | 1.1 | 2.48 | 1.13 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:45:00 | 2861.2 | 2590.08 | 870522.76 | 843809.5 | 43.28 | 3563.352 | 909.474 | -227.893 | 22 | 194 | 26.6 | 56.3 | 27.2 | 55.7 | 0 | 0 | - | - | 28.8 | 52.2 | 254 | 243 | 48.9 | 49.2 | 63.4 | 23.2 | 39.4 | 2.26 | 9.6 | 22.9 | 49 | 66.4 | 23.3 | 41.7 | 2.46 | 8.9 | 23.1 | 20.9 | 22.7 | 27.1 | 2.32 | 1.09 | 2.48 | 1.12 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:50:00 | 2861.2 | 2610.6 | 870522.76 | 843830.12 | 43.92 | 3578.262 | 894.564 | -160.241 | 21 | 194 | 26.5 | 56.2 | 27.1 | 55.7 | 0 | 0 | - | - | 28.7 | 52.2 | 254 | 243 | 48.9 | 49.1 | 63.1 | 22.8 | 39.2 | 2.25 | 9.5 | 22.8 | 49.4 | 66 | 22.9 | 41.7 | 2.45 | 8.8 | 23 | 20.7 | 22.4 | 27.4 | 2.32 | 1.08 | 2.49 | 1.11 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 19:55:00 | 2861.2 | 2634.86 | 870522.76 | 843854.02 | 44.57 | 3600.627 | 872.199 | -222.445 | 21 | 194 | 26.5 | 56.1 | 27 | 55.7 | 0 | 0 | - | - | 28.7 | 52.2 | 254 | 243 | 49.5 | 49.7 | 63 | 22.6 | 39.1 | 2.25 | 9.5 | 22.7 | 49.4 | 66.2 | 22.7 | 41.8 | 2.46 | 8.7 | 23 | 20.4 | 22.2 | 27.2 | 2.32 | 1.08 | 2.48 | 1.11 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:00:00 | 2861.2 | 2667.88 | 870522.76 | 843888.34 | 45.23 | 3622.992 | 849.834 | -358.293 | 20 | 194 | 26.4 | 56.1 | 26.9 | 55.7 | 0 | 0 | - | - | 28.7 | 52.3 | 254 | 243 | 49.5 | 49.7 | 63.2 | 22.3 | 39.2 | 2.26 | 9.5 | 22.7 | 49.4 | 66.1 | 22.6 | 41.7 | 2.45 | 8.7 | 23.1 | 20.3 | 22.1 | 27.9 | 2.34 | 1.07 | 2.48 | 1.1 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:05:00 | 2861.2 | 2688.08 | 870522.76 | 843907.26 | 45.87 | 3667.722 | 805.104 | -2.98 | 19 | 194 | 26.3 | 56 | 26.8 | 55.6 | 0 | 0 | - | - | 28.6 | 52.3 | 254 | 243 | 49.5 | 49.7 | 63.5 | 22.2 | 39.5 | 2.28 | 9.4 | 22.8 | 49.7 | 66.2 | 22.3 | 41.7 | 2.45 | 8.6 | 23.1 | 20.2 | 21.9 | 27.7 | 2.33 | 1.07 | 2.49 | 1.1 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:10:00 | 2861.76 | 2691.6 | 870523.32 | 843910.86 | 46.51 | 3667.722 | 805.104 | -52.992 | 19 | 194 | 26.2 | 55.9 | 26.8 | 55.4 | 0 | 0 | - | - | 28.6 | 52.3 | 254 | 243 | 50 | 50.2 | 63.5 | 22.1 | 39.3 | 2.26 | 9.5 | 23 | 50.1 | 66.3 | 22.2 | 41.7 | 2.45 | 8.6 | 23.2 | 20 | 21.7 | 28.6 | 2.32 | 1.06 | 2.47 | 1.09 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:15:00 | 2861.76 | 2699.56 | 870523.32 | 843918.92 | 47.16 | 3667.722 | 805.104 | -193.021 | 19 | 194 | 26.2 | 55.8 | 26.7 | 55.3 | 0 | 0 | - | - | 28.6 | 52.3 | 254 | 243 | 49.5 | 49.7 | 63.4 | 21.8 | 39.2 | 2.26 | 9.5 | 23.1 | 49.6 | 66.2 | 22 | 41.6 | 2.44 | 8.6 | 23.4 | 19.8 | 21.6 | 28.6 | 2.32 | 1.06 | 2.48 | 1.09 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:20:00 | 2861.76 | 2706.88 | 870523.32 | 843926.1 | 47.79 | 3667.722 | 805.104 | -9.392 | 19 | 194 | 26.1 | 55.7 | 26.6 | 55.3 | 0 | 0 | - | - | 28.6 | 52.3 | 254 | 243 | 50 | 50.2 | 63.4 | 21.7 | 39.2 | 2.25 | 9.4 | 23 | 50.1 | 66.2 | 21.8 | 41.6 | 2.45 | 8.5 | 23.2 | 19.7 | 21.4 | 28.7 | 2.32 | 1.05 | 2.47 | 1.08 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:25:00 | 2861.78 | 2710.3 | 870523.34 | 843929.62 | 48.44 | 3667.722 | 805.104 | -75.387 | 19 | 194 | 26.1 | 55.5 | 26.5 | 55.3 | 0 | 0 | - | - | 28.5 | 52.3 | 254 | 243 | 50 | 50.2 | 63.5 | 21.6 | 39.3 | 2.26 | 9.4 | 23 | 50 | 66.1 | 21.7 | 41.6 | 2.44 | 8.6 | 23.3 | 19.4 | 21.2 | 29.1 | 2.31 | 1.04 | 2.46 | 1.08 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:30:00 | 2861.84 | 2714.66 | 870523.4 | 843933.86 | 49.08 | 3667.722 | 805.104 | -41.535 | 19 | 194 | 26 | 55.5 | 26.2 | 55.4 | 0 | 0 | - | - | 28.6 | 52.3 | 254 | 243 | 50 | 49.7 | 63.4 | 21.3 | 39.1 | 2.25 | 9.4 | 23.2 | 50 | 66 | 21.4 | 41.5 | 2.43 | 8.5 | 23.3 | 19.2 | 20.9 | 28.9 | 2.31 | 1.04 | 2.47 | 1.07 | 254 | 243 | 2400 | 2400
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:35:00 | 2861.84 | 2718.42 | 870523.4 | 843937.66 | 49.66 | 3675.176 | 797.65 | -114.667 | 19 | 194 | 25.9 | 55.4 | 25.9 | 55.6 | 0 | 0 | - | - | 28.5 | 52.3 | 254 | 243 | 50 | 50.2 | 63.3 | 21.2 | 39 | 2.24 | 9.4 | 23.2 | 49.2 | 66.1 | 21.2 | 41.6 | 2.43 | 8.6 | 23.3 | 19.8 | 20.9 | 28.8 | 2.31 | 1.06 | 1.76 | 0.78 | 254 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:40:00 | 2861.84 | 2726.02 | 870523.4 | 843945.3 | 50.03 | 3690.084 | 782.742 | -72.524 | 19 | 194 | 25.8 | 55.5 | 25.8 | 55.8 | 0 | 0 | - | - | 28.5 | 52.3 | 254 | 0 | 48.5 | 48.9 | 63 | 21.1 | 39.2 | 2.26 | 8.7 | 22.6 | 48.1 | 59.5 | 21.9 | 33.9 | 1.74 | 13.3 | 30.4 | 20.8 | 21.9 | 28.6 | 2.4 | 1.09 | 1.61 | 1.41 | 254 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:45:00 | 2861.86 | 2732.42 | 870523.42 | 843951.64 | 50.38 | 3704.992 | 767.834 | -48.136 | 19 | 194 | 25.8 | 55.6 | 26 | 55.4 | 0 | 0 | - | - | 28.5 | 52.3 | 254 | 0 | 45.9 | 45.9 | 64.1 | 22 | 40.6 | 2.34 | 8.7 | 22.4 | 45.7 | 33.6 | 39 | 30.3 | 1.61 | 17 | 7.2 | 21 | 22.1 | 28.7 | 2.4 | 1.1 | 1.48 | 1.43 | 254 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:50:00 | 2861.88 | 2740.08 | 870523.44 | 843959.44 | 50.75 | 3704.992 | 767.834 | -107.226 | 18 | 194 | 25.8 | 55.5 | 26.1 | 55.4 | 0 | 0 | - | - | 28.5 | 52.3 | 254 | 0 | 45.9 | 45.9 | 64.2 | 22.2 | 40.7 | 2.35 | 8.7 | 22.4 | 45.7 | 32.9 | 43.3 | 29.3 | 1.47 | 20.8 | 9.6 | 21 | 22.1 | 28.6 | 2.4 | 1.1 | 1.43 | 1.43 | 254 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 20:55:00 | 2861.88 | 2754.22 | 870523.44 | 843973.58 | 51.11 | 3712.446 | 760.38 | -210.325 | 18 | 194 | 25.8 | 55.5 | 26.1 | 55.3 | 0 | 0 | - | - | 28.5 | 52.2 | 254 | 0 | 45.9 | 45.9 | 64.2 | 22.2 | 40.6 | 2.35 | 8.7 | 22.4 | 45.7 | 32.6 | 42.6 | 28.7 | 1.43 | 20.1 | 10.2 | 20.9 | 22.1 | 27.9 | 2.4 | 1.09 | 1.43 | 1.43 | 254 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:00:00 | 2861.88 | 2767.78 | 870523.44 | 843987.48 | 51.47 | 3712.446 | 760.38 | -128.926 | 18 | 194 | 25.8 | 55.4 | 26 | 55.3 | 0 | 0 | - | - | 28.5 | 52.2 | 254 | 0 | 45.9 | 45.9 | 64.2 | 22.2 | 40.7 | 2.34 | 8.7 | 22.4 | 45.7 | 32.4 | 41.2 | 28.2 | 1.43 | 18.7 | 10 | 20.9 | 21.9 | 28 | 2.4 | 1.09 | 1.43 | 1.43 | 254 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:05:00 | 2861.88 | 2777.8 | 870523.44 | 843997 | 51.84 | 3734.811 | 738.015 | -103.101 | 17 | 194 | 25.7 | 55.4 | 26 | 55.4 | 0 | 0 | - | - | 28.4 | 52.2 | 254 | 0 | 45.9 | 45.9 | 64.1 | 22.2 | 40.7 | 2.34 | 8.6 | 22.3 | 45.7 | 32.1 | 40.2 | 27.9 | 1.43 | 17.8 | 9.8 | 20.8 | 21.9 | 28.3 | 2.4 | 1.09 | 1.42 | 1.43 | 254 | 0 | 2400 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:10:00 | 2861.88 | 2783.34 | 870523.44 | 844002.62 | 52.02 | 3749.721 | 723.105 | -86.537 | 17 | 194 | 25.7 | 55.5 | 25.9 | 55.4 | 0 | 0 | - | - | 28.4 | 52.2 | 254 | 0 | 45.9 | 45.9 | 64.1 | 22.1 | 40.6 | 2.34 | 8.6 | 22.4 | 45.7 | 32 | 39.5 | 27.8 | 1.43 | 17.1 | 9.7 | 22.9 | 22.8 | 28.1 | 1.55 | 1.44 | 1.45 | 1.46 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:15:00 | 2861.9 | 2786.1 | 870523.46 | 844005.34 | 52.14 | 3757.176 | 715.65 | -8.801 | 17 | 194 | 25.6 | 55.5 | 25.9 | 55.4 | 0 | 0 | - | - | 28.4 | 52.2 | 0 | 0 | 0 | 0 | 37.1 | 32.8 | 28.3 | 1.52 | 10 | 12.3 | 0 | 31.4 | 37.7 | 27.8 | 1.46 | 14.4 | 8.4 | 23.6 | 23.4 | 27.7 | 1.48 | 1.48 | 1.48 | 1.49 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:20:00 | 2861.9 | 2791.78 | 870523.46 | 844011.1 | 52.25 | 3757.176 | 715.65 | -56.123 | 17 | 194 | 25.6 | 55.6 | 25.9 | 55.5 | 0 | 0 | - | - | 28.4 | 52.1 | 0 | 0 | 0 | 0 | 30.7 | 36.1 | 29.1 | 1.46 | 12.5 | 7.1 | 0 | 30.7 | 35.1 | 27.8 | 1.48 | 11.3 | 7.2 | 23.8 | 23.7 | 27.3 | 1.49 | 1.49 | 1.49 | 1.5 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:25:00 | 2861.9 | 2796.98 | 870523.46 | 844016.28 | 52.37 | 3757.176 | 715.65 | -42.155 | 17 | 194 | 25.6 | 55.7 | 25.9 | 55.5 | 0 | 0 | - | - | 28.4 | 52.1 | 0 | 0 | 0 | 0 | 29.7 | 34.9 | 28.8 | 1.47 | 11.1 | 5.9 | 0 | 30.2 | 33.4 | 27.7 | 1.49 | 9.2 | 6.3 | 24 | 23.8 | 27.2 | 1.49 | 1.49 | 1.49 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:30:00 | 2861.9 | 2800.62 | 870523.46 | 844019.86 | 52.48 | 3757.176 | 715.65 | -25.059 | 17 | 194 | 25.6 | 55.7 | 25.9 | 55.6 | 0 | 0 | - | - | 28.4 | 52.1 | 0 | 0 | 0 | 0 | 29.2 | 34.1 | 28.7 | 1.48 | 10.1 | 5.3 | 0 | 29.7 | 32.1 | 27.7 | 1.5 | 7.9 | 5.8 | 24.1 | 23.9 | 27.2 | 1.5 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:35:00 | 2866.74 | 2801.46 | 870528.38 | 844020.62 | 52.59 | 3757.176 | 715.65 | 61.403 | 17 | 194 | 25.5 | 55.8 | 25.8 | 55.6 | 0 | 0 | - | - | 28.4 | 52.1 | 0 | 0 | 0 | 0 | 28.9 | 33.4 | 28.3 | 1.48 | 9.4 | 5 | 0 | 29.3 | 31.3 | 27.7 | 1.5 | 7.1 | 5.3 | 24.1 | 23.9 | 27.3 | 1.5 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:40:00 | 2867.78 | 2803.76 | 870529.34 | 844022.94 | 52.69 | 3757.176 | 715.65 | 8.657 | 17 | 194 | 25.5 | 55.8 | 25.8 | 55.6 | 0 | 0 | - | - | 28.3 | 52.1 | 0 | 0 | 0 | 0 | 28.7 | 32.9 | 28.1 | 1.48 | 8.8 | 4.6 | 0 | 28.9 | 30.8 | 27.6 | 1.5 | 6.5 | 4.9 | 24.1 | 24 | 27.3 | 1.5 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:45:00 | 2870.92 | 2804.3 | 870532.54 | 844023.46 | 52.78 | 3757.176 | 715.65 | 101.552 | 17 | 194 | 25.5 | 55.9 | 25.8 | 55.7 | 0 | 0 | - | - | 28.3 | 52.2 | 0 | 0 | 0 | 0 | 28.4 | 32.4 | 27.8 | 1.49 | 8.3 | 4.3 | 0 | 28.7 | 30.3 | 27.6 | 1.5 | 6.1 | 4.6 | 24.2 | 24 | 27.2 | 1.5 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:50:00 | 2879.02 | 2804.3 | 870540.9 | 844023.46 | 52.88 | 3757.176 | 715.65 | 166.906 | 17 | 194 | 25.5 | 55.9 | 25.8 | 55.7 | 0 | 0 | - | - | 28.3 | 52.1 | 0 | 0 | 0 | 0 | 28.2 | 32.1 | 27.7 | 1.49 | 8 | 4.1 | 0 | 28.3 | 30.1 | 27.4 | 1.5 | 5.7 | 4.3 | 24.2 | 24 | 27.2 | 1.5 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 21:55:00 | 2884.26 | 2804.56 | 870545.84 | 844023.74 | 52.98 | 3749.721 | 723.105 | -88.23 | 17 | 194 | 25.4 | 55.9 | 25.8 | 55.7 | 0 | 0 | - | - | 28.3 | 52.1 | 0 | 0 | 0 | 0 | 28.2 | 32 | 27.7 | 1.49 | 7.8 | 4 | 0 | 28.2 | 29.7 | 27.4 | 1.5 | 5.4 | 4.2 | 24.2 | 24 | 27.3 | 1.5 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:00:00 | 2884.3 | 2815.58 | 870545.86 | 844034.96 | 53.07 | 3757.176 | 715.65 | -114.67 | 17 | 194 | 25.4 | 55.9 | 25.7 | 55.8 | 0 | 0 | - | - | 28.3 | 52.2 | 0 | 0 | 0 | 0 | 28.2 | 31.8 | 27.7 | 1.49 | 7.7 | 4 | 0 | 28.1 | 29.6 | 27.4 | 1.5 | 5.3 | 4 | 24.2 | 24 | 27.3 | 1.5 | 1.5 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:05:00 | 2884.3 | 2818.8 | 870545.86 | 844037.98 | 53.16 | 3712.446 | 760.38 | -11.739 | 17 | 194 | 25.4 | 56 | 25.7 | 55.8 | 0 | 0 | - | - | 28.2 | 52.2 | 0 | 0 | 0 | 0 | 28.1 | 31.7 | 27.7 | 1.49 | 7.5 | 3.9 | 0 | 27.9 | 29.3 | 27.4 | 1.5 | 5.1 | 3.9 | 24.2 | 24 | 27.2 | 1.5 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:10:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.25 | 3712.446 | 760.38 | -0.034 | 17 | 194 | 25.4 | 56 | 25.7 | 55.9 | 0 | 0 | - | - | 28.2 | 52.2 | 0 | 0 | 0 | 0 | 28 | 31.7 | 27.6 | 1.49 | 7.5 | 3.8 | 0 | 27.8 | 29.2 | 27.3 | 1.5 | 4.9 | 3.9 | 24.2 | 24.1 | 27.2 | 1.51 | 1.51 | 1.5 | 1.51 | 0 | 0 | 0 | 0
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:15:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.041 | 17 | 194 | 25.3 | 56 | 25.7 | 55.9 | 0 | 0 | - | - | 28.1 | 52.2 | 0 | 0 | 0 | 0 | 27.9 | 31.6 | 27.6 | 1.49 | 7.4 | 3.8 | 0 | 27.7 | 29.1 | 27.3 | 1.5 | 4.7 | 3.7 | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:20:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.034 | 17 | 194 | 25.3 | 56.1 | 25.7 | 55.8 | 0 | 0 | - | - | 28 | 52.4 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:25:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.3 | 56.1 | 25.6 | 55.9 | 0 | 0 | - | - | 27.9 | 52.5 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:30:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.3 | 56.2 | 25.6 | 55.8 | 0 | 0 | - | - | 27.7 | 52.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:35:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.2 | 56.1 | 25.6 | 55.9 | 0 | 0 | - | - | 27.7 | 52.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:40:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.2 | 56.2 | 25.6 | 55.8 | 0 | 0 | - | - | 27.6 | 52.7 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:45:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.2 | 56.2 | 25.6 | 55.9 | 0 | 0 | - | - | 27.5 | 52.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:50:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.2 | 56.2 | 25.6 | 55.9 | 0 | 0 | - | - | 27.4 | 52.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 22:55:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.1 | 56.3 | 25.6 | 55.9 | 0 | 0 | - | - | 27.3 | 52.9 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:00:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.1 | 56.2 | 25.6 | 55.9 | 0 | 0 | - | - | 27.3 | 53 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:05:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.1 | 56.3 | 25.6 | 55.9 | 0 | 0 | - | - | 27.2 | 53 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:10:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.1 | 56.2 | 25.6 | 55.9 | 0 | 0 | - | - | 27.2 | 53 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:15:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.1 | 56.3 | 25.6 | 55.9 | 0 | 0 | - | - | 27.2 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:20:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.1 | 56.3 | 25.5 | 55.8 | 0 | 0 | - | - | 27.1 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:25:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25.1 | 56.3 | 25.5 | 55.9 | 0 | 0 | - | - | 27 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:30:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25 | 56.3 | 25.5 | 55.9 | 0 | 0 | - | - | 27 | 53.1 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:35:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25 | 56.3 | 25.5 | 55.9 | 0 | 0 | - | - | 27 | 53.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:40:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25 | 56.4 | 25.5 | 55.9 | 0 | 0 | - | - | 26.9 | 53.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:45:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25 | 56.4 | 25.5 | 55.9 | 0 | 0 | - | - | 26.9 | 53.2 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:50:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 25 | 56.4 | 25.5 | 55.9 | 0 | 0 | - | - | 26.9 | 53.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Amleang 82MW-03 | / | SACU-29/B29-ESS01 | 2026-06-02 23:55:00 | 2884.3 | 2819.34 | 870545.86 | 844038.5 | 53.29 | 3712.446 | 760.38 | -0.027 | 17 | 194 | 24.9 | 56.4 | 25.5 | 55.8 | 0 | 0 | - | - | 26.8 | 53.3 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -