## 5 minutes
Time range: | 2026-06-03 00:00:00 - 2026-06-03 23:59:59
Export time: | 2026-06-04 00:34:28
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Device status | Voltage(V) | Current(A) | SOC(%) | SOH(%) | SOE(%) | DOD(%) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge Power(kW) | Module with the highest temperature(°C) | Position of the module with the highest temperature | Module with the lowest temperature(°C) | Position of the module with the lowest temperature | Lowest battery pack voltage(V) | Position where the lowest battery pack voltage was detected | Highest battery pack voltage(V) | Position where the highest battery pack voltage was detected | Average Temperature(°C) | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge(kWh) | Total discharge(kWh) | ISO insulation resistance(MΩ)
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:00:00 | Operating | 1337 | -14.6 | 17 | 99 | 15 | 90 | 627.314 | 110.702 | -19.494 | 24.9 | 5 | 24.1 | 4 | 167.1 | 5 | 167.2 | 8 | 0.8 | 0 | 0.22 | 137526.44 | 133201.44 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:05:00 | Operating | 1340.7 | 2.9 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 3.821 | 24.9 | 7 | 24.2 | 2 | 167.5 | 5 | 167.7 | 8 | 0.7 | 0 | 1.44 | 137526.44 | 133202.56 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:10:00 | Operating | 1337.5 | -26.1 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -34.922 | 25 | 5 | 24.2 | 2 | 167.2 | 5 | 167.3 | 8 | 0.8 | 0.58 | 2.16 | 137527.02 | 133203.28 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:15:00 | Operating | 1334.6 | -18.3 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -24.394 | 25 | 5 | 24.2 | 2 | 166.8 | 5 | 166.9 | 8 | 0.8 | 0.58 | 4.5 | 137527.02 | 133205.7 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:20:00 | Operating | 1333.2 | -25.2 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -33.584 | 25 | 5 | 24.2 | 2 | 166.6 | 5 | 166.8 | 8 | 0.8 | 0.58 | 6.08 | 137527.02 | 133207.34 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:25:00 | Operating | 1334.2 | -10.3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -13.717 | 25 | 5 | 24.3 | 4 | 166.7 | 6 | 166.8 | 8 | 0.7 | 0.58 | 8.66 | 137527.02 | 133209.78 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:30:00 | Operating | 1335.1 | -20.3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -27.035 | 25 | 5 | 24.3 | 2 | 166.8 | 6 | 167 | 8 | 0.7 | 0.66 | 9.46 | 137527.1 | 133210.58 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:35:00 | Operating | 1334.9 | -6.7 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -8.986 | 25.1 | 5 | 24.4 | 2 | 166.7 | 6 | 166.9 | 8 | 0.7 | 0.66 | 11.06 | 137527.1 | 133212.18 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:40:00 | Operating | 1335.1 | -2.6 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -3.432 | 25.1 | 7 | 24.4 | 2 | 166.8 | 6 | 167 | 8 | 0.7 | 0.66 | 12.8 | 137527.1 | 133213.94 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:45:00 | Operating | 1335.3 | -6.8 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | -9.134 | 25 | 5 | 24.4 | 4 | 166.9 | 6 | 167 | 8 | 0.6 | 0.78 | 13.96 | 137527.22 | 133215.08 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:50:00 | Operating | 1335.2 | -8 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | -10.695 | 25.1 | 5 | 24.4 | 4 | 166.9 | 6 | 167 | 8 | 0.7 | 0.78 | 14.58 | 137527.22 | 133215.74 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 00:55:00 | Operating | 1331 | -13.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -18.389 | 25.1 | 7 | 24.4 | 4 | 166.3 | 6 | 166.5 | 8 | 0.7 | 0.78 | 16.32 | 137527.22 | 133217.44 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:00:00 | Operating | 1331.6 | -16.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -22.104 | 25.2 | 7 | 24.5 | 2 | 166.4 | 6 | 166.6 | 8 | 0.7 | 0.8 | 17.42 | 137527.24 | 133218.54 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:05:00 | Operating | 1330.2 | -13.2 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -17.522 | 25.2 | 5 | 24.5 | 4 | 166.2 | 6 | 166.4 | 8 | 0.7 | 0.8 | 19.5 | 137527.24 | 133220.68 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:10:00 | Operating | 1331.3 | -13 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -17.133 | 25.2 | 5 | 24.5 | 2 | 166.4 | 6 | 166.5 | 8 | 0.7 | 0.82 | 20.74 | 137527.26 | 133221.88 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:15:00 | Operating | 1328.5 | -21.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -28.886 | 25.2 | 5 | 24.6 | 2 | 166 | 6 | 166.2 | 8 | 0.6 | 0.82 | 22.32 | 137527.26 | 133223.44 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:20:00 | Operating | 1329.5 | -6.9 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -9.213 | 25.2 | 5 | 24.6 | 4 | 166.1 | 6 | 166.3 | 8 | 0.6 | 0.82 | 24.14 | 137527.26 | 133225.26 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:25:00 | Operating | 1332.6 | -8.3 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -11.06 | 25.3 | 5 | 24.6 | 4 | 166.6 | 6 | 166.7 | 8 | 0.7 | 0.96 | 24.66 | 137527.4 | 133225.8 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:30:00 | Operating | 1340 | 14.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 19.71 | 25.3 | 7 | 24.6 | 2 | 167.4 | 6 | 167.6 | 7 | 0.7 | 1.86 | 24.8 | 137528.36 | 133225.92 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:35:00 | Operating | 1341 | 11.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 15.616 | 25.3 | 5 | 24.6 | 4 | 167.5 | 6 | 167.7 | 8 | 0.7 | 3 | 24.8 | 137529.44 | 133225.92 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:40:00 | Operating | 1343.4 | 18.2 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 24.403 | 25.3 | 5 | 24.6 | 2 | 167.8 | 6 | 168 | 8 | 0.7 | 4.04 | 24.82 | 137530.48 | 133225.94 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:45:00 | Operating | 1347.3 | 17.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 23.925 | 25.3 | 5 | 24.6 | 4 | 168.3 | 6 | 168.5 | 7 | 0.7 | 6.38 | 24.82 | 137532.86 | 133225.94 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:50:00 | Operating | 1349.3 | 12.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 16.741 | 25.4 | 7 | 24.6 | 2 | 168.6 | 6 | 168.8 | 7 | 0.8 | 8.52 | 24.82 | 137535 | 133225.94 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 01:55:00 | Operating | 1346.3 | 2.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 3.582 | 25.3 | 5 | 24.6 | 4 | 168.2 | 6 | 168.4 | 8 | 0.7 | 9.2 | 24.84 | 137535.64 | 133225.98 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:00:00 | Operating | 1340.4 | -16.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -22.712 | 25.3 | 5 | 24.7 | 2 | 167.5 | 5 | 167.7 | 8 | 0.7 | 9.34 | 25.5 | 137535.78 | 133226.62 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:05:00 | Operating | 1341.4 | 4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.301 | 25.3 | 5 | 24.7 | 2 | 167.5 | 5 | 167.7 | 8 | 0.8 | 9.36 | 26.48 | 137535.8 | 133227.6 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:10:00 | Operating | 1342.9 | 4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.331 | 25.4 | 5 | 24.7 | 2 | 167.8 | 6 | 168 | 8 | 0.7 | 10.14 | 26.72 | 137536.58 | 133227.86 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:15:00 | Operating | 1339.2 | -13.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -18.074 | 25.4 | 5 | 24.6 | 2 | 167.4 | 6 | 167.5 | 8 | 0.7 | 10.2 | 27.26 | 137536.64 | 133228.38 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:20:00 | Operating | 1340.4 | 5.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 7.59 | 25.4 | 5 | 24.7 | 2 | 167.5 | 6 | 167.6 | 8 | 0.7 | 10.22 | 28.12 | 137536.68 | 133229.24 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:25:00 | Operating | 1341.7 | -4.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -6.401 | 25.4 | 5 | 24.7 | 2 | 167.7 | 6 | 167.8 | 8 | 0.7 | 10.86 | 28.14 | 137537.3 | 133229.26 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:30:00 | Operating | 1340 | -2.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -3.209 | 25.4 | 5 | 24.7 | 2 | 167.5 | 6 | 167.6 | 8 | 0.6 | 10.9 | 28.6 | 137537.34 | 133229.74 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:35:00 | Operating | 1341.6 | 11.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 15.255 | 25.5 | 7 | 24.7 | 2 | 167.6 | 6 | 167.7 | 8 | 0.8 | 11 | 28.94 | 137537.44 | 133230.06 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:40:00 | Operating | 1343.4 | 4.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 6.47 | 25.4 | 5 | 24.7 | 2 | 167.9 | 6 | 168 | 8 | 0.7 | 11.7 | 29 | 137538.14 | 133230.12 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:45:00 | Operating | 1342.2 | 2.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 3.623 | 25.5 | 5 | 24.8 | 2 | 167.7 | 6 | 167.9 | 8 | 0.8 | 11.88 | 29.22 | 137538.34 | 133230.34 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:50:00 | Operating | 1340.3 | -8.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -11.407 | 25.4 | 5 | 24.8 | 2 | 167.5 | 6 | 167.7 | 8 | 0.8 | 12.24 | 29.52 | 137538.68 | 133230.64 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 02:55:00 | Operating | 1341.6 | 6.1 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 8.168 | 25.5 | 5 | 24.8 | 2 | 167.6 | 6 | 167.8 | 8 | 0.8 | 12.4 | 30.06 | 137538.84 | 133231.18 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:00:00 | Operating | 1343.1 | 8.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 11.382 | 25.5 | 5 | 24.7 | 2 | 167.8 | 6 | 168 | 8 | 0.7 | 12.78 | 30.32 | 137539.22 | 133231.44 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:05:00 | Operating | 1340.9 | -1.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -1.804 | 25.5 | 5 | 24.8 | 2 | 167.6 | 6 | 167.7 | 8 | 0.8 | 13.06 | 30.88 | 137539.5 | 133232 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:10:00 | Operating | 1339.4 | -3.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -5.223 | 25.5 | 5 | 24.7 | 2 | 167.4 | 6 | 167.6 | 8 | 0.7 | 13.16 | 31.26 | 137539.6 | 133232.4 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:15:00 | Operating | 1338.5 | -3.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -4.626 | 25.5 | 5 | 24.8 | 2 | 167.3 | 6 | 167.4 | 8 | 0.7 | 13.2 | 31.88 | 137539.64 | 133233.02 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:20:00 | Operating | 1339.4 | 4.2 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.605 | 25.6 | 5 | 24.8 | 2 | 167.3 | 6 | 167.5 | 8 | 0.7 | 13.36 | 32.46 | 137539.8 | 133233.58 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:25:00 | Operating | 1349.8 | 23 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 31.043 | 25.5 | 5 | 24.9 | 2 | 168.6 | 6 | 168.8 | 7 | 0.8 | 15.8 | 32.46 | 137542.24 | 133233.58 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:30:00 | Operating | 1345.7 | 2.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 3.801 | 25.6 | 7 | 24.8 | 2 | 168.2 | 6 | 168.3 | 8 | 0.7 | 16.54 | 32.62 | 137542.98 | 133233.74 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:35:00 | Operating | 1345.1 | 1.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 1.727 | 25.5 | 7 | 24.8 | 2 | 168.1 | 6 | 168.2 | 8 | 0.7 | 16.94 | 32.74 | 137543.38 | 133233.86 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:40:00 | Operating | 1353.8 | 28.4 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | 38.485 | 25.6 | 5 | 24.9 | 2 | 169.1 | 6 | 169.3 | 7 | 0.7 | 18.98 | 32.74 | 137545.52 | 133233.86 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:45:00 | Operating | 1362.6 | 57.3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 78.093 | 25.6 | 7 | 24.8 | 2 | 170.1 | 1 | 170.4 | 7 | 0.7 | 24.2 | 32.74 | 137550.64 | 133233.86 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:50:00 | Operating | 1366.8 | 58.3 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 79.651 | 25.6 | 7 | 24.8 | 2 | 170.7 | 1 | 171 | 7 | 0.8 | 31.6 | 32.74 | 137558.04 | 133233.86 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 03:55:00 | Operating | 1365.1 | 44.6 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 60.897 | 25.6 | 5 | 24.9 | 2 | 170.5 | 1 | 170.7 | 7 | 0.8 | 36.68 | 32.74 | 137563.12 | 133233.86 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:00:00 | Operating | 1371.9 | 61.9 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 84.958 | 25.6 | 5 | 24.9 | 2 | 171.3 | 6 | 171.5 | 7 | 0.8 | 43.08 | 32.74 | 137569.82 | 133233.86 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:05:00 | Operating | 1361.2 | -1.3 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -1.798 | 25.6 | 5 | 24.9 | 2 | 169.9 | 1 | 170.1 | 7 | 0.7 | 45.84 | 32.96 | 137572.28 | 133234.08 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:10:00 | Operating | 1350.9 | -28.2 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -38.272 | 25.7 | 5 | 24.9 | 2 | 168.8 | 1 | 169 | 7 | 0.8 | 45.84 | 35.38 | 137572.28 | 133236.5 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:15:00 | Operating | 1350.5 | -12.7 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -17.123 | 25.7 | 7 | 25 | 2 | 168.7 | 1 | 169 | 7 | 0.7 | 45.84 | 37.88 | 137572.28 | 133239 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:20:00 | Operating | 1347.1 | -18.3 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | -24.59 | 25.7 | 5 | 25 | 2 | 168.3 | 1 | 168.6 | 7 | 0.9 | 45.84 | 40.36 | 137572.28 | 133241.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:25:00 | Operating | 1339.2 | -49.5 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | -66.226 | 25.7 | 5 | 25 | 2 | 167.4 | 1 | 167.7 | 7 | 0.8 | 45.84 | 43.62 | 137572.28 | 133244.74 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:30:00 | Operating | 1332.5 | -51.2 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -68.516 | 25.8 | 5 | 25.1 | 2 | 166.5 | 1 | 166.7 | 7 | 0.8 | 45.84 | 49.04 | 137572.28 | 133250.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:35:00 | Operating | 1328.8 | -49.3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -65.509 | 25.9 | 5 | 25.2 | 2 | 166.1 | 6 | 166.3 | 8 | 0.8 | 45.84 | 54.02 | 137572.28 | 133255.14 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:40:00 | Operating | 1329.8 | -34.7 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -46.189 | 25.9 | 5 | 25.2 | 2 | 166.2 | 5 | 166.4 | 8 | 0.7 | 45.84 | 58.56 | 137572.28 | 133259.8 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:45:00 | Operating | 1329.7 | -25.1 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -33.366 | 26 | 5 | 25.3 | 2 | 166.1 | 5 | 166.4 | 8 | 0.8 | 45.84 | 61.86 | 137572.28 | 133263.1 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:50:00 | Operating | 1330.3 | -13 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -17.316 | 26 | 5 | 25.3 | 2 | 166.2 | 5 | 166.4 | 8 | 0.6 | 45.84 | 64.92 | 137572.28 | 133266.1 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 04:55:00 | Operating | 1333.7 | -1.8 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -2.431 | 26.1 | 5 | 25.4 | 2 | 166.6 | 5 | 166.8 | 8 | 0.8 | 45.84 | 65.66 | 137572.28 | 133266.8 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:00:00 | Operating | 1335.7 | -0.8 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -1.12 | 26 | 5 | 25.4 | 2 | 166.9 | 5 | 167.1 | 8 | 0.7 | 46.12 | 65.88 | 137572.56 | 133267 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:05:00 | Operating | 1331.4 | -11.2 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -14.865 | 26.1 | 7 | 25.3 | 2 | 166.4 | 5 | 166.6 | 8 | 0.8 | 46.18 | 67.12 | 137572.62 | 133268.24 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:10:00 | Operating | 1323.7 | -41.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -55.213 | 26.1 | 5 | 25.4 | 2 | 165.4 | 6 | 165.6 | 8 | 0.7 | 46.18 | 69.5 | 137572.62 | 133270.62 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:15:00 | Operating | 1331.2 | -2.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -3.792 | 26.1 | 5 | 25.4 | 2 | 166.4 | 6 | 166.5 | 8 | 0.7 | 46.24 | 71.08 | 137572.68 | 133272.2 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:20:00 | Operating | 1331.5 | -3.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -5.005 | 26.1 | 5 | 25.4 | 2 | 166.3 | 6 | 166.5 | 8 | 0.7 | 46.26 | 71.5 | 137572.7 | 133272.62 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:25:00 | Operating | 1331.1 | -7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -9.383 | 26.1 | 5 | 25.4 | 2 | 166.3 | 6 | 166.5 | 8 | 0.7 | 46.26 | 72.12 | 137572.7 | 133273.26 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:30:00 | Operating | 1329.5 | -10 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -13.357 | 26.1 | 5 | 25.5 | 2 | 166.1 | 6 | 166.3 | 8 | 0.6 | 46.26 | 73.2 | 137572.7 | 133274.32 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:35:00 | Operating | 1332.9 | 3.4 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | 4.591 | 26.2 | 7 | 25.4 | 2 | 166.5 | 6 | 166.7 | 8 | 0.8 | 46.32 | 73.66 | 137572.76 | 133274.78 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:40:00 | Operating | 1330.7 | -6.8 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -8.992 | 26.2 | 7 | 25.5 | 2 | 166.3 | 6 | 166.5 | 8 | 0.7 | 46.38 | 74.12 | 137572.82 | 133275.26 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:45:00 | Operating | 1331 | -5.3 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -7.054 | 26.1 | 5 | 25.5 | 2 | 166.3 | 6 | 166.5 | 8 | 0.6 | 46.38 | 74.56 | 137572.82 | 133275.72 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:50:00 | Operating | 1331 | -2 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -2.719 | 26.2 | 7 | 25.5 | 2 | 166.3 | 6 | 166.5 | 8 | 0.7 | 46.38 | 75.24 | 137572.82 | 133276.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 05:55:00 | Operating | 1330.1 | -0.1 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -0.069 | 26.1 | 5 | 25.5 | 2 | 166.2 | 6 | 166.4 | 8 | 0.6 | 46.38 | 75.96 | 137572.82 | 133277.1 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:00:00 | Operating | 1329.8 | -3.8 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -5.097 | 26.2 | 5 | 25.5 | 4 | 166.2 | 6 | 166.4 | 8 | 0.7 | 46.42 | 76.6 | 137572.86 | 133277.72 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:05:00 | Operating | 1339.5 | 24.4 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | 32.709 | 26.2 | 5 | 25.5 | 2 | 167.4 | 6 | 167.5 | 8 | 0.7 | 47.48 | 76.86 | 137573.92 | 133277.98 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:10:00 | Operating | 1344.4 | 25.3 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 34.005 | 26.2 | 5 | 25.5 | 2 | 168 | 6 | 168.1 | 8 | 0.7 | 50.1 | 76.86 | 137576.64 | 133277.98 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:15:00 | Operating | 1349.1 | 23.9 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 32.183 | 26.2 | 5 | 25.5 | 2 | 168.5 | 1 | 168.8 | 7 | 0.7 | 53.92 | 76.86 | 137580.46 | 133277.98 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:20:00 | Operating | 1354 | 35.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 47.993 | 26.2 | 7 | 25.5 | 2 | 169.1 | 1 | 169.4 | 7 | 0.7 | 58.18 | 76.86 | 137584.78 | 133277.98 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:25:00 | Operating | 1350.3 | 15.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 20.826 | 26.2 | 5 | 25.5 | 2 | 168.7 | 1 | 168.9 | 7 | 0.7 | 60.3 | 76.86 | 137586.8 | 133277.98 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:30:00 | Operating | 1351.2 | 17.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 23.574 | 26.2 | 5 | 25.5 | 2 | 168.8 | 1 | 169 | 7 | 0.7 | 61.64 | 76.86 | 137588.08 | 133277.98 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:35:00 | Operating | 1354.9 | 25.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 33.993 | 26.2 | 5 | 25.5 | 2 | 169.3 | 1 | 169.6 | 7 | 0.7 | 64.22 | 76.86 | 137590.76 | 133277.98 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:40:00 | Operating | 1356.5 | 27.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 36.753 | 26.2 | 5 | 25.5 | 2 | 169.5 | 1 | 169.7 | 7 | 0.8 | 66.94 | 76.86 | 137593.48 | 133277.98 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:45:00 | Operating | 1361 | 29.1 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | 39.565 | 26.2 | 5 | 25.5 | 2 | 169.9 | 6 | 170.1 | 7 | 0.6 | 70.96 | 76.86 | 137597.54 | 133277.98 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:50:00 | Operating | 1359 | 17.7 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 23.996 | 26.3 | 7 | 25.5 | 2 | 169.9 | 6 | 170.1 | 7 | 0.8 | 73.88 | 76.86 | 137600.42 | 133277.98 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 06:55:00 | Operating | 1353.4 | -8.6 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -11.591 | 26.3 | 5 | 25.6 | 2 | 169.1 | 6 | 169.3 | 7 | 0.7 | 75.18 | 76.98 | 137601.62 | 133278.1 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:00:00 | Operating | 1348.3 | -23.6 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -26.797 | 26.3 | 5 | 25.6 | 2 | 168.5 | 1 | 168.7 | 7 | 0.6 | 75.24 | 77.78 | 137601.68 | 133279 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:05:00 | Operating | 1348.4 | -5.3 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -7.18 | 26.3 | 5 | 25.6 | 2 | 168.5 | 1 | 168.7 | 7 | 0.7 | 75.24 | 79.36 | 137601.68 | 133280.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:10:00 | Operating | 1346.6 | -3.8 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -5.049 | 26.3 | 5 | 25.7 | 2 | 168.3 | 1 | 168.5 | 7 | 0.7 | 75.24 | 80.9 | 137601.68 | 133282.02 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:15:00 | Operating | 1348.6 | -6.3 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -8.489 | 26.4 | 7 | 25.6 | 2 | 168.5 | 1 | 168.7 | 7 | 0.7 | 75.92 | 80.94 | 137602.36 | 133282.06 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:20:00 | Operating | 1347.9 | -8.9 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -11.977 | 26.3 | 5 | 25.7 | 2 | 168.5 | 1 | 168.6 | 7 | 0.8 | 76.18 | 81.2 | 137602.62 | 133282.34 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:25:00 | Operating | 1342.1 | -13.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -18.076 | 26.4 | 5 | 25.6 | 2 | 167.7 | 1 | 167.9 | 7 | 0.7 | 76.18 | 83.14 | 137602.62 | 133284.26 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:30:00 | Operating | 1342.9 | -14.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -19.847 | 26.4 | 7 | 25.7 | 2 | 167.8 | 1 | 168 | 7 | 0.7 | 76.18 | 84.02 | 137602.62 | 133285.14 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:35:00 | Operating | 1341.8 | -11.6 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -15.505 | 26.4 | 5 | 25.7 | 2 | 167.7 | 1 | 167.8 | 7 | 0.7 | 76.48 | 85.14 | 137602.92 | 133286.32 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:40:00 | Operating | 1344 | -1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -1.372 | 26.4 | 5 | 25.7 | 2 | 167.9 | 1 | 168.1 | 7 | 0.7 | 76.58 | 86.02 | 137603.02 | 133287.14 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:45:00 | Operating | 1346.5 | 1.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 2.422 | 26.4 | 7 | 25.6 | 2 | 168.3 | 6 | 168.4 | 7 | 0.8 | 77.22 | 86.1 | 137603.66 | 133287.22 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:50:00 | Operating | 1349.4 | 5.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 7.883 | 26.4 | 5 | 25.7 | 2 | 168.6 | 6 | 168.8 | 7 | 0.7 | 78.24 | 86.1 | 137604.68 | 133287.22 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 07:55:00 | Operating | 1348.9 | 5.4 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 7.327 | 26.4 | 5 | 25.7 | 2 | 168.5 | 6 | 168.7 | 7 | 0.7 | 78.6 | 86.14 | 137605.06 | 133287.26 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:00:00 | Operating | 1349.8 | 12.3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 16.572 | 26.4 | 5 | 25.7 | 2 | 168.7 | 6 | 168.8 | 7 | 0.7 | 79 | 86.18 | 137605.44 | 133287.3 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:05:00 | Operating | 1347.8 | -8.4 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -11.354 | 26.4 | 5 | 25.7 | 2 | 168.4 | 6 | 168.6 | 7 | 0.7 | 79.56 | 86.22 | 137606 | 133287.38 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:10:00 | Operating | 1346 | -3.4 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -4.565 | 26.5 | 7 | 25.7 | 2 | 168.2 | 1 | 168.4 | 8 | 0.8 | 79.56 | 87.14 | 137606 | 133288.26 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:15:00 | Operating | 1347.4 | 4.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 5.303 | 26.4 | 5 | 25.8 | 2 | 168.4 | 1 | 168.5 | 7 | 0.6 | 79.78 | 87.56 | 137606.22 | 133288.68 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:20:00 | Operating | 1345.1 | -0.3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -0.451 | 26.4 | 5 | 25.8 | 2 | 168.1 | 1 | 168.2 | 7 | 0.6 | 79.8 | 88.24 | 137606.24 | 133289.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:25:00 | Operating | 1347.7 | 5.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 6.928 | 26.5 | 7 | 25.8 | 2 | 168.4 | 1 | 168.5 | 7 | 0.7 | 80.18 | 88.24 | 137606.64 | 133289.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:30:00 | Operating | 1352 | 13.7 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | 18.553 | 26.5 | 5 | 25.7 | 2 | 168.9 | 6 | 169.1 | 7 | 0.8 | 81.44 | 88.24 | 137607.94 | 133289.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:35:00 | Operating | 1354.5 | 22.9 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | 31.068 | 26.5 | 5 | 25.8 | 2 | 169.2 | 6 | 169.4 | 7 | 0.7 | 82.5 | 88.24 | 137608.94 | 133289.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:40:00 | Operating | 1358.6 | 27.3 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 37.145 | 26.5 | 5 | 25.8 | 2 | 169.7 | 6 | 169.9 | 7 | 0.7 | 84.54 | 88.24 | 137611.1 | 133289.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:45:00 | Operating | 1357.6 | 14.3 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 19.38 | 26.5 | 7 | 25.8 | 2 | 169.6 | 6 | 169.8 | 8 | 0.7 | 86.76 | 88.24 | 137613.2 | 133289.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:50:00 | Operating | 1364.1 | 36.6 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 49.933 | 26.5 | 5 | 25.8 | 2 | 170.4 | 6 | 170.6 | 7 | 0.7 | 90.08 | 88.24 | 137616.52 | 133289.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 08:55:00 | Operating | 1367.2 | 39.4 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 54.047 | 26.6 | 5 | 25.8 | 2 | 170.8 | 6 | 171 | 7 | 0.7 | 94.42 | 88.24 | 137621.02 | 133289.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:00:00 | Operating | 1369.6 | 45.7 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 62.57 | 26.6 | 5 | 25.9 | 2 | 171.1 | 6 | 171.3 | 7 | 0.8 | 98.88 | 88.24 | 137625.72 | 133289.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:05:00 | Operating | 1369.4 | 34.7 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 47.505 | 26.6 | 5 | 25.9 | 2 | 171.1 | 6 | 171.3 | 7 | 0.8 | 104.5 | 88.24 | 137630.94 | 133289.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:10:00 | Operating | 1368 | 25.9 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 35.49 | 26.6 | 7 | 25.8 | 2 | 170.9 | 6 | 171.1 | 7 | 0.7 | 106.84 | 88.26 | 137633.28 | 133289.38 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:15:00 | Operating | 1368.8 | 31.1 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 42.511 | 26.6 | 5 | 25.9 | 2 | 171.1 | 6 | 171.2 | 7 | 0.7 | 109.02 | 88.26 | 137635.46 | 133289.38 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:20:00 | Operating | 1361.7 | -16.4 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -22.365 | 26.6 | 5 | 25.9 | 2 | 170.2 | 6 | 170.3 | 7 | 0.7 | 110.08 | 88.3 | 137636.52 | 133289.46 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:25:00 | Operating | 1368.4 | 41.1 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 56.173 | 26.7 | 5 | 25.9 | 2 | 171 | 6 | 171.1 | 7 | 0.8 | 111.52 | 90.66 | 137637.96 | 133291.78 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:30:00 | Operating | 1366.2 | 25.7 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 35.168 | 26.7 | 5 | 26 | 2 | 170.7 | 6 | 170.9 | 8 | 0.7 | 112.78 | 91.18 | 137639.22 | 133292.3 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:35:00 | Operating | 1372.3 | 42.4 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 58.111 | 26.7 | 5 | 26.1 | 2 | 171.5 | 5 | 171.6 | 8 | 0.7 | 117.76 | 91.18 | 137644.36 | 133292.3 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:40:00 | Operating | 1377.8 | 52.4 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | 72.235 | 26.8 | 7 | 26 | 2 | 172.1 | 5 | 172.3 | 8 | 0.8 | 126.2 | 91.18 | 137652.86 | 133292.3 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:45:00 | Operating | 1375.6 | 47.1 | 22 | 99 | 20 | 90 | 590.413 | 147.603 | 64.802 | 26.8 | 7 | 26 | 2 | 171.9 | 5 | 172 | 8 | 0.7 | 129.26 | 91.36 | 137655.7 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:50:00 | Operating | 1381.3 | 73.8 | 23 | 99 | 21 | 90 | 583.033 | 154.983 | 101.901 | 26.8 | 5 | 26.1 | 2 | 172.6 | 5 | 172.7 | 8 | 0.7 | 135.02 | 91.36 | 137661.46 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 09:55:00 | Operating | 1384.8 | 75 | 24 | 99 | 23 | 90 | 568.273 | 169.743 | 103.824 | 26.9 | 5 | 26.1 | 2 | 173 | 5 | 173.1 | 8 | 0.8 | 145.1 | 91.36 | 137671.54 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:00:00 | Operating | 1378.5 | 34.2 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | 47.189 | 26.9 | 5 | 26.2 | 2 | 172.3 | 5 | 172.4 | 8 | 0.7 | 150 | 91.36 | 137676.58 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:05:00 | Operating | 1379.1 | 32.2 | 25 | 99 | 24 | 90 | 560.893 | 177.124 | 44.564 | 26.9 | 5 | 26.2 | 2 | 172.3 | 5 | 172.4 | 8 | 0.7 | 154.38 | 91.36 | 137680.82 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:10:00 | Operating | 1375.5 | 7.3 | 26 | 99 | 24 | 90 | 560.893 | 177.124 | 10.046 | 26.9 | 5 | 26.2 | 2 | 171.9 | 5 | 172 | 8 | 0.7 | 156.52 | 91.36 | 137682.96 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:15:00 | Operating | 1379.8 | 40.4 | 26 | 99 | 25 | 90 | 553.512 | 184.504 | 55.72 | 26.9 | 5 | 26.2 | 2 | 172.4 | 5 | 172.5 | 8 | 0.6 | 159.2 | 91.36 | 137685.64 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:20:00 | Operating | 1384 | 45.2 | 27 | 99 | 26 | 90 | 546.132 | 191.884 | 62.495 | 27 | 5 | 26.2 | 2 | 173.1 | 5 | 173.2 | 8 | 0.6 | 165.7 | 91.36 | 137692.4 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:25:00 | Operating | 1382 | 41.5 | 28 | 99 | 26 | 90 | 546.132 | 191.884 | 57.316 | 27 | 5 | 26.3 | 2 | 172.7 | 5 | 172.8 | 8 | 0.7 | 169.3 | 91.36 | 137695.92 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:30:00 | Operating | 1383.9 | 50.1 | 28 | 99 | 27 | 90 | 538.752 | 199.264 | 69.342 | 27 | 5 | 26.3 | 2 | 172.9 | 5 | 173 | 8 | 0.7 | 174.4 | 91.36 | 137701.06 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:35:00 | Operating | 1386.1 | 57.2 | 29 | 99 | 28 | 90 | 531.372 | 206.644 | 79.427 | 27.1 | 5 | 26.4 | 2 | 173.2 | 5 | 173.3 | 8 | 0.7 | 181.1 | 91.36 | 137707.78 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:40:00 | Operating | 1380.9 | 26.2 | 30 | 99 | 29 | 90 | 523.992 | 214.025 | 36.163 | 27.1 | 5 | 26.4 | 2 | 172.6 | 5 | 172.7 | 8 | 0.6 | 185.06 | 91.36 | 137711.62 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:45:00 | Operating | 1386.6 | 62.9 | 30 | 99 | 29 | 90 | 523.992 | 214.025 | 87.224 | 27.1 | 5 | 26.5 | 2 | 173.2 | 5 | 173.3 | 4 | 0.7 | 190.04 | 91.36 | 137716.48 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:50:00 | Operating | 1387.3 | 63.3 | 31 | 99 | 30 | 90 | 516.612 | 221.405 | 87.751 | 27.2 | 5 | 26.5 | 2 | 173.3 | 5 | 173.4 | 4 | 0.7 | 197.2 | 91.36 | 137723.64 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 10:55:00 | Operating | 1385.1 | 46.4 | 32 | 99 | 31 | 90 | 509.231 | 228.785 | 64.221 | 27.3 | 5 | 26.6 | 2 | 173.1 | 5 | 173.1 | 4 | 0.7 | 202.94 | 91.36 | 137729.58 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:00:00 | Operating | 1392.3 | 101.7 | 33 | 99 | 32 | 90 | 501.851 | 236.165 | 141.509 | 27.5 | 8 | 26.7 | 2 | 173.9 | 5 | 174 | 2 | 0.8 | 210.74 | 91.36 | 137737.62 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:05:00 | Operating | 1392.7 | 100.6 | 35 | 99 | 34 | 90 | 487.091 | 250.925 | 140.131 | 27.7 | 5 | 26.9 | 2 | 174 | 5 | 174.1 | 2 | 0.8 | 224.24 | 91.36 | 137751.1 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:10:00 | Operating | 1400.2 | 167.9 | 37 | 99 | 36 | 90 | 472.331 | 265.686 | 235.072 | 28.1 | 7 | 27.2 | 2 | 174.9 | 5 | 174.9 | 2 | 0.9 | 237.58 | 91.36 | 137764.02 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:15:00 | Operating | 1396.4 | 133.3 | 40 | 99 | 39 | 90 | 450.19 | 287.826 | 186.076 | 28.6 | 5 | 27.8 | 2 | 174.5 | 5 | 174.5 | 2 | 0.8 | 257.66 | 91.36 | 137784.1 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:20:00 | Operating | 1391.4 | 96.8 | 42 | 99 | 40 | 90 | 442.81 | 295.206 | 135.117 | 28.8 | 7 | 27.9 | 2 | 173.9 | 5 | 173.9 | 2 | 0.8 | 270.6 | 91.36 | 137797.04 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:25:00 | Operating | 1393.7 | 118.7 | 43 | 99 | 42 | 90 | 428.05 | 309.967 | 165.43 | 28.9 | 8 | 28.1 | 2 | 174.1 | 5 | 174.2 | 2 | 0.8 | 282 | 91.36 | 137808.44 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:30:00 | Operating | 1397.6 | 145.7 | 46 | 99 | 44 | 90 | 413.289 | 324.727 | 203.534 | 29.1 | 7 | 28.3 | 2 | 174.6 | 5 | 174.7 | 2 | 0.8 | 297.84 | 91.36 | 137824.28 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:35:00 | Operating | 1401.2 | 168.5 | 48 | 99 | 47 | 90 | 391.149 | 346.868 | 236.029 | 29.4 | 7 | 28.6 | 2 | 175 | 5 | 175.1 | 7 | 0.8 | 316.76 | 91.36 | 137843.2 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:40:00 | Operating | 1401.6 | 165.9 | 51 | 99 | 49 | 90 | 376.388 | 361.628 | 232.445 | 29.7 | 5 | 28.9 | 2 | 175.1 | 5 | 175.2 | 2 | 0.7 | 337 | 91.36 | 137864.18 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:45:00 | Operating | 1386.4 | 36.2 | 53 | 99 | 51 | 90 | 361.628 | 376.388 | 50.212 | 29.7 | 5 | 28.9 | 6 | 173.3 | 5 | 173.3 | 2 | 0.8 | 349.04 | 91.36 | 137875.48 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:50:00 | Operating | 1390.5 | 86.1 | 53 | 99 | 52 | 90 | 354.248 | 383.768 | 119.737 | 29.5 | 5 | 28.7 | 2 | 173.8 | 5 | 173.8 | 2 | 0.8 | 354.32 | 91.36 | 137880.76 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 11:55:00 | Operating | 1400.2 | 153.2 | 55 | 99 | 54 | 90 | 339.487 | 398.529 | 214.381 | 29.6 | 5 | 28.7 | 6 | 174.9 | 5 | 175 | 7 | 0.9 | 367.5 | 91.36 | 137893.94 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:00:00 | Operating | 1400.2 | 131.9 | 58 | 99 | 56 | 90 | 324.727 | 413.289 | 184.598 | 29.9 | 5 | 29 | 2 | 175 | 5 | 175 | 2 | 0.9 | 385.84 | 91.36 | 137912.86 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:05:00 | Operating | 1398.9 | 117.9 | 60 | 99 | 58 | 90 | 309.967 | 428.05 | 164.818 | 30 | 5 | 29.1 | 2 | 174.8 | 5 | 174.9 | 2 | 0.8 | 399.88 | 91.36 | 137926.32 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:10:00 | Operating | 1400.2 | 118.6 | 62 | 99 | 60 | 90 | 295.206 | 442.81 | 166.055 | 30 | 5 | 29.1 | 6 | 174.9 | 5 | 175 | 2 | 0.9 | 412.92 | 91.36 | 137939.36 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:15:00 | Operating | 1397.6 | 90.9 | 63 | 99 | 62 | 90 | 280.446 | 457.57 | 126.947 | 30.1 | 5 | 29.1 | 6 | 174.6 | 5 | 174.7 | 8 | 0.9 | 424.26 | 91.36 | 137950.7 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:20:00 | Operating | 1407.6 | 158.7 | 65 | 99 | 63 | 90 | 273.066 | 464.95 | 223.385 | 30 | 5 | 29 | 6 | 175.9 | 5 | 176 | 8 | 1 | 435.64 | 91.36 | 137962.74 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:25:00 | Operating | 1405.7 | 117.6 | 67 | 99 | 66 | 90 | 250.925 | 487.091 | 165.28 | 30.3 | 5 | 29.3 | 2 | 175.7 | 5 | 175.7 | 4 | 0.9 | 452.96 | 91.36 | 137979.4 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:30:00 | Operating | 1407.1 | 127.8 | 69 | 99 | 68 | 90 | 236.165 | 501.851 | 179.855 | 30.3 | 5 | 29.3 | 2 | 175.8 | 2 | 175.9 | 7 | 1 | 465.78 | 91.36 | 137992.76 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:35:00 | Operating | 1403.8 | 89.2 | 71 | 99 | 70 | 90 | 221.405 | 516.612 | 125.164 | 30.3 | 5 | 29.3 | 2 | 175.5 | 5 | 175.5 | 4 | 1 | 480.84 | 91.36 | 138007.68 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:40:00 | Operating | 1396.5 | 32.7 | 72 | 99 | 71 | 90 | 214.025 | 523.992 | 45.599 | 30.1 | 5 | 29.1 | 6 | 174.7 | 8 | 174.7 | 3 | 1 | 488.94 | 91.36 | 138015.56 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:45:00 | Operating | 1402 | 77.7 | 73 | 99 | 71 | 90 | 214.025 | 523.992 | 108.855 | 29.9 | 5 | 28.9 | 6 | 175.2 | 8 | 175.3 | 4 | 1 | 492.62 | 91.36 | 138019.42 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:50:00 | Operating | 1400.3 | 52.6 | 74 | 99 | 73 | 90 | 199.264 | 538.752 | 73.687 | 29.8 | 5 | 28.8 | 6 | 175.2 | 8 | 175.1 | 4 | 1 | 502.52 | 91.36 | 138028.96 | 133292.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 12:55:00 | Operating | 1385.3 | -36.5 | 74 | 99 | 73 | 90 | 199.264 | 538.752 | -50.533 | 29.6 | 5 | 28.6 | 6 | 173.3 | 7 | 173.3 | 3 | 1 | 504.86 | 91.8 | 138031.3 | 133293.06 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:00:00 | Operating | 1390.1 | 10.2 | 74 | 99 | 73 | 90 | 199.264 | 538.752 | 14.112 | 29.4 | 5 | 28.5 | 1 | 173.8 | 8 | 173.9 | 3 | 0.9 | 505.34 | 92.68 | 138031.78 | 133293.8 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:05:00 | Operating | 1392 | 21.6 | 74 | 99 | 73 | 90 | 199.264 | 538.752 | 30.085 | 29.2 | 5 | 28.2 | 4 | 174 | 8 | 174.1 | 4 | 1 | 505.94 | 93.04 | 138032.46 | 133294.16 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:10:00 | Operating | 1413.2 | 131.3 | 76 | 99 | 74 | 90 | 191.884 | 546.132 | 185.558 | 29.1 | 8 | 28.1 | 4 | 176.6 | 2 | 176.6 | 7 | 1 | 515 | 93.04 | 138041.44 | 133294.16 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:15:00 | Operating | 1410.1 | 100.8 | 78 | 99 | 76 | 90 | 177.124 | 560.893 | 142.08 | 29 | 5 | 28.1 | 3 | 176.3 | 5 | 176.3 | 4 | 0.9 | 529 | 93.04 | 138055.9 | 133294.16 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:20:00 | Operating | 1404.9 | 70.6 | 79 | 99 | 78 | 90 | 162.363 | 575.653 | 99.099 | 28.9 | 5 | 28 | 3 | 175.6 | 5 | 175.6 | 2 | 0.9 | 539.72 | 93.04 | 138066.46 | 133294.16 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:25:00 | Operating | 1410.1 | 105.8 | 80 | 99 | 79 | 90 | 154.983 | 583.033 | 149.218 | 28.9 | 5 | 27.9 | 2 | 176.2 | 5 | 176.2 | 2 | 1 | 549.76 | 93.04 | 138076.2 | 133294.16 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:30:00 | Operating | 1407.5 | 86.5 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | 121.738 | 28.7 | 5 | 27.7 | 6 | 175.9 | 5 | 175.9 | 2 | 1 | 560.28 | 93.04 | 138087.06 | 133294.16 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:35:00 | Operating | 1401.4 | 41.8 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 58.484 | 28.6 | 5 | 27.6 | 3 | 175.2 | 5 | 175.2 | 2 | 1 | 568.72 | 93.04 | 138095.16 | 133294.16 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:40:00 | Operating | 1390.1 | 6.2 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 8.626 | 28.3 | 5 | 27.4 | 2 | 173.8 | 8 | 173.8 | 4 | 1.1 | 569.66 | 94.94 | 138096.12 | 133296.06 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:45:00 | Operating | 1392.9 | 14.4 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 20.119 | 28.1 | 5 | 27.1 | 3 | 174.2 | 8 | 174.2 | 2 | 1 | 570.86 | 94.94 | 138097.3 | 133296.06 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:50:00 | Operating | 1384.1 | -39.1 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -54.12 | 28 | 8 | 26.8 | 4 | 173.1 | 7 | 173.1 | 4 | 1 | 572.28 | 95.7 | 138098.72 | 133296.82 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 13:55:00 | Operating | 1384.2 | -17 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -23.532 | 27.7 | 8 | 26.6 | 4 | 173.1 | 7 | 173.1 | 4 | 0.9 | 572.28 | 98.56 | 138098.72 | 133299.74 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:00:00 | Operating | 1402.9 | 76.9 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 107.916 | 27.5 | 8 | 26.5 | 2 | 175.3 | 8 | 175.4 | 7 | 1.1 | 573.92 | 99.88 | 138100.98 | 133301 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:05:00 | Operating | 1408.4 | 70.8 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | 99.645 | 27.3 | 5 | 26.3 | 3 | 176 | 1 | 176.1 | 2 | 1 | 582.82 | 99.88 | 138109.56 | 133301 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:10:00 | Operating | 1404.2 | 39.7 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | 55.771 | 27.1 | 8 | 26.1 | 4 | 175.5 | 5 | 175.6 | 2 | 1.1 | 591.36 | 99.88 | 138117.8 | 133301 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:15:00 | Operating | 1402.6 | 32.5 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 45.592 | 26.9 | 5 | 26 | 2 | 175.3 | 5 | 175.4 | 2 | 1 | 595.58 | 99.88 | 138122.02 | 133301 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:20:00 | Operating | 1388.6 | -23.1 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -32.02 | 26.7 | 5 | 25.7 | 3 | 173.7 | 5 | 173.7 | 2 | 1 | 596.94 | 100.24 | 138123.38 | 133301.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:25:00 | Operating | 1391.7 | 15.7 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 21.825 | 26.5 | 8 | 25.5 | 4 | 174 | 8 | 174 | 2 | 1 | 597.1 | 102.08 | 138123.6 | 133303.2 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:30:00 | Operating | 1393.3 | 4.4 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 6.182 | 26.3 | 8 | 25.2 | 3 | 174.2 | 8 | 174.2 | 2 | 1.1 | 599.3 | 102.08 | 138125.76 | 133303.2 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:35:00 | Operating | 1381.9 | -11.8 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | -16.372 | 26.1 | 8 | 25 | 4 | 172.6 | 7 | 172.7 | 4 | 1.1 | 599.4 | 105.78 | 138125.84 | 133306.9 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:40:00 | Operating | 1406.4 | 62.1 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 87.252 | 25.8 | 5 | 24.8 | 4 | 175.7 | 1 | 175.8 | 2 | 1 | 603.26 | 105.94 | 138129.7 | 133307.06 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:45:00 | Operating | 1403.7 | 27.1 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 38.067 | 25.6 | 5 | 24.6 | 3 | 175.5 | 1 | 175.5 | 2 | 1 | 609.1 | 105.94 | 138135.54 | 133307.06 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:50:00 | Operating | 1401.7 | 28 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 39.151 | 25.4 | 5 | 24.4 | 3 | 175.2 | 1 | 175.3 | 2 | 1 | 611.56 | 105.94 | 138138 | 133307.06 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 14:55:00 | Operating | 1389.7 | -12.4 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -17.2 | 25.2 | 5 | 24.2 | 2 | 173.7 | 5 | 173.8 | 2 | 1 | 612.92 | 106.6 | 138139.36 | 133307.78 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:00:00 | Operating | 1385 | -16.4 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -22.736 | 25 | 5 | 24 | 2 | 173.1 | 5 | 173.2 | 4 | 1 | 612.92 | 108.28 | 138139.36 | 133309.4 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:05:00 | Operating | 1394.2 | 23.4 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 32.636 | 24.9 | 8 | 23.8 | 3 | 174.3 | 8 | 174.3 | 2 | 1.1 | 613.54 | 108.6 | 138140.08 | 133309.72 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:10:00 | Operating | 1398.3 | 18.5 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 25.871 | 24.8 | 5 | 23.8 | 2 | 174.8 | 1 | 174.8 | 2 | 1 | 616.24 | 108.6 | 138142.68 | 133309.72 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:15:00 | Operating | 1393.2 | -4.4 | 88 | 99 | 87 | 90 | 95.942 | 642.075 | -6.128 | 24.8 | 8 | 23.8 | 2 | 174.2 | 1 | 174.2 | 2 | 1 | 617.64 | 108.6 | 138144.08 | 133309.72 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:20:00 | Operating | 1382.6 | -30.8 | 87 | 99 | 87 | 90 | 95.942 | 642.075 | -42.58 | 24.8 | 8 | 23.8 | 1 | 172.8 | 5 | 172.9 | 3 | 1 | 617.64 | 110.48 | 138144.08 | 133311.74 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:25:00 | Operating | 1377.7 | -39.2 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -54.01 | 24.7 | 8 | 23.7 | 3 | 172.2 | 7 | 172.3 | 4 | 1 | 617.64 | 114.94 | 138144.08 | 133316.22 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:30:00 | Operating | 1377.6 | -32.4 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -44.689 | 24.7 | 5 | 23.7 | 4 | 172.2 | 7 | 172.2 | 4 | 1 | 617.64 | 119.58 | 138144.08 | 133320.7 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:35:00 | Operating | 1379.3 | -23.1 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -31.915 | 24.8 | 5 | 23.8 | 3 | 172.4 | 7 | 172.5 | 3 | 1 | 617.64 | 122.58 | 138144.08 | 133323.8 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:40:00 | Operating | 1387 | 11.1 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 15.347 | 24.8 | 5 | 23.8 | 2 | 173.4 | 7 | 173.4 | 4 | 0.9 | 618.52 | 122.82 | 138144.96 | 133323.94 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:45:00 | Operating | 1389.7 | 19.7 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 27.432 | 24.7 | 5 | 23.8 | 3 | 173.7 | 8 | 173.7 | 4 | 1 | 619.32 | 122.82 | 138145.84 | 133323.94 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:50:00 | Operating | 1389.9 | 27.6 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 38.328 | 24.7 | 5 | 23.8 | 3 | 173.6 | 5 | 173.7 | 3 | 0.9 | 619.64 | 123.24 | 138146.12 | 133324.36 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 15:55:00 | Operating | 1381.8 | -25.8 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -35.659 | 24.7 | 5 | 23.8 | 3 | 172.7 | 7 | 172.8 | 3 | 0.9 | 620.1 | 124.14 | 138146.54 | 133325.26 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:00:00 | Operating | 1378.4 | -25.5 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | -35.178 | 24.7 | 5 | 23.8 | 4 | 172.3 | 7 | 172.3 | 4 | 0.9 | 620.1 | 128.34 | 138146.54 | 133329.66 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:05:00 | Operating | 1379.6 | -19.2 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | -26.508 | 24.7 | 5 | 23.9 | 1 | 172.5 | 7 | 172.5 | 3 | 1 | 620.1 | 131.14 | 138146.54 | 133332.26 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:10:00 | Operating | 1380.3 | -9.8 | 84 | 99 | 84 | 90 | 118.082 | 619.934 | -13.266 | 24.7 | 5 | 23.8 | 4 | 172.5 | 7 | 172.6 | 4 | 0.9 | 620.1 | 133.08 | 138146.54 | 133334.2 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:15:00 | Operating | 1380.4 | -17.4 | 84 | 99 | 84 | 90 | 118.082 | 619.934 | -24.035 | 24.8 | 8 | 23.9 | 3 | 172.6 | 7 | 172.6 | 4 | 0.9 | 620.1 | 134.7 | 138146.54 | 133335.88 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:20:00 | Operating | 1381.1 | -17.3 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -24.09 | 24.8 | 5 | 23.9 | 3 | 172.6 | 7 | 172.7 | 4 | 1 | 620.1 | 136.02 | 138146.54 | 133337.14 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:25:00 | Operating | 1380.9 | -15.5 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -21.339 | 24.8 | 5 | 23.9 | 4 | 172.6 | 7 | 172.7 | 4 | 0.8 | 620.1 | 137.88 | 138146.54 | 133339.04 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:30:00 | Operating | 1381.6 | -14.1 | 84 | 99 | 82 | 90 | 132.843 | 605.174 | -19.505 | 24.8 | 8 | 23.9 | 4 | 172.7 | 7 | 172.7 | 4 | 0.9 | 620.14 | 139 | 138146.58 | 133340.12 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:35:00 | Operating | 1386.2 | 14 | 84 | 99 | 82 | 90 | 132.843 | 605.174 | 19.342 | 24.8 | 7 | 23.9 | 4 | 173.2 | 8 | 173.3 | 4 | 0.9 | 620.3 | 139.98 | 138146.8 | 133341.1 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:40:00 | Operating | 1390.5 | 14.4 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | 20.067 | 24.8 | 5 | 24 | 4 | 173.8 | 8 | 173.8 | 4 | 0.9 | 622.5 | 139.98 | 138148.94 | 133341.1 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:45:00 | Operating | 1392.2 | 15.5 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | 21.636 | 24.8 | 7 | 24 | 4 | 174 | 8 | 174 | 4 | 0.8 | 624.3 | 139.98 | 138150.8 | 133341.1 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:50:00 | Operating | 1383.4 | -22.5 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -31.176 | 24.8 | 5 | 24 | 4 | 172.9 | 7 | 173 | 3 | 0.9 | 624.92 | 140.68 | 138151.36 | 133341.8 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 16:55:00 | Operating | 1381.5 | -16.8 | 84 | 99 | 82 | 90 | 132.843 | 605.174 | -23.186 | 24.9 | 8 | 24.1 | 4 | 172.7 | 7 | 172.7 | 4 | 0.8 | 624.96 | 143.24 | 138151.4 | 133344.38 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:00:00 | Operating | 1373.1 | -58.4 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -80.188 | 24.8 | 5 | 24.1 | 4 | 171.6 | 7 | 171.7 | 4 | 0.7 | 624.96 | 147.9 | 138151.4 | 133349.28 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:05:00 | Operating | 1383.2 | 11.7 | 83 | 99 | 81 | 90 | 140.223 | 597.793 | 16.226 | 24.9 | 7 | 24.1 | 4 | 172.9 | 7 | 172.9 | 2 | 0.7 | 625.06 | 151.26 | 138151.5 | 133352.38 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:10:00 | Operating | 1384.3 | 7.6 | 83 | 99 | 81 | 90 | 140.223 | 597.793 | 10.535 | 24.9 | 7 | 24.2 | 4 | 173.1 | 7 | 173.1 | 4 | 0.8 | 625.36 | 151.56 | 138151.8 | 133352.68 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:15:00 | Operating | 1378.3 | -30.2 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -41.626 | 24.9 | 5 | 24.2 | 4 | 172.3 | 7 | 172.3 | 4 | 0.7 | 625.54 | 153.56 | 138151.98 | 133354.68 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:20:00 | Operating | 1378.9 | -23.3 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -32.176 | 24.9 | 5 | 24.2 | 4 | 172.4 | 7 | 172.4 | 3 | 0.7 | 625.54 | 156.44 | 138151.98 | 133357.56 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:25:00 | Operating | 1378.7 | -23.4 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -32.315 | 25 | 7 | 24.3 | 4 | 172.4 | 7 | 172.4 | 4 | 0.6 | 625.54 | 159.06 | 138151.98 | 133360.28 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:30:00 | Operating | 1379.7 | -16.5 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -22.795 | 25 | 5 | 24.3 | 2 | 172.5 | 7 | 172.5 | 3 | 0.8 | 625.54 | 161.82 | 138151.98 | 133362.94 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:35:00 | Operating | 1382 | -6.8 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -9.36 | 25 | 7 | 24.3 | 4 | 172.8 | 7 | 172.8 | 4 | 0.7 | 625.54 | 163.16 | 138151.98 | 133364.3 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:40:00 | Operating | 1381 | -26.5 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -36.54 | 25 | 5 | 24.2 | 4 | 172.6 | 7 | 172.7 | 3 | 0.7 | 625.54 | 164.54 | 138151.98 | 133365.66 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:45:00 | Operating | 1375 | -45 | 80 | 99 | 79 | 90 | 154.983 | 583.033 | -61.924 | 25 | 5 | 24.3 | 4 | 171.9 | 7 | 171.9 | 3 | 0.6 | 625.54 | 169.06 | 138151.98 | 133370.4 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:50:00 | Operating | 1375.1 | -45.6 | 79 | 99 | 78 | 90 | 162.363 | 575.653 | -62.697 | 25.1 | 5 | 24.4 | 2 | 171.9 | 1 | 171.9 | 4 | 0.7 | 625.54 | 174.08 | 138151.98 | 133375.2 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 17:55:00 | Operating | 1375.9 | -35.9 | 79 | 99 | 78 | 90 | 162.363 | 575.653 | -49.396 | 25.1 | 5 | 24.4 | 4 | 172 | 1 | 172 | 5 | 0.7 | 625.54 | 179.56 | 138151.98 | 133380.84 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:00:00 | Operating | 1374.4 | -45.6 | 78 | 99 | 77 | 90 | 169.743 | 568.273 | -62.631 | 25.2 | 5 | 24.5 | 4 | 171.8 | 1 | 171.8 | 4 | 0.6 | 625.54 | 186.1 | 138151.98 | 133387.22 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:05:00 | Operating | 1375.7 | -40.2 | 77 | 99 | 76 | 90 | 177.124 | 560.893 | -55.218 | 25.2 | 5 | 24.5 | 4 | 172 | 1 | 172 | 4 | 0.6 | 625.54 | 190.2 | 138151.98 | 133391.48 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:10:00 | Operating | 1375.6 | -41.3 | 77 | 99 | 76 | 90 | 177.124 | 560.893 | -56.773 | 25.2 | 5 | 24.6 | 2 | 171.9 | 1 | 172 | 5 | 0.7 | 625.54 | 194.6 | 138151.98 | 133395.72 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:15:00 | Operating | 1373.2 | -55.4 | 76 | 99 | 75 | 90 | 184.504 | 553.512 | -76.049 | 25.3 | 5 | 24.6 | 4 | 171.7 | 1 | 171.7 | 5 | 0.7 | 625.54 | 200.06 | 138151.98 | 133401.4 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:20:00 | Operating | 1369.9 | -79.5 | 75 | 99 | 74 | 90 | 191.884 | 546.132 | -108.881 | 25.3 | 5 | 24.7 | 2 | 171.3 | 6 | 171.3 | 5 | 0.6 | 625.54 | 206.7 | 138151.98 | 133407.82 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:25:00 | Operating | 1365.3 | -101 | 73 | 99 | 72 | 90 | 206.644 | 531.372 | -137.812 | 25.4 | 5 | 24.8 | 2 | 170.7 | 6 | 170.8 | 8 | 0.6 | 625.54 | 216.62 | 138151.98 | 133418.12 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:30:00 | Operating | 1363.7 | -92.7 | 72 | 99 | 70 | 90 | 221.405 | 516.612 | -126.368 | 25.6 | 5 | 24.9 | 2 | 170.5 | 6 | 170.6 | 8 | 0.8 | 625.54 | 228.16 | 138151.98 | 133429.68 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:35:00 | Operating | 1361.7 | -96.2 | 70 | 99 | 69 | 90 | 228.785 | 509.231 | -130.921 | 25.8 | 5 | 24.9 | 2 | 170.1 | 6 | 170.3 | 8 | 0.7 | 625.54 | 238.58 | 138151.98 | 133439.7 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:40:00 | Operating | 1356.1 | -111.8 | 69 | 99 | 67 | 90 | 243.545 | 494.471 | -151.594 | 25.8 | 5 | 25.1 | 2 | 169.5 | 6 | 169.7 | 8 | 0.7 | 625.54 | 250.12 | 138151.98 | 133451.24 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:45:00 | Operating | 1355 | -105.1 | 67 | 99 | 65 | 90 | 258.306 | 479.711 | -142.32 | 25.8 | 5 | 25.2 | 2 | 169.4 | 6 | 169.5 | 8 | 0.7 | 625.54 | 261.66 | 138151.98 | 133463.22 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:50:00 | Operating | 1353.9 | -104.2 | 65 | 99 | 64 | 90 | 265.686 | 472.331 | -141.12 | 26 | 5 | 25.2 | 2 | 169.3 | 6 | 169.4 | 8 | 0.7 | 625.54 | 273.76 | 138151.98 | 133474.88 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 18:55:00 | Operating | 1351.2 | -127.5 | 63 | 99 | 62 | 90 | 280.446 | 457.57 | -172.188 | 25.9 | 5 | 25.1 | 2 | 169 | 6 | 169 | 3 | 0.9 | 625.54 | 285.12 | 138151.98 | 133486.76 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:00:00 | Operating | 1348.6 | -141.5 | 61 | 99 | 59 | 90 | 302.587 | 435.43 | -190.855 | 26.1 | 5 | 25.3 | 2 | 168.7 | 6 | 168.7 | 5 | 0.8 | 625.54 | 299.6 | 138151.98 | 133501.88 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:05:00 | Operating | 1347.4 | -148.5 | 59 | 99 | 57 | 90 | 317.347 | 420.669 | -200.053 | 26.2 | 5 | 25.3 | 2 | 168.5 | 7 | 168.6 | 3 | 0.7 | 625.54 | 316.22 | 138151.98 | 133517.34 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:10:00 | Operating | 1347.4 | -145.9 | 56 | 99 | 54 | 90 | 339.487 | 398.529 | -196.461 | 26.3 | 5 | 25.5 | 2 | 168.5 | 6 | 168.6 | 5 | 0.7 | 625.54 | 334.26 | 138151.98 | 133535.38 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:15:00 | Operating | 1345.3 | -160.9 | 54 | 99 | 52 | 90 | 354.248 | 383.768 | -216.49 | 26.4 | 5 | 25.5 | 2 | 168.3 | 6 | 168.3 | 5 | 0.7 | 625.54 | 351.1 | 138151.98 | 133552.82 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:20:00 | Operating | 1344.2 | -167.6 | 51 | 99 | 49 | 90 | 376.388 | 361.628 | -225.145 | 26.5 | 5 | 25.6 | 2 | 168.1 | 6 | 168.2 | 3 | 0.8 | 625.54 | 369.64 | 138151.98 | 133570.76 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:25:00 | Operating | 1341.4 | -185.1 | 48 | 99 | 46 | 90 | 398.529 | 339.487 | -248.189 | 26.5 | 5 | 25.8 | 2 | 167.8 | 6 | 167.9 | 5 | 0.8 | 625.54 | 389 | 138151.98 | 133590.88 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:30:00 | Operating | 1337.3 | -208.1 | 45 | 99 | 42 | 90 | 428.05 | 309.967 | -278.144 | 26.7 | 5 | 26 | 2 | 167.3 | 6 | 167.4 | 5 | 0.7 | 625.54 | 411.92 | 138151.98 | 133613.04 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:35:00 | Operating | 1335.4 | -212.1 | 42 | 99 | 39 | 90 | 450.19 | 287.826 | -283.18 | 27.1 | 5 | 26.4 | 2 | 167.1 | 2 | 167.2 | 3 | 0.7 | 625.54 | 435.46 | 138151.98 | 133637.44 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:40:00 | Operating | 1333.9 | -207.5 | 38 | 99 | 36 | 90 | 472.331 | 265.686 | -276.723 | 27.3 | 5 | 26.6 | 2 | 166.9 | 6 | 167 | 5 | 0.7 | 625.54 | 458.16 | 138151.98 | 133659.28 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:45:00 | Operating | 1332.2 | -200.9 | 35 | 99 | 33 | 90 | 494.471 | 243.545 | -267.625 | 27.7 | 5 | 27 | 2 | 166.7 | 6 | 166.8 | 3 | 0.7 | 625.54 | 481.38 | 138151.98 | 133682.5 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:50:00 | Operating | 1325.1 | -235.2 | 31 | 99 | 29 | 90 | 523.992 | 214.025 | -311.657 | 28.1 | 5 | 27.6 | 2 | 165.9 | 6 | 166 | 3 | 0.5 | 625.54 | 506.92 | 138151.98 | 133708.04 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 19:55:00 | Operating | 1332.2 | -150.8 | 28 | 99 | 26 | 90 | 546.132 | 191.884 | -200.904 | 28.7 | 5 | 28.1 | 2 | 166.7 | 6 | 166.8 | 3 | 0.6 | 625.54 | 530.02 | 138151.98 | 133731.14 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:00:00 | Operating | 1339.6 | -88.3 | 26 | 99 | 24 | 90 | 560.893 | 177.124 | -118.246 | 28.7 | 5 | 28 | 4 | 167.6 | 6 | 167.6 | 3 | 0.7 | 625.54 | 542.92 | 138151.98 | 133744.04 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:05:00 | Operating | 1344.5 | -45.9 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | -61.7 | 28.6 | 5 | 28 | 2 | 168.1 | 6 | 168.2 | 8 | 0.6 | 625.54 | 551.94 | 138151.98 | 133753.28 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:10:00 | Operating | 1353.9 | 2.4 | 24 | 99 | 23 | 90 | 568.273 | 169.743 | 3.188 | 28.5 | 5 | 27.7 | 2 | 169.3 | 6 | 169.4 | 8 | 0.8 | 625.78 | 553.54 | 138152.22 | 133754.66 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:15:00 | Operating | 1350 | -32.7 | 24 | 99 | 23 | 90 | 568.273 | 169.743 | -44.083 | 28.3 | 5 | 27.6 | 2 | 168.8 | 1 | 168.9 | 8 | 0.7 | 625.84 | 555.08 | 138152.28 | 133756.34 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:20:00 | Operating | 1345.3 | -49.3 | 23 | 99 | 22 | 90 | 575.653 | 162.363 | -66.279 | 28.2 | 5 | 27.6 | 2 | 168.2 | 1 | 168.3 | 8 | 0.6 | 625.84 | 560.18 | 138152.28 | 133761.5 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:25:00 | Operating | 1344 | -46 | 23 | 99 | 21 | 90 | 583.033 | 154.983 | -61.757 | 28.2 | 5 | 27.3 | 4 | 168 | 6 | 168.1 | 8 | 0.9 | 625.84 | 565.56 | 138152.28 | 133766.68 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:30:00 | Operating | 1344 | -37.9 | 22 | 99 | 21 | 90 | 583.033 | 154.983 | -50.924 | 27.9 | 5 | 27.2 | 4 | 168 | 6 | 168.1 | 8 | 0.7 | 625.84 | 570.8 | 138152.28 | 133772.06 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:35:00 | Operating | 1343.9 | -36.5 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | -48.927 | 27.9 | 5 | 27 | 6 | 168 | 6 | 168.1 | 8 | 0.9 | 625.84 | 574.74 | 138152.28 | 133776 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:40:00 | Operating | 1342.9 | -34.7 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | -46.63 | 27.7 | 5 | 26.8 | 6 | 167.9 | 6 | 168 | 8 | 0.8 | 625.84 | 579.16 | 138152.28 | 133780.28 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:45:00 | Operating | 1342.5 | -32.8 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -43.969 | 27.5 | 5 | 26.6 | 6 | 167.9 | 6 | 168 | 8 | 1 | 625.84 | 582.92 | 138152.28 | 133784.04 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:50:00 | Operating | 1343.2 | -22.4 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -30.039 | 27.4 | 5 | 26.5 | 3 | 167.9 | 6 | 168 | 8 | 0.9 | 625.84 | 586.22 | 138152.28 | 133787.44 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 20:55:00 | Operating | 1340.5 | -32.2 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -43.214 | 27.1 | 5 | 26.3 | 6 | 167.6 | 6 | 167.7 | 8 | 0.8 | 625.84 | 590.42 | 138152.28 | 133791.68 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:00:00 | Operating | 1340.8 | -28 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | -37.533 | 27 | 5 | 26.1 | 6 | 167.6 | 6 | 167.7 | 8 | 0.8 | 625.84 | 593.04 | 138152.28 | 133794.38 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:05:00 | Operating | 1344.1 | -11.3 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -15.202 | 26.8 | 5 | 25.9 | 6 | 168 | 6 | 168.1 | 8 | 0.9 | 625.84 | 594.84 | 138152.28 | 133796.02 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:10:00 | Operating | 1347.5 | 7.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 10.048 | 26.5 | 5 | 25.7 | 4 | 168.4 | 6 | 168.5 | 8 | 0.8 | 625.88 | 595.54 | 138152.32 | 133796.66 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:15:00 | Operating | 1346 | -4.2 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -5.704 | 26.3 | 5 | 25.4 | 6 | 168.2 | 6 | 168.4 | 8 | 0.9 | 626 | 596.02 | 138152.44 | 133797.16 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:20:00 | Operating | 1344.2 | -14.1 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -18.96 | 26.1 | 5 | 25.2 | 6 | 168 | 6 | 168.2 | 8 | 0.8 | 626.16 | 596.66 | 138152.6 | 133797.78 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:25:00 | Operating | 1347.2 | 3.7 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 4.956 | 25.9 | 5 | 25 | 6 | 168.4 | 6 | 168.5 | 8 | 0.9 | 626.22 | 597.54 | 138152.66 | 133798.66 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:30:00 | Operating | 1347 | -8.3 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -11.218 | 25.7 | 5 | 24.8 | 6 | 168.4 | 6 | 168.5 | 8 | 0.9 | 626.72 | 597.58 | 138153.16 | 133798.7 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:35:00 | Operating | 1345.7 | -5.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -7.275 | 25.6 | 5 | 24.6 | 6 | 168.2 | 6 | 168.3 | 8 | 1 | 626.72 | 598.44 | 138153.16 | 133799.58 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:40:00 | Operating | 1344.9 | -8.3 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -11.126 | 25.5 | 5 | 24.5 | 6 | 168.1 | 6 | 168.2 | 8 | 1 | 626.74 | 599.32 | 138153.18 | 133800.44 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:45:00 | Operating | 1345.5 | -3.7 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -5.098 | 25.2 | 5 | 24.4 | 4 | 168.2 | 1 | 168.3 | 8 | 0.8 | 626.76 | 599.84 | 138153.2 | 133800.96 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:50:00 | Operating | 1348.1 | 10.1 | 18 | 99 | 16 | 90 | 612.554 | 125.462 | 13.631 | 25.1 | 5 | 24.3 | 4 | 168.4 | 1 | 168.6 | 8 | 0.8 | 626.8 | 600.12 | 138153.24 | 133801.24 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 21:55:00 | Operating | 1345.1 | -1.7 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -2.252 | 25.1 | 5 | 24.2 | 3 | 168.1 | 6 | 168.2 | 8 | 0.9 | 627.06 | 600.98 | 138153.5 | 133802.12 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:00:00 | Operating | 1342.9 | -13.2 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -17.813 | 24.9 | 5 | 24 | 6 | 167.8 | 6 | 168 | 8 | 0.9 | 627.18 | 601.82 | 138153.62 | 133802.94 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:05:00 | Operating | 1344.3 | -5.8 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | -7.813 | 24.8 | 5 | 24 | 2 | 168 | 1 | 168.2 | 8 | 0.8 | 627.2 | 602.64 | 138153.64 | 133803.78 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:10:00 | Operating | 1346.8 | 3.2 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 4.299 | 24.8 | 5 | 23.9 | 2 | 168.3 | 6 | 168.4 | 8 | 0.9 | 627.32 | 602.9 | 138153.76 | 133804.02 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:15:00 | Operating | 1346.9 | 0.6 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 0.777 | 24.7 | 5 | 23.8 | 6 | 168.3 | 1 | 168.5 | 8 | 0.9 | 627.64 | 602.92 | 138154.08 | 133804.04 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:20:00 | Operating | 1349.3 | 8.6 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | 11.546 | 24.6 | 5 | 23.8 | 2 | 168.6 | 6 | 168.8 | 8 | 0.8 | 628.24 | 602.96 | 138154.68 | 133804.08 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:25:00 | Operating | 1354.4 | 23.6 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 31.976 | 24.6 | 5 | 23.8 | 2 | 169.2 | 1 | 169.4 | 8 | 0.8 | 629.96 | 602.96 | 138156.4 | 133804.08 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:30:00 | Operating | 1361.8 | 43.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 59.235 | 24.6 | 5 | 23.8 | 4 | 170.1 | 1 | 170.2 | 7 | 0.8 | 633.18 | 602.96 | 138159.84 | 133804.08 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:35:00 | Operating | 1356 | 11 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 14.904 | 24.5 | 5 | 23.8 | 4 | 169.5 | 1 | 169.6 | 8 | 0.8 | 634.98 | 602.96 | 138161.42 | 133804.08 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:40:00 | Operating | 1355.5 | 10.3 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 13.9 | 24.6 | 5 | 23.8 | 2 | 169.4 | 1 | 169.5 | 8 | 0.8 | 635.32 | 603.34 | 138161.82 | 133804.46 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:45:00 | Operating | 1361.1 | 27.7 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 37.649 | 24.6 | 5 | 23.8 | 3 | 169.9 | 1 | 170 | 8 | 0.8 | 637.36 | 603.34 | 138163.8 | 133804.46 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:50:00 | Operating | 1362.2 | 19 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 25.905 | 24.6 | 5 | 23.8 | 3 | 170.2 | 1 | 170.3 | 7 | 0.9 | 640.88 | 603.34 | 138167.32 | 133804.46 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 22:55:00 | Operating | 1356.3 | -4.1 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -5.524 | 24.6 | 5 | 23.8 | 4 | 169.5 | 1 | 169.6 | 8 | 0.8 | 641.52 | 603.4 | 138167.96 | 133804.52 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:00:00 | Operating | 1352.4 | -7.7 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -10.413 | 24.6 | 5 | 23.8 | 6 | 169 | 5 | 169.1 | 8 | 0.8 | 641.52 | 604.48 | 138167.96 | 133805.7 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:05:00 | Operating | 1356.5 | 6.4 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 8.699 | 24.7 | 5 | 23.9 | 2 | 169.5 | 6 | 169.7 | 8 | 0.9 | 642.08 | 604.7 | 138168.52 | 133805.82 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:10:00 | Operating | 1356 | 0.5 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 0.73 | 24.6 | 5 | 23.9 | 2 | 169.5 | 6 | 169.6 | 8 | 0.8 | 642.92 | 604.8 | 138169.36 | 133805.92 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:15:00 | Operating | 1356.1 | 0.8 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 1.065 | 24.7 | 5 | 23.9 | 4 | 169.5 | 1 | 169.6 | 8 | 0.7 | 643.52 | 604.88 | 138169.96 | 133806.02 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:20:00 | Operating | 1358.7 | 10.4 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 14.114 | 24.6 | 5 | 23.9 | 2 | 169.8 | 1 | 169.9 | 8 | 0.7 | 644.28 | 604.9 | 138170.72 | 133806.02 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:25:00 | Operating | 1362.2 | 21.6 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 29.423 | 24.7 | 5 | 23.9 | 4 | 170.2 | 1 | 170.3 | 8 | 0.7 | 645.88 | 604.9 | 138172.4 | 133806.02 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:30:00 | Operating | 1363.9 | 22.9 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 31.163 | 24.7 | 5 | 23.9 | 2 | 170.4 | 1 | 170.5 | 8 | 0.8 | 648.06 | 604.9 | 138174.5 | 133806.02 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:35:00 | Operating | 1360.6 | -1.2 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -1.584 | 24.7 | 5 | 23.9 | 4 | 169.9 | 1 | 170 | 8 | 0.8 | 649.34 | 604.98 | 138175.78 | 133806.1 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:40:00 | Operating | 1361 | 2.4 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 3.249 | 24.7 | 5 | 24 | 2 | 169.9 | 1 | 170 | 8 | 0.7 | 649.7 | 605.26 | 138176.14 | 133806.38 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:45:00 | Operating | 1357.7 | -2.9 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -3.997 | 24.7 | 5 | 24 | 2 | 169.7 | 5 | 169.8 | 8 | 0.8 | 650.06 | 605.48 | 138176.5 | 133806.64 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:50:00 | Operating | 1361.9 | 11.7 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 15.867 | 24.8 | 7 | 24 | 2 | 170.2 | 1 | 170.3 | 8 | 0.7 | 650.76 | 605.8 | 138177.2 | 133806.92 | 1.06
Amleang 136MW-01 | / | SACU-04/B04-ESS04/ESR-HV2510089507 | 2026-06-03 23:55:00 | Operating | 1364.4 | 15.6 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | 21.244 | 24.8 | 5 | 24 | 2 | 170.5 | 1 | 170.6 | 7 | 0.8 | 653.1 | 605.8 | 138179.54 | 133806.92 | 1.06