## 5 minutes
Time range: | 2026-06-03 00:00:00 - 2026-06-03 23:59:59
Export time: | 2026-06-04 00:34:28
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Device status | Voltage(V) | Current(A) | SOC(%) | SOH(%) | SOE(%) | DOD(%) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge Power(kW) | Module with the highest temperature(°C) | Position of the module with the highest temperature | Module with the lowest temperature(°C) | Position of the module with the lowest temperature | Lowest battery pack voltage(V) | Position where the lowest battery pack voltage was detected | Highest battery pack voltage(V) | Position where the highest battery pack voltage was detected | Average Temperature(°C) | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge(kWh) | Total discharge(kWh) | ISO insulation resistance(MΩ)
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:00:00 | Operating | 1337.9 | -15.1 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -20.195 | 24.2 | 6 | 23.9 | 1 | 167.1 | 2 | 167.3 | 8 | 0.3 | 0 | 0.32 | 138821.46 | 134689.98 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:05:00 | Operating | 1342.3 | 9.1 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 12.282 | 24.2 | 4 | 23.9 | 1 | 167.6 | 2 | 167.8 | 8 | 0.3 | 0 | 1.46 | 138821.46 | 134691.12 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:10:00 | Operating | 1338.2 | -25.5 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -34.189 | 24.2 | 5 | 23.9 | 1 | 167.2 | 2 | 167.4 | 8 | 0.3 | 0.58 | 2.16 | 138822.04 | 134691.9 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:15:00 | Operating | 1335.6 | -18.3 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -24.497 | 24.2 | 4 | 23.9 | 1 | 166.8 | 2 | 167 | 7 | 0.3 | 0.58 | 4.6 | 138822.04 | 134694.26 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:20:00 | Operating | 1334 | -25.9 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -34.628 | 24.2 | 3 | 24 | 1 | 166.7 | 2 | 166.9 | 8 | 0.2 | 0.58 | 6.22 | 138822.04 | 134696 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:25:00 | Operating | 1335.3 | -10.6 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -14.192 | 24.3 | 4 | 24 | 1 | 166.8 | 2 | 167 | 7 | 0.3 | 0.58 | 8.72 | 138822.04 | 134698.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:30:00 | Operating | 1336.7 | -15.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -20.149 | 24.3 | 6 | 24 | 1 | 167 | 2 | 167.2 | 8 | 0.3 | 0.66 | 9.42 | 138822.12 | 134699.14 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:35:00 | Operating | 1335.3 | -12.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -17.067 | 24.3 | 4 | 24 | 1 | 166.8 | 2 | 167 | 7 | 0.3 | 0.66 | 11.1 | 138822.12 | 134700.76 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:40:00 | Operating | 1336.1 | -2.7 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | -3.638 | 24.4 | 8 | 24.1 | 1 | 166.9 | 2 | 167.1 | 8 | 0.3 | 0.66 | 12.88 | 138822.12 | 134702.54 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:45:00 | Operating | 1336.3 | -6.8 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | -9.073 | 24.4 | 6 | 24.1 | 1 | 166.9 | 2 | 167.2 | 7 | 0.3 | 0.78 | 14.04 | 138822.24 | 134703.72 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:50:00 | Operating | 1336.2 | -8.1 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -10.773 | 24.4 | 6 | 24.1 | 1 | 166.9 | 2 | 167.1 | 7 | 0.3 | 0.78 | 14.68 | 138822.24 | 134704.34 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 00:55:00 | Operating | 1333 | -20.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -27.764 | 24.4 | 4 | 24.1 | 1 | 166.4 | 2 | 166.7 | 7 | 0.3 | 0.78 | 16.32 | 138822.24 | 134705.98 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:00:00 | Operating | 1333 | -16.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -22.488 | 24.4 | 4 | 24.1 | 1 | 166.5 | 2 | 166.7 | 8 | 0.3 | 0.8 | 17.44 | 138822.26 | 134707.16 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:05:00 | Operating | 1331.6 | -19.1 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -25.419 | 24.5 | 8 | 24.2 | 1 | 166.3 | 2 | 166.5 | 8 | 0.3 | 0.8 | 19.58 | 138822.26 | 134709.3 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:10:00 | Operating | 1333.3 | -6.9 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -9.155 | 24.5 | 6 | 24.2 | 1 | 166.5 | 2 | 166.8 | 8 | 0.3 | 0.82 | 20.84 | 138822.28 | 134710.54 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:15:00 | Operating | 1329.9 | -21.6 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -28.769 | 24.5 | 4 | 24.2 | 1 | 166.1 | 2 | 166.4 | 7 | 0.3 | 0.82 | 22.36 | 138822.28 | 134712.02 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:20:00 | Operating | 1330.1 | -14.5 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -19.279 | 24.5 | 5 | 24.2 | 1 | 166.1 | 2 | 166.4 | 7 | 0.3 | 0.82 | 24.2 | 138822.28 | 134713.92 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:25:00 | Operating | 1334.5 | -2.9 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -3.852 | 24.5 | 4 | 24.3 | 1 | 166.7 | 2 | 166.9 | 8 | 0.2 | 0.96 | 24.78 | 138822.42 | 134714.44 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:30:00 | Operating | 1341.3 | 14.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 19.833 | 24.6 | 6 | 24.3 | 1 | 167.5 | 2 | 167.8 | 8 | 0.3 | 1.88 | 24.92 | 138823.34 | 134714.58 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:35:00 | Operating | 1341.6 | 5.5 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 7.406 | 24.5 | 4 | 24.3 | 1 | 167.5 | 2 | 167.8 | 8 | 0.2 | 2.98 | 24.92 | 138824.48 | 134714.58 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:40:00 | Operating | 1344 | 11.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 15.888 | 24.5 | 5 | 24.3 | 1 | 167.8 | 2 | 168.1 | 8 | 0.2 | 4.02 | 24.94 | 138825.52 | 134714.6 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:45:00 | Operating | 1349.2 | 17.1 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | 23.096 | 24.5 | 3 | 24.3 | 1 | 168.5 | 2 | 168.7 | 8 | 0.3 | 6.28 | 24.94 | 138827.82 | 134714.6 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:50:00 | Operating | 1352.1 | 18.2 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 24.579 | 24.6 | 4 | 24.3 | 1 | 168.8 | 2 | 169 | 8 | 0.2 | 8.48 | 24.94 | 138829.94 | 134714.6 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 01:55:00 | Operating | 1346.9 | -3.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -4.404 | 24.6 | 5 | 24.3 | 1 | 168.2 | 2 | 168.5 | 8 | 0.3 | 9.22 | 24.96 | 138830.68 | 134714.62 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:00:00 | Operating | 1341.3 | -16.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -22.451 | 24.6 | 6 | 24.3 | 1 | 167.6 | 2 | 167.8 | 8 | 0.3 | 9.36 | 25.52 | 138830.82 | 134715.24 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:05:00 | Operating | 1342.3 | 4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.275 | 24.6 | 5 | 24.4 | 1 | 167.6 | 2 | 167.8 | 8 | 0.3 | 9.38 | 26.64 | 138830.84 | 134716.3 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:10:00 | Operating | 1344 | 3.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.002 | 24.6 | 5 | 24.4 | 1 | 167.9 | 2 | 168.1 | 8 | 0.2 | 10.16 | 26.88 | 138831.62 | 134716.54 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:15:00 | Operating | 1340.1 | -13.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -18.321 | 24.6 | 3 | 24.4 | 1 | 167.4 | 2 | 167.6 | 8 | 0.2 | 10.22 | 27.4 | 138831.68 | 134717.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:20:00 | Operating | 1341.4 | 5.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 7.737 | 24.7 | 5 | 24.4 | 1 | 167.5 | 2 | 167.8 | 8 | 0.2 | 10.24 | 28.28 | 138831.72 | 134717.94 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:25:00 | Operating | 1342.8 | -4.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -6.408 | 24.6 | 4 | 24.4 | 1 | 167.7 | 2 | 168 | 8 | 0.2 | 10.88 | 28.28 | 138832.34 | 134717.94 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:30:00 | Operating | 1341 | -2.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -3.922 | 24.6 | 5 | 24.4 | 1 | 167.5 | 2 | 167.7 | 8 | 0.3 | 10.92 | 28.76 | 138832.38 | 134718.42 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:35:00 | Operating | 1342.1 | 11 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 14.779 | 24.7 | 6 | 24.4 | 1 | 167.6 | 2 | 167.9 | 8 | 0.2 | 11.02 | 29.12 | 138832.48 | 134718.78 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:40:00 | Operating | 1344.5 | 4.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 6.535 | 24.6 | 4 | 24.4 | 1 | 167.9 | 2 | 168.2 | 8 | 0.2 | 11.72 | 29.16 | 138833.2 | 134718.82 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:45:00 | Operating | 1343.4 | 2.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 3.548 | 24.7 | 6 | 24.4 | 1 | 167.8 | 2 | 168 | 8 | 0.2 | 11.92 | 29.4 | 138833.38 | 134719.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:50:00 | Operating | 1341.3 | -8.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -11.27 | 24.6 | 3 | 24.4 | 1 | 167.7 | 2 | 167.8 | 8 | 0.3 | 12.26 | 29.68 | 138833.72 | 134719.34 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 02:55:00 | Operating | 1342.7 | 6.1 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 8.261 | 24.7 | 5 | 24.4 | 1 | 167.7 | 2 | 167.9 | 8 | 0.3 | 12.42 | 30.26 | 138833.88 | 134719.92 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:00:00 | Operating | 1344.2 | 8.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 11.373 | 24.7 | 6 | 24.4 | 1 | 167.9 | 2 | 168.1 | 8 | 0.3 | 12.8 | 30.52 | 138834.26 | 134720.18 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:05:00 | Operating | 1342 | -1.1 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -1.461 | 24.7 | 3 | 24.4 | 1 | 167.6 | 2 | 167.8 | 8 | 0.3 | 13.1 | 31.08 | 138834.56 | 134720.74 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:10:00 | Operating | 1340.4 | -4.4 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -5.898 | 24.7 | 4 | 24.4 | 1 | 167.5 | 2 | 167.7 | 8 | 0.3 | 13.2 | 31.48 | 138834.66 | 134721.14 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:15:00 | Operating | 1339.6 | -3.5 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -4.672 | 24.7 | 5 | 24.5 | 1 | 167.3 | 2 | 167.6 | 8 | 0.3 | 13.22 | 32.12 | 138834.68 | 134721.78 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:20:00 | Operating | 1340.4 | 4.2 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | 5.634 | 24.7 | 4 | 24.5 | 1 | 167.4 | 2 | 167.7 | 8 | 0.2 | 13.38 | 32.7 | 138834.84 | 134722.36 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:25:00 | Operating | 1352 | 22.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 30.941 | 24.7 | 4 | 24.5 | 1 | 168.7 | 2 | 169 | 8 | 0.2 | 15.8 | 32.7 | 138837.34 | 134722.36 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:30:00 | Operating | 1346.8 | 2.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 3.769 | 24.7 | 4 | 24.5 | 1 | 168.2 | 2 | 168.5 | 8 | 0.2 | 16.56 | 32.84 | 138838.04 | 134722.5 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:35:00 | Operating | 1346 | 1.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 1.849 | 24.7 | 4 | 24.5 | 1 | 168.2 | 2 | 168.4 | 8 | 0.2 | 16.96 | 32.96 | 138838.42 | 134722.62 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:40:00 | Operating | 1355.1 | 28.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 38.666 | 24.7 | 4 | 24.5 | 1 | 169.2 | 2 | 169.4 | 8 | 0.3 | 19.08 | 32.96 | 138840.66 | 134722.62 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:45:00 | Operating | 1364 | 57.4 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 78.194 | 24.8 | 6 | 24.5 | 1 | 170.3 | 2 | 170.5 | 4 | 0.3 | 24.16 | 32.96 | 138845.86 | 134722.62 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:50:00 | Operating | 1368.1 | 58.7 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 80.324 | 24.8 | 5 | 24.5 | 1 | 170.8 | 2 | 171.1 | 4 | 0.3 | 31.6 | 32.96 | 138853.06 | 134722.62 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 03:55:00 | Operating | 1366.4 | 44.7 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 61.169 | 24.8 | 5 | 24.6 | 1 | 170.6 | 2 | 170.9 | 8 | 0.2 | 36.72 | 32.96 | 138858.34 | 134722.62 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:00:00 | Operating | 1372.8 | 61.9 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | 85.069 | 24.9 | 5 | 24.6 | 1 | 171.4 | 2 | 171.6 | 5 | 0.3 | 43.38 | 32.96 | 138865.14 | 134722.62 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:05:00 | Operating | 1361.2 | -2.1 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -2.885 | 24.9 | 6 | 24.6 | 1 | 170.1 | 2 | 170.2 | 8 | 0.3 | 45.94 | 33.18 | 138867.4 | 134722.84 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:10:00 | Operating | 1352.4 | -35.6 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -48.223 | 24.9 | 6 | 24.6 | 1 | 168.9 | 2 | 169.1 | 4 | 0.3 | 45.94 | 35.56 | 138867.4 | 134725.22 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:15:00 | Operating | 1352.1 | -19.8 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -26.826 | 24.9 | 6 | 24.7 | 1 | 168.8 | 2 | 169 | 4 | 0.3 | 45.94 | 38.02 | 138867.4 | 134727.78 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:20:00 | Operating | 1348.8 | -18.3 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | -24.732 | 24.9 | 3 | 24.7 | 1 | 168.5 | 2 | 168.7 | 4 | 0.3 | 45.94 | 40.56 | 138867.4 | 134730.3 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:25:00 | Operating | 1341.5 | -42.4 | 17 | 99 | 15 | 90 | 627.314 | 110.702 | -56.925 | 25 | 3 | 24.7 | 1 | 167.6 | 2 | 167.9 | 4 | 0.3 | 45.94 | 43.88 | 138867.4 | 134733.54 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:30:00 | Operating | 1333.8 | -51.2 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -68.281 | 25 | 4 | 24.8 | 1 | 166.7 | 2 | 166.9 | 4 | 0.2 | 45.94 | 49.3 | 138867.4 | 134739.16 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:35:00 | Operating | 1329.8 | -61.4 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -81.697 | 25.1 | 6 | 24.8 | 1 | 166.3 | 2 | 166.5 | 4 | 0.2 | 45.94 | 54.28 | 138867.4 | 134743.94 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:40:00 | Operating | 1330.9 | -34.5 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | -45.888 | 25.1 | 3 | 24.9 | 1 | 166.3 | 2 | 166.5 | 8 | 0.2 | 45.94 | 58.86 | 138867.4 | 134748.52 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:45:00 | Operating | 1330.7 | -25.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -33.738 | 25.2 | 5 | 25 | 1 | 166.2 | 2 | 166.4 | 8 | 0.2 | 45.94 | 62.28 | 138867.4 | 134751.94 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:50:00 | Operating | 1331.9 | -13.2 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -17.617 | 25.2 | 3 | 25 | 1 | 166.3 | 2 | 166.5 | 8 | 0.2 | 45.94 | 65.32 | 138867.4 | 134754.98 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 04:55:00 | Operating | 1334.1 | -5.8 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -7.684 | 25.2 | 3 | 25 | 1 | 166.6 | 2 | 166.9 | 8 | 0.2 | 45.94 | 66.04 | 138867.4 | 134755.72 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:00:00 | Operating | 1336.4 | -0.8 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -1.106 | 25.2 | 3 | 25 | 1 | 166.9 | 2 | 167.2 | 8 | 0.2 | 46.22 | 66.28 | 138867.68 | 134755.94 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:05:00 | Operating | 1332.9 | -14.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -19.615 | 25.2 | 3 | 25 | 1 | 166.4 | 2 | 166.6 | 8 | 0.3 | 46.28 | 67.4 | 138867.74 | 134757.14 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:10:00 | Operating | 1325.1 | -42.6 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -56.496 | 25.3 | 6 | 25 | 1 | 165.5 | 2 | 165.8 | 8 | 0.3 | 46.28 | 69.86 | 138867.74 | 134759.7 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:15:00 | Operating | 1333.1 | 1.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 2.216 | 25.3 | 6 | 25.1 | 1 | 166.5 | 2 | 166.7 | 8 | 0.2 | 46.34 | 71.52 | 138867.8 | 134761.18 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:20:00 | Operating | 1332.9 | -7.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -10.389 | 25.3 | 3 | 25.1 | 1 | 166.4 | 2 | 166.7 | 8 | 0.2 | 46.34 | 71.92 | 138867.8 | 134761.62 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:25:00 | Operating | 1333 | -7.6 | 13 | 99 | 11 | 90 | 656.835 | 81.181 | -10.185 | 25.3 | 4 | 25.1 | 1 | 166.4 | 2 | 166.7 | 8 | 0.2 | 46.36 | 72.6 | 138867.82 | 134762.26 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:30:00 | Operating | 1332 | -6 | 13 | 99 | 11 | 90 | 656.835 | 81.181 | -7.973 | 25.3 | 4 | 25.1 | 1 | 166.2 | 2 | 166.5 | 8 | 0.2 | 46.36 | 73.58 | 138867.82 | 134763.24 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:35:00 | Operating | 1334 | 3.4 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | 4.535 | 25.4 | 6 | 25.1 | 1 | 166.6 | 2 | 166.9 | 8 | 0.3 | 46.42 | 74.14 | 138867.88 | 134763.8 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:40:00 | Operating | 1332.9 | -6.4 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -8.5 | 25.3 | 3 | 25.1 | 1 | 166.4 | 2 | 166.6 | 8 | 0.2 | 46.46 | 74.58 | 138867.92 | 134764.24 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:45:00 | Operating | 1333 | -5.3 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -7.033 | 25.4 | 3 | 25.1 | 1 | 166.4 | 2 | 166.7 | 8 | 0.3 | 46.46 | 75.06 | 138867.92 | 134764.72 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:50:00 | Operating | 1333 | -2.2 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -2.947 | 25.3 | 3 | 25.1 | 1 | 166.4 | 2 | 166.7 | 8 | 0.2 | 46.46 | 75.74 | 138867.92 | 134765.4 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 05:55:00 | Operating | 1332 | -3.5 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -4.651 | 25.3 | 3 | 25.1 | 1 | 166.3 | 2 | 166.5 | 8 | 0.2 | 46.46 | 76.46 | 138867.92 | 134766.14 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:00:00 | Operating | 1332 | -3.9 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -5.251 | 25.4 | 3 | 25.1 | 1 | 166.3 | 2 | 166.5 | 8 | 0.3 | 46.5 | 77.12 | 138867.96 | 134766.78 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:05:00 | Operating | 1340.6 | 27.7 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | 37.121 | 25.4 | 4 | 25.1 | 1 | 167.4 | 2 | 167.7 | 8 | 0.3 | 47.48 | 77.4 | 138868.94 | 134767.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:10:00 | Operating | 1345.2 | 21.7 | 13 | 99 | 11 | 90 | 656.835 | 81.181 | 29.151 | 25.4 | 5 | 25.1 | 1 | 168 | 2 | 168.3 | 8 | 0.3 | 50.12 | 77.4 | 138871.68 | 134767.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:15:00 | Operating | 1351.6 | 24.1 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 32.542 | 25.3 | 2 | 25.1 | 1 | 168.7 | 2 | 169 | 8 | 0.2 | 53.98 | 77.4 | 138875.44 | 134767.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:20:00 | Operating | 1355.5 | 35.5 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | 48.179 | 25.4 | 5 | 25.1 | 1 | 169.3 | 2 | 169.5 | 8 | 0.3 | 58.24 | 77.4 | 138879.84 | 134767.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:25:00 | Operating | 1352.3 | 15.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 21.209 | 25.4 | 4 | 25.1 | 1 | 168.8 | 2 | 169.1 | 4 | 0.3 | 60.4 | 77.4 | 138881.9 | 134767.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:30:00 | Operating | 1352.6 | 17.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 23.68 | 25.4 | 3 | 25.1 | 1 | 168.9 | 2 | 169.2 | 8 | 0.3 | 61.72 | 77.4 | 138883.18 | 134767.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:35:00 | Operating | 1356.5 | 25.6 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | 34.546 | 25.4 | 4 | 25.2 | 1 | 169.4 | 2 | 169.6 | 8 | 0.2 | 64.5 | 77.4 | 138885.96 | 134767.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:40:00 | Operating | 1357.8 | 27.6 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 37.472 | 25.5 | 5 | 25.2 | 1 | 169.6 | 2 | 169.8 | 8 | 0.2 | 67.1 | 77.4 | 138888.56 | 134767.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:45:00 | Operating | 1361.5 | 33.5 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | 45.719 | 25.4 | 4 | 25.2 | 1 | 170.1 | 2 | 170.3 | 8 | 0.3 | 71.1 | 77.4 | 138892.56 | 134767.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:50:00 | Operating | 1360.9 | 25.4 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 34.582 | 25.5 | 5 | 25.2 | 1 | 170 | 2 | 170.2 | 8 | 0.3 | 74 | 77.4 | 138895.58 | 134767.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 06:55:00 | Operating | 1354.8 | -8.7 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -11.806 | 25.4 | 3 | 25.2 | 1 | 169.3 | 2 | 169.5 | 4 | 0.2 | 75.32 | 77.48 | 138896.78 | 134767.14 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:00:00 | Operating | 1349.8 | -23.7 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -31.962 | 25.5 | 5 | 25.2 | 1 | 168.7 | 2 | 168.8 | 4 | 0.3 | 75.4 | 78.18 | 138896.86 | 134768 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:05:00 | Operating | 1349.7 | -5.2 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -7.032 | 25.5 | 3 | 25.3 | 1 | 168.6 | 2 | 168.8 | 4 | 0.3 | 75.4 | 79.9 | 138896.86 | 134769.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:10:00 | Operating | 1348 | -0.6 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -0.792 | 25.5 | 5 | 25.3 | 1 | 168.4 | 2 | 168.6 | 4 | 0.2 | 75.4 | 81.44 | 138896.86 | 134771.1 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:15:00 | Operating | 1350.2 | -6.8 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -9.188 | 25.6 | 5 | 25.3 | 1 | 168.7 | 2 | 168.9 | 4 | 0.2 | 76.08 | 81.48 | 138897.54 | 134771.16 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:20:00 | Operating | 1349.2 | -8.9 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -12.046 | 25.5 | 3 | 25.3 | 1 | 168.6 | 2 | 168.8 | 4 | 0.2 | 76.34 | 81.72 | 138897.8 | 134771.42 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:25:00 | Operating | 1343.4 | -17.9 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -24.047 | 25.5 | 3 | 25.3 | 1 | 167.9 | 2 | 168.1 | 4 | 0.3 | 76.34 | 83.64 | 138897.8 | 134773.3 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:30:00 | Operating | 1345 | -8.9 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -12.176 | 25.5 | 3 | 25.3 | 1 | 168 | 2 | 168.2 | 4 | 0.2 | 76.34 | 84.48 | 138897.8 | 134774.18 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:35:00 | Operating | 1342.2 | -16.6 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -22.335 | 25.6 | 6 | 25.3 | 1 | 167.7 | 2 | 167.9 | 4 | 0.3 | 76.64 | 85.6 | 138898.1 | 134775.26 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:40:00 | Operating | 1345.4 | 1.6 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 2.299 | 25.6 | 5 | 25.3 | 1 | 168.1 | 2 | 168.3 | 4 | 0.3 | 76.7 | 86.64 | 138898.18 | 134776.3 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:45:00 | Operating | 1348.2 | 5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 6.8 | 25.6 | 5 | 25.3 | 1 | 168.4 | 2 | 168.6 | 4 | 0.3 | 77.36 | 86.72 | 138898.82 | 134776.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:50:00 | Operating | 1352 | 10.3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 13.912 | 25.6 | 5 | 25.3 | 1 | 168.8 | 2 | 169 | 8 | 0.3 | 78.26 | 86.72 | 138899.78 | 134776.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 07:55:00 | Operating | 1349.3 | 2.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 3.312 | 25.6 | 3 | 25.3 | 1 | 168.5 | 2 | 168.7 | 8 | 0.3 | 78.76 | 86.74 | 138900.22 | 134776.4 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:00:00 | Operating | 1350.8 | 6.2 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 8.429 | 25.6 | 5 | 25.3 | 1 | 168.7 | 2 | 168.9 | 4 | 0.3 | 79.06 | 86.8 | 138900.54 | 134776.46 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:05:00 | Operating | 1350.1 | -2.2 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -3.017 | 25.6 | 5 | 25.3 | 1 | 168.7 | 2 | 168.8 | 8 | 0.3 | 79.72 | 86.8 | 138901.18 | 134776.46 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:10:00 | Operating | 1346.8 | -2.9 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -3.926 | 25.6 | 5 | 25.4 | 1 | 168.3 | 2 | 168.5 | 8 | 0.2 | 79.72 | 87.74 | 138901.18 | 134777.4 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:15:00 | Operating | 1348.4 | 4.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 6.195 | 25.6 | 3 | 25.4 | 1 | 168.4 | 2 | 168.6 | 8 | 0.2 | 79.9 | 88.2 | 138901.36 | 134777.86 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:20:00 | Operating | 1346 | -0.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -0.659 | 25.6 | 3 | 25.4 | 1 | 168.2 | 2 | 168.4 | 8 | 0.2 | 79.96 | 88.9 | 138901.42 | 134778.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:25:00 | Operating | 1348 | 1.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 2.412 | 25.7 | 6 | 25.4 | 1 | 168.4 | 2 | 168.6 | 8 | 0.2 | 80.32 | 88.9 | 138901.78 | 134778.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:30:00 | Operating | 1353.4 | 13.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 18.623 | 25.6 | 3 | 25.4 | 1 | 169.1 | 2 | 169.3 | 8 | 0.2 | 81.46 | 88.9 | 138903.02 | 134778.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:35:00 | Operating | 1355.5 | 23 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | 31.139 | 25.7 | 6 | 25.4 | 1 | 169.3 | 2 | 169.5 | 8 | 0.3 | 82.66 | 88.9 | 138904.12 | 134778.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:40:00 | Operating | 1359.6 | 27.5 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | 37.375 | 25.8 | 8 | 25.4 | 1 | 169.8 | 2 | 170 | 8 | 0.3 | 84.72 | 88.9 | 138906.18 | 134778.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:45:00 | Operating | 1358.3 | 14.6 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 19.796 | 25.7 | 8 | 25.4 | 1 | 169.7 | 2 | 169.9 | 8 | 0.3 | 86.88 | 88.9 | 138908.38 | 134778.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:50:00 | Operating | 1365.2 | 36.5 | 17 | 99 | 15 | 90 | 627.314 | 110.702 | 49.883 | 25.7 | 5 | 25.4 | 1 | 170.5 | 2 | 170.7 | 8 | 0.4 | 90.24 | 88.9 | 138911.7 | 134778.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 08:55:00 | Operating | 1368.2 | 39.4 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 54.004 | 25.8 | 8 | 25.4 | 1 | 170.9 | 2 | 171.1 | 8 | 0.4 | 94.56 | 88.9 | 138916.02 | 134778.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:00:00 | Operating | 1371.6 | 45.3 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | 62.169 | 25.8 | 6 | 25.5 | 1 | 171.2 | 2 | 171.4 | 8 | 0.3 | 99.06 | 88.9 | 138920.74 | 134778.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:05:00 | Operating | 1371.6 | 34.6 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 47.512 | 25.8 | 5 | 25.5 | 1 | 171.2 | 2 | 171.4 | 8 | 0.4 | 104.58 | 88.9 | 138926.18 | 134778.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:10:00 | Operating | 1369.1 | 26.1 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 35.748 | 25.9 | 6 | 25.5 | 1 | 171 | 2 | 171.2 | 8 | 0.4 | 107.04 | 88.92 | 138928.5 | 134778.58 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:15:00 | Operating | 1370.8 | 31 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 42.539 | 25.9 | 8 | 25.5 | 1 | 171.1 | 2 | 171.3 | 8 | 0.4 | 109.24 | 88.92 | 138930.7 | 134778.58 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:20:00 | Operating | 1362.3 | -16.1 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -21.988 | 26 | 8 | 25.5 | 1 | 170.2 | 2 | 170.4 | 8 | 0.5 | 110.34 | 88.96 | 138931.8 | 134778.64 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:25:00 | Operating | 1369.4 | 43.5 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 59.604 | 26 | 8 | 25.6 | 1 | 171 | 2 | 171.2 | 8 | 0.4 | 111.56 | 91.32 | 138933.2 | 134780.98 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:30:00 | Operating | 1367 | 25.9 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 35.416 | 26 | 8 | 25.6 | 1 | 170.8 | 2 | 170.9 | 8 | 0.4 | 113 | 91.84 | 138934.46 | 134781.5 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:35:00 | Operating | 1371.9 | 33 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 45.319 | 26.1 | 8 | 25.6 | 1 | 171.4 | 2 | 171.5 | 6 | 0.5 | 118 | 91.84 | 138939.46 | 134781.5 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:40:00 | Operating | 1378.2 | 52.7 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | 72.71 | 26.1 | 8 | 25.7 | 1 | 172.2 | 2 | 172.4 | 8 | 0.4 | 126.4 | 91.84 | 138947.86 | 134781.5 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:45:00 | Operating | 1376.1 | 49.9 | 22 | 99 | 20 | 90 | 590.413 | 147.603 | 68.801 | 26.1 | 8 | 25.7 | 1 | 171.9 | 2 | 172.1 | 8 | 0.5 | 129.38 | 92.02 | 138951.04 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:50:00 | Operating | 1383.2 | 82.3 | 23 | 99 | 21 | 90 | 583.033 | 154.983 | 113.961 | 26.2 | 8 | 25.7 | 1 | 172.7 | 2 | 172.9 | 8 | 0.5 | 135.78 | 92.02 | 138957.56 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 09:55:00 | Operating | 1385.7 | 78.1 | 24 | 99 | 22 | 90 | 575.653 | 162.363 | 108.486 | 26.3 | 8 | 25.8 | 1 | 173.1 | 2 | 173.2 | 8 | 0.5 | 146.08 | 92.02 | 138967.54 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:00:00 | Operating | 1379.3 | 33.9 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | 46.739 | 26.3 | 8 | 25.8 | 1 | 172.3 | 2 | 172.5 | 8 | 0.5 | 150.74 | 92.02 | 138972.2 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:05:00 | Operating | 1379.4 | 32.4 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | 44.797 | 26.4 | 8 | 25.9 | 1 | 172.4 | 2 | 172.5 | 8 | 0.5 | 154.86 | 92.02 | 138976.32 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:10:00 | Operating | 1375.5 | 7.3 | 26 | 99 | 24 | 90 | 560.893 | 177.124 | 10.066 | 26.3 | 8 | 25.9 | 1 | 171.9 | 2 | 172 | 8 | 0.4 | 156.94 | 92.02 | 138978.4 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:15:00 | Operating | 1380.5 | 40.2 | 26 | 99 | 24 | 90 | 560.893 | 177.124 | 55.586 | 26.4 | 8 | 25.9 | 1 | 172.5 | 2 | 172.6 | 7 | 0.5 | 159.84 | 92.02 | 138981.3 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:20:00 | Operating | 1383.7 | 45.4 | 27 | 99 | 26 | 90 | 546.132 | 191.884 | 62.868 | 26.4 | 8 | 25.9 | 1 | 172.9 | 2 | 173 | 8 | 0.5 | 166.56 | 92.02 | 138988.02 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:25:00 | Operating | 1382.9 | 49.5 | 27 | 99 | 26 | 90 | 546.132 | 191.884 | 68.551 | 26.4 | 8 | 25.9 | 1 | 172.8 | 1 | 172.9 | 7 | 0.5 | 170.08 | 92.02 | 138991.54 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:30:00 | Operating | 1383.9 | 48.4 | 28 | 99 | 27 | 90 | 538.752 | 199.264 | 66.995 | 26.5 | 8 | 25.9 | 7 | 173 | 2 | 173 | 7 | 0.6 | 175.06 | 92.02 | 138996.72 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:35:00 | Operating | 1385.1 | 46.4 | 29 | 99 | 28 | 90 | 531.372 | 206.644 | 64.392 | 26.6 | 8 | 26 | 1 | 173.1 | 2 | 173.2 | 7 | 0.6 | 181.74 | 92.02 | 139003.44 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:40:00 | Operating | 1381.1 | 26.4 | 30 | 99 | 29 | 90 | 523.992 | 214.025 | 36.371 | 26.6 | 8 | 26 | 1 | 172.6 | 1 | 172.7 | 7 | 0.6 | 185.72 | 92.02 | 139007.18 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:45:00 | Operating | 1386.7 | 63.2 | 30 | 99 | 29 | 90 | 523.992 | 214.025 | 87.688 | 26.7 | 8 | 26.1 | 1 | 173.3 | 2 | 173.3 | 7 | 0.6 | 190.68 | 92.02 | 139012.38 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:50:00 | Operating | 1387.1 | 61.8 | 31 | 99 | 30 | 90 | 516.612 | 221.405 | 85.741 | 26.7 | 8 | 26.1 | 7 | 173.4 | 5 | 173.4 | 7 | 0.6 | 197.9 | 92.02 | 139019.62 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 10:55:00 | Operating | 1385.1 | 49 | 32 | 99 | 31 | 90 | 509.231 | 228.785 | 68.04 | 26.9 | 8 | 26.2 | 1 | 173.1 | 5 | 173.2 | 7 | 0.7 | 203.46 | 92.02 | 139024.92 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:00:00 | Operating | 1392.2 | 102.2 | 33 | 99 | 32 | 90 | 501.851 | 236.165 | 142.358 | 27 | 8 | 26.4 | 1 | 174 | 8 | 174 | 7 | 0.6 | 211.24 | 92.02 | 139033.12 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:05:00 | Operating | 1392.9 | 100.9 | 35 | 99 | 34 | 90 | 487.091 | 250.925 | 140.627 | 27.3 | 8 | 26.6 | 1 | 174.1 | 5 | 174.1 | 2 | 0.6 | 224.9 | 92.02 | 139046.36 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:10:00 | Operating | 1400 | 168.6 | 37 | 99 | 36 | 90 | 472.331 | 265.686 | 236.35 | 27.6 | 8 | 26.9 | 1 | 174.9 | 6 | 175 | 7 | 0.7 | 238.42 | 92.02 | 139059.88 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:15:00 | Operating | 1397.4 | 141 | 40 | 99 | 38 | 90 | 457.57 | 280.446 | 197.163 | 28.1 | 8 | 27.5 | 1 | 174.6 | 8 | 174.6 | 4 | 0.6 | 257.84 | 92.02 | 139080 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:20:00 | Operating | 1391.6 | 97.8 | 42 | 99 | 40 | 90 | 442.81 | 295.206 | 136.165 | 28.3 | 8 | 27.8 | 1 | 173.9 | 8 | 174 | 2 | 0.6 | 271.14 | 92.02 | 139093.08 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:25:00 | Operating | 1393.4 | 115.2 | 43 | 99 | 41 | 90 | 435.43 | 302.587 | 160.685 | 28.5 | 8 | 27.8 | 1 | 174.1 | 5 | 174.2 | 4 | 0.7 | 282.66 | 92.02 | 139104.6 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:30:00 | Operating | 1397.1 | 146.4 | 45 | 99 | 44 | 90 | 413.289 | 324.727 | 204.762 | 28.7 | 8 | 28.1 | 1 | 174.6 | 8 | 174.6 | 7 | 0.7 | 298.56 | 92.02 | 139120.02 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:35:00 | Operating | 1401.6 | 175.6 | 48 | 99 | 46 | 90 | 398.529 | 339.487 | 246.317 | 29.1 | 8 | 28.3 | 1 | 175.2 | 7 | 175.2 | 5 | 0.7 | 317.08 | 92.02 | 139139.28 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:40:00 | Operating | 1402.2 | 171 | 51 | 99 | 49 | 90 | 376.388 | 361.628 | 239.898 | 29.5 | 8 | 28.7 | 1 | 175.2 | 2 | 175.3 | 5 | 0.7 | 338.62 | 92.02 | 139160.08 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:45:00 | Operating | 1386.5 | 47.4 | 52 | 99 | 51 | 90 | 361.628 | 376.388 | 65.739 | 29.5 | 8 | 28.7 | 1 | 173.4 | 1 | 173.4 | 7 | 0.8 | 350.32 | 92.02 | 139171.78 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:50:00 | Operating | 1391.1 | 87.1 | 53 | 99 | 52 | 90 | 354.248 | 383.768 | 121.266 | 29.3 | 8 | 28.6 | 1 | 173.8 | 1 | 173.9 | 5 | 0.9 | 355.54 | 92.02 | 139177 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 11:55:00 | Operating | 1400.2 | 155 | 55 | 99 | 54 | 90 | 339.487 | 398.529 | 217.334 | 29.3 | 8 | 28.5 | 1 | 174.8 | 2 | 174.9 | 5 | 0.8 | 368.82 | 92.02 | 139190.28 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:00:00 | Operating | 1400.8 | 132.3 | 58 | 99 | 56 | 90 | 324.727 | 413.289 | 185.531 | 29.7 | 8 | 28.8 | 3 | 175.1 | 1 | 175.1 | 5 | 0.8 | 387.36 | 92.02 | 139209.4 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:05:00 | Operating | 1399.6 | 122.1 | 60 | 99 | 58 | 90 | 309.967 | 428.05 | 170.999 | 29.7 | 8 | 28.9 | 1 | 174.9 | 2 | 175 | 5 | 0.8 | 401.5 | 92.02 | 139222.96 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:10:00 | Operating | 1400.4 | 117.2 | 61 | 99 | 60 | 90 | 295.206 | 442.81 | 164.326 | 29.8 | 8 | 28.9 | 3 | 175 | 2 | 175.2 | 5 | 0.8 | 414.76 | 92.02 | 139236.22 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:15:00 | Operating | 1398.3 | 92 | 63 | 99 | 61 | 90 | 287.826 | 450.19 | 128.703 | 29.8 | 8 | 28.9 | 3 | 174.7 | 2 | 174.9 | 5 | 0.9 | 426.18 | 92.02 | 139247.64 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:20:00 | Operating | 1409 | 160.6 | 65 | 99 | 63 | 90 | 273.066 | 464.95 | 226.33 | 29.8 | 8 | 28.9 | 3 | 175.9 | 2 | 176.1 | 5 | 0.9 | 437.54 | 92.02 | 139259.66 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:25:00 | Operating | 1405.9 | 118.8 | 67 | 99 | 65 | 90 | 258.306 | 479.711 | 167.191 | 30.1 | 8 | 29.1 | 3 | 175.7 | 2 | 175.8 | 5 | 0.9 | 455.04 | 92.02 | 139276.5 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:30:00 | Operating | 1403.7 | 101.2 | 69 | 99 | 67 | 90 | 243.545 | 494.471 | 142.302 | 29.9 | 8 | 29.1 | 1 | 175.5 | 2 | 175.5 | 6 | 0.8 | 467.16 | 92.02 | 139288.62 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:35:00 | Operating | 1403.8 | 89.7 | 71 | 99 | 69 | 90 | 228.785 | 509.231 | 126.109 | 30 | 8 | 29.1 | 3 | 175.7 | 3 | 175.6 | 6 | 0.9 | 483.4 | 92.02 | 139304.86 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:40:00 | Operating | 1397.1 | 40.2 | 72 | 99 | 71 | 90 | 214.025 | 523.992 | 56.17 | 29.8 | 8 | 29 | 1 | 174.7 | 8 | 174.7 | 5 | 0.8 | 491.7 | 92.02 | 139313.16 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:45:00 | Operating | 1401.6 | 85.9 | 72 | 99 | 71 | 90 | 214.025 | 523.992 | 120.495 | 29.6 | 8 | 28.8 | 1 | 175.2 | 7 | 175.3 | 6 | 0.8 | 495.4 | 92.02 | 139316.86 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:50:00 | Operating | 1400.8 | 59.9 | 74 | 99 | 72 | 90 | 206.644 | 531.372 | 83.959 | 29.4 | 8 | 28.6 | 3 | 175.2 | 3 | 175.2 | 5 | 0.8 | 505.14 | 92.02 | 139326.6 | 134781.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 12:55:00 | Operating | 1385.3 | -36.4 | 74 | 99 | 73 | 90 | 199.264 | 538.752 | -50.586 | 29.3 | 8 | 28.4 | 1 | 173.3 | 5 | 173.3 | 2 | 0.9 | 507.84 | 92.36 | 139329.3 | 134782.02 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:00:00 | Operating | 1390.2 | 1.1 | 74 | 99 | 73 | 90 | 199.264 | 538.752 | 1.509 | 29.1 | 8 | 28.1 | 3 | 173.8 | 8 | 173.8 | 2 | 1 | 508.32 | 93.34 | 139329.78 | 134783 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:05:00 | Operating | 1391.8 | 21.9 | 74 | 99 | 73 | 90 | 199.264 | 538.752 | 30.56 | 28.8 | 8 | 28 | 3 | 174 | 8 | 174.1 | 2 | 0.8 | 508.9 | 93.7 | 139330.36 | 134783.36 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:10:00 | Operating | 1413.1 | 133.2 | 75 | 99 | 74 | 90 | 191.884 | 546.132 | 188.423 | 28.7 | 8 | 27.8 | 3 | 176.6 | 2 | 176.7 | 5 | 0.9 | 517.66 | 93.7 | 139339.12 | 134783.36 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:15:00 | Operating | 1410.7 | 108.8 | 77 | 99 | 76 | 90 | 177.124 | 560.893 | 153.597 | 28.8 | 8 | 27.8 | 3 | 176.3 | 8 | 176.4 | 7 | 1 | 531.9 | 93.7 | 139353.86 | 134783.36 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:20:00 | Operating | 1404.7 | 70.8 | 79 | 99 | 77 | 90 | 169.743 | 568.273 | 99.643 | 28.7 | 8 | 27.8 | 1 | 175.6 | 8 | 175.7 | 7 | 0.9 | 543.16 | 93.7 | 139364.62 | 134783.36 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:25:00 | Operating | 1410.1 | 98.1 | 80 | 99 | 79 | 90 | 154.983 | 583.033 | 138.32 | 28.5 | 8 | 27.6 | 3 | 176.1 | 8 | 176.2 | 7 | 0.9 | 552.92 | 93.7 | 139374.38 | 134783.36 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:30:00 | Operating | 1407.4 | 87.6 | 82 | 99 | 80 | 90 | 147.603 | 590.413 | 123.398 | 28.4 | 8 | 27.5 | 1 | 175.9 | 3 | 176 | 7 | 0.9 | 564.08 | 93.7 | 139385.54 | 134783.36 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:35:00 | Operating | 1400.5 | 36.8 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 51.622 | 28.3 | 8 | 27.4 | 1 | 175.1 | 5 | 175.2 | 7 | 0.9 | 572.84 | 93.7 | 139394.3 | 134783.36 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:40:00 | Operating | 1391 | 6.4 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 8.946 | 28.2 | 8 | 27.1 | 3 | 173.8 | 3 | 173.8 | 2 | 1 | 573.62 | 95.62 | 139395.1 | 134785.28 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:45:00 | Operating | 1392.9 | 14.9 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 20.711 | 28 | 8 | 27 | 1 | 174.2 | 5 | 174.2 | 2 | 1 | 574.78 | 95.62 | 139396.3 | 134785.28 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:50:00 | Operating | 1384.3 | -38.9 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -53.89 | 27.7 | 8 | 26.7 | 3 | 173.2 | 5 | 173.2 | 2 | 1 | 576.3 | 96.3 | 139397.76 | 134785.96 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 13:55:00 | Operating | 1384.1 | -17.1 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -23.68 | 27.6 | 8 | 26.6 | 1 | 173.1 | 5 | 173.1 | 2 | 0.9 | 576.3 | 99.18 | 139397.76 | 134788.9 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:00:00 | Operating | 1402.4 | 77.6 | 83 | 99 | 81 | 90 | 140.223 | 597.793 | 108.963 | 27.3 | 8 | 26.3 | 1 | 175.3 | 1 | 175.3 | 5 | 0.9 | 578 | 100.56 | 139399.76 | 134790.22 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:05:00 | Operating | 1408.8 | 71.7 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | 101.093 | 27.2 | 8 | 26.2 | 3 | 176 | 3 | 176.1 | 4 | 0.9 | 587 | 100.56 | 139408.46 | 134790.22 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:10:00 | Operating | 1404 | 40.2 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | 56.514 | 27 | 8 | 26.1 | 1 | 175.5 | 5 | 175.6 | 7 | 1 | 595.48 | 100.56 | 139417.12 | 134790.22 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:15:00 | Operating | 1403.2 | 40.3 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 56.598 | 26.9 | 8 | 25.9 | 1 | 175.4 | 5 | 175.5 | 7 | 0.9 | 599.72 | 100.56 | 139421.36 | 134790.22 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:20:00 | Operating | 1389.3 | -23.2 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -32.208 | 26.8 | 8 | 25.7 | 3 | 173.7 | 5 | 173.7 | 7 | 0.9 | 601.34 | 100.9 | 139422.8 | 134790.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:25:00 | Operating | 1391.6 | 16 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 22.299 | 26.5 | 8 | 25.6 | 1 | 174 | 5 | 174 | 7 | 1 | 601.46 | 102.78 | 139423 | 134792.44 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:30:00 | Operating | 1394.2 | 4.5 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 6.218 | 26.3 | 8 | 25.3 | 1 | 174.3 | 5 | 174.3 | 7 | 1 | 603.68 | 102.78 | 139425.14 | 134792.44 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:35:00 | Operating | 1378.8 | -40.5 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | -55.88 | 26.1 | 8 | 25.1 | 1 | 172.4 | 5 | 172.4 | 2 | 1 | 603.84 | 106.04 | 139425.3 | 134795.7 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:40:00 | Operating | 1404.4 | 62.7 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 88.157 | 25.9 | 8 | 25 | 1 | 175.5 | 1 | 175.6 | 5 | 1.1 | 606.98 | 106.66 | 139428.72 | 134796.32 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:45:00 | Operating | 1405.3 | 35.3 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 49.721 | 25.8 | 8 | 24.7 | 1 | 175.7 | 5 | 175.7 | 7 | 1 | 613.3 | 106.66 | 139434.92 | 134796.32 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:50:00 | Operating | 1401.1 | 28.4 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 39.789 | 25.5 | 8 | 24.5 | 3 | 175.1 | 5 | 175.2 | 7 | 1 | 615.86 | 106.66 | 139437.44 | 134796.32 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 14:55:00 | Operating | 1390.9 | -12.5 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -17.438 | 25.4 | 8 | 24.3 | 3 | 173.8 | 5 | 173.8 | 7 | 1 | 617.58 | 107.22 | 139439.04 | 134796.88 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:00:00 | Operating | 1384.4 | -23.9 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -33.168 | 25.2 | 8 | 24.1 | 1 | 173.1 | 5 | 173.2 | 2 | 1 | 617.58 | 108.62 | 139439.04 | 134798.46 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:05:00 | Operating | 1392.5 | 16.5 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 23.066 | 25 | 8 | 23.9 | 1 | 174.1 | 5 | 174.1 | 7 | 1 | 618.06 | 109.32 | 139439.52 | 134798.98 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:10:00 | Operating | 1398.4 | 18.6 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 25.985 | 24.8 | 8 | 23.9 | 1 | 174.8 | 5 | 174.8 | 7 | 1.1 | 620.72 | 109.32 | 139442.26 | 134798.98 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:15:00 | Operating | 1394.9 | 4.4 | 88 | 99 | 86 | 90 | 103.322 | 634.694 | 6.18 | 24.7 | 8 | 23.8 | 1 | 174.4 | 5 | 174.5 | 7 | 0.9 | 622.32 | 109.32 | 139443.8 | 134798.98 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:20:00 | Operating | 1383 | -30.9 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -42.772 | 24.7 | 8 | 23.8 | 1 | 172.9 | 5 | 172.9 | 2 | 0.9 | 622.36 | 110.9 | 139443.82 | 134800.68 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:25:00 | Operating | 1377.7 | -38.9 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -53.677 | 24.6 | 8 | 23.7 | 1 | 172.2 | 4 | 172.3 | 2 | 0.8 | 622.36 | 115.48 | 139443.82 | 134805.14 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:30:00 | Operating | 1377.3 | -32.3 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -44.477 | 24.6 | 8 | 23.7 | 1 | 172.2 | 4 | 172.2 | 6 | 0.8 | 622.36 | 120 | 139443.82 | 134809.78 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:35:00 | Operating | 1379.3 | -23.6 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | -32.516 | 24.5 | 8 | 23.7 | 1 | 172.4 | 5 | 172.5 | 6 | 0.9 | 622.36 | 123.28 | 139443.82 | 134812.94 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:40:00 | Operating | 1387 | 11.2 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 15.556 | 24.5 | 8 | 23.7 | 1 | 173.4 | 8 | 173.4 | 6 | 0.9 | 623.22 | 123.58 | 139444.72 | 134813.24 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:45:00 | Operating | 1390.4 | 19.8 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 27.545 | 24.5 | 8 | 23.7 | 1 | 173.7 | 8 | 173.7 | 6 | 0.8 | 624.06 | 123.58 | 139445.52 | 134813.24 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:50:00 | Operating | 1389.1 | 19 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 26.381 | 24.5 | 8 | 23.7 | 1 | 173.5 | 8 | 173.6 | 5 | 0.9 | 624.4 | 123.98 | 139445.9 | 134813.64 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 15:55:00 | Operating | 1381.9 | -25.4 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -35.175 | 24.5 | 8 | 23.7 | 1 | 172.8 | 8 | 172.8 | 2 | 0.9 | 624.86 | 124.92 | 139446.32 | 134814.58 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:00:00 | Operating | 1378.3 | -26.2 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | -36.118 | 24.6 | 8 | 23.7 | 1 | 172.3 | 5 | 172.3 | 2 | 0.8 | 624.86 | 129.1 | 139446.32 | 134818.88 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:05:00 | Operating | 1379.5 | -19.4 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | -26.731 | 24.6 | 8 | 23.7 | 1 | 172.5 | 5 | 172.5 | 2 | 0.9 | 624.86 | 131.86 | 139446.32 | 134821.6 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:10:00 | Operating | 1380.2 | -18.1 | 84 | 99 | 84 | 90 | 118.082 | 619.934 | -25.012 | 24.5 | 8 | 23.7 | 1 | 172.6 | 5 | 172.6 | 2 | 0.7 | 624.86 | 133.84 | 139446.32 | 134823.5 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:15:00 | Operating | 1380.3 | -17.6 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -24.342 | 24.5 | 8 | 23.8 | 1 | 172.6 | 8 | 172.7 | 2 | 0.8 | 624.86 | 135.54 | 139446.32 | 134825.2 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:20:00 | Operating | 1381 | -17.8 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -24.654 | 24.5 | 8 | 23.8 | 1 | 172.7 | 8 | 172.7 | 2 | 0.7 | 624.86 | 136.84 | 139446.32 | 134826.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:25:00 | Operating | 1380.9 | -15.4 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -21.292 | 24.5 | 8 | 23.8 | 1 | 172.6 | 5 | 172.7 | 2 | 0.7 | 624.86 | 138.78 | 139446.32 | 134828.44 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:30:00 | Operating | 1381.5 | -14.1 | 84 | 99 | 82 | 90 | 132.843 | 605.174 | -19.541 | 24.6 | 8 | 23.8 | 1 | 172.7 | 8 | 172.7 | 2 | 0.7 | 624.92 | 139.9 | 139446.38 | 134829.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:35:00 | Operating | 1386 | 14.2 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 19.684 | 24.5 | 8 | 23.7 | 1 | 173.2 | 8 | 173.3 | 2 | 0.7 | 625.08 | 140.9 | 139446.6 | 134830.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:40:00 | Operating | 1391.2 | 20.9 | 84 | 99 | 82 | 90 | 132.843 | 605.174 | 29.075 | 24.5 | 8 | 23.8 | 1 | 173.8 | 8 | 173.9 | 5 | 0.7 | 627.24 | 140.9 | 139448.7 | 134830.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:45:00 | Operating | 1392.2 | 15.7 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | 21.878 | 24.5 | 8 | 23.9 | 1 | 174 | 8 | 174 | 6 | 0.8 | 629.1 | 140.9 | 139450.62 | 134830.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:50:00 | Operating | 1383.6 | -22.7 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -31.474 | 24.6 | 8 | 23.9 | 1 | 173 | 8 | 173 | 2 | 0.8 | 629.76 | 141.54 | 139451.22 | 134831.2 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 16:55:00 | Operating | 1381.4 | -16.8 | 84 | 99 | 82 | 90 | 132.843 | 605.174 | -23.216 | 24.6 | 8 | 23.8 | 1 | 172.8 | 8 | 172.8 | 2 | 0.7 | 629.78 | 144.14 | 139451.24 | 134833.82 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:00:00 | Operating | 1373 | -58.7 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -80.607 | 24.6 | 8 | 23.8 | 1 | 171.6 | 5 | 171.7 | 2 | 0.7 | 629.78 | 148.6 | 139451.24 | 134838.5 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:05:00 | Operating | 1383.2 | 11.8 | 83 | 99 | 81 | 90 | 140.223 | 597.793 | 16.382 | 24.5 | 8 | 23.9 | 1 | 172.9 | 8 | 172.9 | 2 | 0.7 | 629.88 | 152.22 | 139451.34 | 134841.88 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:10:00 | Operating | 1384.4 | 7.9 | 83 | 99 | 81 | 90 | 140.223 | 597.793 | 10.962 | 24.6 | 8 | 23.9 | 1 | 173 | 8 | 173.1 | 6 | 0.7 | 630.16 | 152.52 | 139451.64 | 134842.18 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:15:00 | Operating | 1378.3 | -30.2 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -41.702 | 24.6 | 8 | 23.9 | 1 | 172.3 | 5 | 172.3 | 2 | 0.7 | 630.38 | 154.46 | 139451.84 | 134844.12 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:20:00 | Operating | 1378.7 | -23.5 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -32.442 | 24.5 | 8 | 23.9 | 1 | 172.4 | 5 | 172.4 | 2 | 0.7 | 630.38 | 157.3 | 139451.84 | 134847.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:25:00 | Operating | 1378.6 | -23.7 | 81 | 99 | 81 | 90 | 140.223 | 597.793 | -32.696 | 24.6 | 8 | 24 | 1 | 172.4 | 8 | 172.4 | 2 | 0.7 | 630.38 | 160.08 | 139451.84 | 134849.74 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:30:00 | Operating | 1379.7 | -16.6 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -22.929 | 24.5 | 8 | 24 | 1 | 172.5 | 3 | 172.5 | 2 | 0.6 | 630.38 | 162.8 | 139451.84 | 134852.52 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:35:00 | Operating | 1381.8 | -7.1 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -9.883 | 24.6 | 8 | 24 | 1 | 172.8 | 8 | 172.8 | 2 | 0.6 | 630.38 | 164.22 | 139451.84 | 134853.88 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:40:00 | Operating | 1380.9 | -16.9 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -23.405 | 24.7 | 8 | 24 | 1 | 172.7 | 8 | 172.7 | 2 | 0.6 | 630.38 | 165.58 | 139451.84 | 134855.28 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:45:00 | Operating | 1374.2 | -53.8 | 80 | 99 | 79 | 90 | 154.983 | 583.033 | -74.061 | 24.6 | 8 | 24 | 1 | 171.8 | 3 | 171.8 | 2 | 0.6 | 630.38 | 170.18 | 139451.84 | 134859.84 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:50:00 | Operating | 1375.1 | -45.5 | 79 | 99 | 78 | 90 | 162.363 | 575.653 | -62.632 | 24.7 | 8 | 24.1 | 1 | 171.9 | 5 | 172 | 6 | 0.6 | 630.38 | 175.04 | 139451.84 | 134864.88 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 17:55:00 | Operating | 1375.8 | -36.6 | 79 | 99 | 78 | 90 | 162.363 | 575.653 | -50.383 | 24.6 | 8 | 24.1 | 1 | 172 | 3 | 172 | 8 | 0.6 | 630.38 | 180.62 | 139451.84 | 134870.44 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:00:00 | Operating | 1374.4 | -45.6 | 78 | 99 | 77 | 90 | 169.743 | 568.273 | -62.682 | 24.6 | 8 | 24.2 | 1 | 171.8 | 3 | 171.8 | 7 | 0.6 | 630.38 | 187.14 | 139451.84 | 134877 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:05:00 | Operating | 1375.8 | -40 | 77 | 99 | 76 | 90 | 177.124 | 560.893 | -55.104 | 24.8 | 8 | 24.2 | 1 | 172 | 5 | 172 | 8 | 0.6 | 630.38 | 191.4 | 139451.84 | 134881.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:10:00 | Operating | 1375.6 | -41.4 | 76 | 99 | 76 | 90 | 177.124 | 560.893 | -57.071 | 24.7 | 8 | 24.3 | 1 | 172 | 5 | 172 | 7 | 0.4 | 630.38 | 195.66 | 139451.84 | 134885.5 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:15:00 | Operating | 1373.4 | -55.9 | 76 | 99 | 75 | 90 | 184.504 | 553.512 | -76.907 | 24.8 | 8 | 24.3 | 1 | 171.7 | 5 | 171.7 | 8 | 0.5 | 630.38 | 201.26 | 139451.84 | 134890.92 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:20:00 | Operating | 1371.4 | -79.4 | 75 | 99 | 74 | 90 | 191.884 | 546.132 | -108.871 | 24.8 | 8 | 24.4 | 1 | 171.3 | 5 | 171.4 | 8 | 0.4 | 630.38 | 207.9 | 139451.84 | 134897.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:25:00 | Operating | 1366.3 | -93.4 | 73 | 99 | 72 | 90 | 206.644 | 531.372 | -127.836 | 24.9 | 8 | 24.5 | 1 | 170.9 | 2 | 170.9 | 8 | 0.3 | 630.38 | 217.84 | 139451.84 | 134907.5 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:30:00 | Operating | 1364.8 | -92.4 | 72 | 99 | 70 | 90 | 221.405 | 516.612 | -126.29 | 25.1 | 8 | 24.6 | 1 | 170.6 | 2 | 170.7 | 8 | 0.4 | 630.38 | 229.24 | 139451.84 | 134919.28 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:35:00 | Operating | 1362.7 | -96.7 | 70 | 99 | 69 | 90 | 228.785 | 509.231 | -131.895 | 25 | 3 | 24.7 | 2 | 170.3 | 2 | 170.5 | 8 | 0.3 | 630.38 | 239.72 | 139451.84 | 134929.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:40:00 | Operating | 1358.6 | -104.3 | 69 | 99 | 67 | 90 | 243.545 | 494.471 | -141.859 | 25.2 | 6 | 24.9 | 1 | 169.8 | 2 | 170 | 8 | 0.3 | 630.38 | 251.2 | 139451.84 | 134941.3 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:45:00 | Operating | 1355.9 | -104.7 | 67 | 99 | 65 | 90 | 258.306 | 479.711 | -142.137 | 25.4 | 8 | 25 | 1 | 169.5 | 2 | 169.6 | 8 | 0.3 | 630.38 | 263.08 | 139451.84 | 134952.74 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:50:00 | Operating | 1354.6 | -104.7 | 65 | 99 | 64 | 90 | 265.686 | 472.331 | -141.979 | 25.4 | 8 | 25 | 1 | 169.4 | 2 | 169.4 | 8 | 0.4 | 630.38 | 274.7 | 139451.84 | 134964.8 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 18:55:00 | Operating | 1352.3 | -127.6 | 64 | 99 | 62 | 90 | 280.446 | 457.57 | -172.566 | 25.3 | 3 | 25.1 | 1 | 169 | 5 | 169.1 | 8 | 0.4 | 630.38 | 286.2 | 139451.84 | 134976.36 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:00:00 | Operating | 1348.7 | -141.8 | 61 | 99 | 59 | 90 | 302.587 | 435.43 | -191.35 | 25.5 | 6 | 25.1 | 2 | 168.7 | 5 | 168.7 | 8 | 0.3 | 630.38 | 301.2 | 139451.84 | 134991.44 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:05:00 | Operating | 1347.3 | -149 | 59 | 99 | 57 | 90 | 317.347 | 420.669 | -201.068 | 25.5 | 3 | 25.2 | 2 | 168.6 | 5 | 168.6 | 7 | 0.3 | 630.38 | 317.2 | 139451.84 | 135007.48 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:10:00 | Operating | 1347.4 | -145.4 | 56 | 99 | 54 | 90 | 339.487 | 398.529 | -196.15 | 25.7 | 6 | 25.3 | 2 | 168.6 | 5 | 168.6 | 2 | 0.3 | 630.38 | 335.46 | 139451.84 | 135025.72 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:15:00 | Operating | 1345.4 | -161.2 | 54 | 99 | 52 | 90 | 354.248 | 383.768 | -217.064 | 25.7 | 4 | 25.4 | 2 | 168.3 | 5 | 168.4 | 8 | 0.4 | 630.38 | 352.98 | 139451.84 | 135042.64 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:20:00 | Operating | 1344 | -168.3 | 51 | 99 | 49 | 90 | 376.388 | 361.628 | -226.395 | 25.8 | 4 | 25.5 | 2 | 168.2 | 5 | 168.2 | 2 | 0.3 | 630.38 | 370.98 | 139451.84 | 135060.64 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:25:00 | Operating | 1341.3 | -185.3 | 49 | 99 | 46 | 90 | 398.529 | 339.487 | -248.762 | 26 | 4 | 25.6 | 2 | 167.9 | 5 | 167.9 | 7 | 0.4 | 630.38 | 390.52 | 139451.84 | 135080.18 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:30:00 | Operating | 1337.4 | -209 | 46 | 99 | 43 | 90 | 420.669 | 317.347 | -279.729 | 26.2 | 4 | 25.8 | 2 | 167.3 | 5 | 167.4 | 7 | 0.4 | 630.38 | 410.78 | 139451.84 | 135101.32 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:35:00 | Operating | 1335.6 | -213.4 | 42 | 99 | 39 | 90 | 450.19 | 287.826 | -285.262 | 26.6 | 4 | 26.1 | 2 | 167.2 | 5 | 167.3 | 4 | 0.5 | 630.38 | 437.12 | 139451.84 | 135126.78 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:40:00 | Operating | 1334.1 | -208.1 | 39 | 99 | 36 | 90 | 472.331 | 265.686 | -277.848 | 26.9 | 4 | 26.4 | 8 | 167 | 2 | 167 | 4 | 0.5 | 630.38 | 459.84 | 139451.84 | 135149.5 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:45:00 | Operating | 1332.9 | -203.1 | 35 | 99 | 33 | 90 | 494.471 | 243.545 | -270.837 | 27.3 | 4 | 26.7 | 7 | 166.8 | 2 | 166.8 | 4 | 0.6 | 630.38 | 483.44 | 139451.84 | 135173.92 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:50:00 | Operating | 1325.4 | -236.4 | 31 | 99 | 29 | 90 | 523.992 | 214.025 | -313.674 | 27.8 | 4 | 27.2 | 2 | 165.9 | 5 | 166 | 4 | 0.6 | 630.38 | 508.98 | 139451.84 | 135198.64 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 19:55:00 | Operating | 1333 | -151.7 | 28 | 99 | 27 | 90 | 538.752 | 199.264 | -202.281 | 28.4 | 4 | 27.7 | 7 | 166.7 | 5 | 166.8 | 4 | 0.7 | 630.38 | 532.22 | 139451.84 | 135222.54 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:00:00 | Operating | 1340 | -89.5 | 26 | 99 | 24 | 90 | 560.893 | 177.124 | -120.057 | 28.3 | 4 | 27.7 | 7 | 167.6 | 2 | 167.7 | 4 | 0.6 | 630.38 | 545.54 | 139451.84 | 135235.56 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:05:00 | Operating | 1344.9 | -46.5 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | -62.637 | 28.1 | 4 | 27.7 | 1 | 168.2 | 2 | 168.3 | 4 | 0.4 | 630.38 | 554.98 | 139451.84 | 135244.64 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:10:00 | Operating | 1354.5 | 2.2 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | 3.039 | 27.9 | 4 | 27.5 | 7 | 169.4 | 2 | 169.4 | 4 | 0.4 | 630.62 | 556.46 | 139452.08 | 135246.12 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:15:00 | Operating | 1351.5 | -32.8 | 24 | 99 | 23 | 90 | 568.273 | 169.743 | -44.309 | 27.8 | 5 | 27.4 | 7 | 168.9 | 2 | 169 | 8 | 0.4 | 630.68 | 558 | 139452.14 | 135247.8 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:20:00 | Operating | 1345.8 | -49.9 | 24 | 99 | 22 | 90 | 575.653 | 162.363 | -67.435 | 27.8 | 6 | 27.3 | 1 | 168.3 | 2 | 168.4 | 8 | 0.5 | 630.68 | 563.3 | 139452.14 | 135253.14 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:25:00 | Operating | 1344.4 | -49.7 | 23 | 99 | 21 | 90 | 583.033 | 154.983 | -66.91 | 27.6 | 6 | 27.3 | 1 | 168.1 | 2 | 168.2 | 8 | 0.3 | 630.68 | 568.56 | 139452.14 | 135258.42 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:30:00 | Operating | 1344.5 | -38.5 | 22 | 99 | 20 | 90 | 590.413 | 147.603 | -51.848 | 27.6 | 6 | 27.1 | 1 | 168.1 | 2 | 168.2 | 8 | 0.5 | 630.68 | 574.08 | 139452.14 | 135263.74 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:35:00 | Operating | 1344.3 | -37.3 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | -50.146 | 27.3 | 6 | 27 | 3 | 168.1 | 2 | 168.2 | 8 | 0.3 | 630.68 | 578.24 | 139452.14 | 135268.04 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:40:00 | Operating | 1343.6 | -35.3 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | -47.532 | 27.2 | 6 | 26.8 | 3 | 168 | 2 | 168.1 | 8 | 0.4 | 630.68 | 582.46 | 139452.14 | 135272.12 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:45:00 | Operating | 1343.5 | -32.4 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -43.614 | 27.1 | 6 | 26.7 | 1 | 168 | 2 | 168.1 | 8 | 0.3 | 630.68 | 586.24 | 139452.14 | 135276.02 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:50:00 | Operating | 1344.2 | -22.5 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -30.384 | 26.8 | 5 | 26.5 | 1 | 168 | 2 | 168.2 | 8 | 0.4 | 630.68 | 589.72 | 139452.14 | 135279.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 20:55:00 | Operating | 1341.6 | -32.6 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -43.723 | 26.7 | 6 | 26.4 | 1 | 167.7 | 2 | 167.8 | 8 | 0.3 | 630.68 | 593.9 | 139452.14 | 135283.7 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:00:00 | Operating | 1341.9 | -27.8 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | -37.397 | 26.5 | 5 | 26.2 | 1 | 167.7 | 2 | 167.9 | 8 | 0.3 | 630.68 | 596.62 | 139452.14 | 135286.4 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:05:00 | Operating | 1345.3 | -11.9 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | -15.99 | 26.3 | 4 | 26 | 1 | 168.1 | 2 | 168.3 | 8 | 0.3 | 630.68 | 598.46 | 139452.14 | 135288.12 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:10:00 | Operating | 1348.6 | 7.6 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 10.248 | 26.1 | 5 | 25.8 | 3 | 168.5 | 2 | 168.7 | 8 | 0.3 | 630.7 | 599.14 | 139452.16 | 135288.8 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:15:00 | Operating | 1347.2 | -4.3 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -5.78 | 25.9 | 6 | 25.6 | 1 | 168.3 | 2 | 168.5 | 8 | 0.4 | 630.84 | 599.64 | 139452.3 | 135289.3 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:20:00 | Operating | 1345.5 | -14.1 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -18.957 | 25.7 | 6 | 25.4 | 1 | 168.1 | 2 | 168.3 | 8 | 0.3 | 631 | 600.28 | 139452.46 | 135289.94 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:25:00 | Operating | 1348.4 | 3.7 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 4.987 | 25.5 | 6 | 25.1 | 1 | 168.5 | 2 | 168.7 | 8 | 0.4 | 631.06 | 601.18 | 139452.52 | 135290.84 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:30:00 | Operating | 1350.5 | 5.1 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 6.942 | 25.3 | 6 | 24.9 | 1 | 168.7 | 2 | 168.9 | 8 | 0.4 | 631.52 | 601.2 | 139452.98 | 135290.86 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:35:00 | Operating | 1347.1 | -5.4 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -7.303 | 25 | 5 | 24.6 | 1 | 168.3 | 2 | 168.5 | 8 | 0.4 | 631.54 | 602.06 | 139453 | 135291.72 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:40:00 | Operating | 1346.2 | -8.4 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -11.295 | 24.9 | 6 | 24.5 | 1 | 168.2 | 2 | 168.4 | 8 | 0.4 | 631.56 | 602.92 | 139453.02 | 135292.58 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:45:00 | Operating | 1346.2 | -7.3 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -9.904 | 24.7 | 6 | 24.3 | 1 | 168.2 | 2 | 168.4 | 8 | 0.5 | 631.58 | 603.48 | 139453.04 | 135293.14 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:50:00 | Operating | 1348.1 | 2.1 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | 2.826 | 24.6 | 8 | 24.1 | 1 | 168.4 | 2 | 168.6 | 8 | 0.5 | 631.58 | 603.82 | 139453.04 | 135293.5 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 21:55:00 | Operating | 1345.9 | -5.5 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -7.385 | 24.5 | 8 | 24 | 1 | 168.2 | 2 | 168.3 | 8 | 0.4 | 631.9 | 604.66 | 139453.36 | 135294.32 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:00:00 | Operating | 1343.9 | -17.6 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -23.629 | 24.4 | 8 | 23.9 | 1 | 167.9 | 2 | 168.1 | 8 | 0.4 | 632 | 605.42 | 139453.46 | 135295.08 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:05:00 | Operating | 1346.2 | -1.2 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -1.669 | 24.3 | 8 | 23.9 | 1 | 168.2 | 2 | 168.4 | 8 | 0.4 | 632 | 606.38 | 139453.46 | 135296.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:10:00 | Operating | 1348.1 | 6.9 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | 9.366 | 24.3 | 8 | 23.8 | 1 | 168.4 | 2 | 168.6 | 8 | 0.5 | 632.1 | 606.68 | 139453.56 | 135296.34 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:15:00 | Operating | 1348.2 | 0.6 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | 0.875 | 24.2 | 8 | 23.7 | 1 | 168.4 | 2 | 168.6 | 8 | 0.5 | 632.44 | 606.68 | 139453.9 | 135296.34 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:20:00 | Operating | 1351.6 | 8.9 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | 11.982 | 24.1 | 6 | 23.8 | 1 | 168.7 | 2 | 168.9 | 8 | 0.6 | 632.98 | 606.72 | 139454.44 | 135296.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:25:00 | Operating | 1355.5 | 23.5 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | 31.933 | 24.2 | 8 | 23.7 | 1 | 169.3 | 2 | 169.5 | 8 | 0.4 | 634.6 | 606.72 | 139456.14 | 135296.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:30:00 | Operating | 1362.6 | 49.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 67.525 | 24.1 | 6 | 23.7 | 1 | 170.2 | 2 | 170.4 | 8 | 0.3 | 637.7 | 606.72 | 139459.34 | 135296.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:35:00 | Operating | 1357.1 | 11 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 15.017 | 24.1 | 8 | 23.7 | 1 | 169.6 | 2 | 169.7 | 8 | 0.4 | 639.82 | 606.72 | 139461.28 | 135296.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:40:00 | Operating | 1356.7 | 16.6 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 22.616 | 24.2 | 8 | 23.7 | 1 | 169.5 | 2 | 169.6 | 8 | 0.3 | 640.14 | 607.12 | 139461.68 | 135296.78 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:45:00 | Operating | 1361.1 | 27.6 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 37.636 | 24.1 | 6 | 23.7 | 1 | 170 | 2 | 170.2 | 8 | 0.4 | 642.2 | 607.12 | 139463.66 | 135296.78 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:50:00 | Operating | 1363.2 | 19 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 25.971 | 24.2 | 8 | 23.8 | 1 | 170.3 | 2 | 170.4 | 8 | 0.4 | 645.72 | 607.12 | 139467.18 | 135296.78 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 22:55:00 | Operating | 1357.3 | -4.1 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -5.571 | 24.1 | 5 | 23.7 | 3 | 169.6 | 2 | 169.7 | 8 | 0.4 | 646.34 | 607.2 | 139467.8 | 135296.86 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:00:00 | Operating | 1353.5 | -7.8 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -10.602 | 24.1 | 6 | 23.7 | 1 | 169.1 | 2 | 169.3 | 8 | 0.4 | 646.34 | 608.4 | 139467.8 | 135298.06 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:05:00 | Operating | 1357.5 | 6.4 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 8.763 | 24.2 | 6 | 23.8 | 1 | 169.6 | 2 | 169.8 | 8 | 0.3 | 646.88 | 608.52 | 139468.38 | 135298.18 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:10:00 | Operating | 1357.1 | 0.1 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 0.668 | 24.2 | 8 | 23.8 | 1 | 169.6 | 2 | 169.7 | 8 | 0.4 | 647.76 | 608.64 | 139469.24 | 135298.3 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:15:00 | Operating | 1357 | 0.7 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 0.973 | 24.1 | 6 | 23.7 | 1 | 169.6 | 2 | 169.7 | 8 | 0.5 | 648.36 | 608.72 | 139469.82 | 135298.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:20:00 | Operating | 1359.7 | 10.4 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 14.217 | 24.2 | 8 | 23.8 | 1 | 169.9 | 2 | 170 | 8 | 0.4 | 649.1 | 608.72 | 139470.6 | 135298.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:25:00 | Operating | 1363.1 | 21.4 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 29.183 | 24.2 | 8 | 23.8 | 1 | 170.3 | 2 | 170.4 | 8 | 0.4 | 650.74 | 608.72 | 139472.2 | 135298.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:30:00 | Operating | 1364.9 | 23.2 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 31.755 | 24.1 | 6 | 23.8 | 1 | 170.5 | 2 | 170.7 | 8 | 0.4 | 652.82 | 608.72 | 139474.38 | 135298.38 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:35:00 | Operating | 1360.5 | -1.2 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -1.694 | 24.2 | 6 | 23.7 | 1 | 170 | 2 | 170.1 | 8 | 0.3 | 654.18 | 608.8 | 139475.64 | 135298.46 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:40:00 | Operating | 1360.6 | 2.3 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 3.141 | 24.1 | 6 | 23.8 | 1 | 170 | 2 | 170.1 | 8 | 0.3 | 654.54 | 609.1 | 139476.02 | 135298.76 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:45:00 | Operating | 1358.6 | -3 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -4.056 | 24.1 | 6 | 23.8 | 1 | 169.8 | 2 | 169.9 | 8 | 0.5 | 654.92 | 609.34 | 139476.38 | 135299 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:50:00 | Operating | 1362.5 | 11.5 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | 15.707 | 24.2 | 6 | 23.8 | 1 | 170.2 | 2 | 170.4 | 8 | 0.4 | 655.56 | 609.64 | 139477.08 | 135299.3 | 1.091
Amleang 136MW-01 | / | SACU-13/B13-ESS04/ESR-HV2510089570 | 2026-06-03 23:55:00 | Operating | 1365.1 | 15.5 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | 21.208 | 24.1 | 4 | 23.8 | 1 | 170.6 | 2 | 170.7 | 8 | 0.4 | 657.94 | 609.64 | 139479.4 | 135299.3 | 1.091