## 5 minutes
Time range: | 2026-06-03 00:00:00 - 2026-06-03 23:59:59
Export time: | 2026-06-04 00:34:28
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Device status | Voltage(V) | Current(A) | SOC(%) | SOH(%) | SOE(%) | DOD(%) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge Power(kW) | Module with the highest temperature(°C) | Position of the module with the highest temperature | Module with the lowest temperature(°C) | Position of the module with the lowest temperature | Lowest battery pack voltage(V) | Position where the lowest battery pack voltage was detected | Highest battery pack voltage(V) | Position where the highest battery pack voltage was detected | Average Temperature(°C) | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge(kWh) | Total discharge(kWh) | ISO insulation resistance(MΩ)
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:00:00 | Operating | 1340.8 | -23.4 | 17 | 99 | 15 | 90 | 627.314 | 110.702 | -31.062 | 24.4 | 8 | 24 | 1 | 167.1 | 6 | 167.6 | 2 | 0.3 | 0 | 0 | 140205.04 | 136033.16 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:05:00 | Operating | 1342.5 | -3.1 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -4.203 | 24.4 | 8 | 24.1 | 1 | 167.3 | 6 | 167.8 | 2 | 0.3 | 0 | 1.44 | 140205.04 | 136034.52 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:10:00 | Operating | 1343.5 | -14.2 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -19.031 | 24.5 | 8 | 24.1 | 1 | 167.5 | 6 | 167.9 | 2 | 0.3 | 0.58 | 2.1 | 140205.62 | 136035.14 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:15:00 | Operating | 1338.4 | -17.2 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -23.017 | 24.4 | 4 | 24.1 | 1 | 166.8 | 6 | 167.2 | 2 | 0.4 | 0.58 | 4.44 | 140205.62 | 136037.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:20:00 | Operating | 1337.9 | -32.7 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -43.754 | 24.5 | 8 | 24.2 | 1 | 166.9 | 6 | 167.3 | 2 | 0.4 | 0.58 | 6 | 140205.62 | 136039.12 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:25:00 | Operating | 1337.4 | -16.1 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -21.501 | 24.6 | 8 | 24.2 | 1 | 166.7 | 6 | 167.1 | 2 | 0.3 | 0.58 | 8.7 | 140205.62 | 136041.8 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:30:00 | Operating | 1340.8 | -10.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -13.537 | 24.6 | 8 | 24.2 | 1 | 167.2 | 6 | 167.6 | 2 | 0.3 | 0.66 | 9.46 | 140205.7 | 136042.54 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:35:00 | Operating | 1337.8 | -19.2 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -25.722 | 24.6 | 8 | 24.3 | 1 | 166.8 | 6 | 167.2 | 2 | 0.4 | 0.66 | 11.14 | 140205.7 | 136044.18 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:40:00 | Operating | 1338.2 | -8.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -11.898 | 24.6 | 8 | 24.3 | 1 | 166.8 | 6 | 167.2 | 2 | 0.3 | 0.66 | 12.96 | 140205.7 | 136046.04 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:45:00 | Operating | 1339.8 | -1 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | -1.396 | 24.6 | 8 | 24.3 | 1 | 167 | 6 | 167.4 | 2 | 0.4 | 0.78 | 14.24 | 140205.82 | 136047.28 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:50:00 | Operating | 1339.4 | -8.2 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | -10.982 | 24.7 | 8 | 24.3 | 1 | 167 | 6 | 167.4 | 2 | 0.4 | 0.78 | 14.82 | 140205.82 | 136047.86 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 00:55:00 | Operating | 1336.3 | -21.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -29.391 | 24.7 | 8 | 24.3 | 6 | 166.5 | 6 | 166.9 | 1 | 0.4 | 0.78 | 16.4 | 140205.82 | 136049.52 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 01:00:00 | Operating | 1336.3 | -24.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -32.546 | 24.7 | 8 | 24.4 | 1 | 166.5 | 6 | 166.9 | 1 | 0.3 | 0.8 | 17.52 | 140205.84 | 136050.64 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 01:05:00 | Operating | 1335.4 | -13.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -18.422 | 24.7 | 8 | 24.4 | 1 | 166.4 | 6 | 166.8 | 2 | 0.3 | 0.8 | 19.76 | 140205.84 | 136052.86 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 01:10:00 | Operating | 1336.6 | -13 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -17.313 | 24.7 | 8 | 24.5 | 1 | 166.5 | 6 | 166.9 | 2 | 0.4 | 0.82 | 21.06 | 140205.86 | 136054.1 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 01:15:00 | Operating | 1333.6 | -23.1 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -30.746 | 24.8 | 8 | 24.5 | 1 | 166.2 | 6 | 166.7 | 2 | 0.3 | 0.82 | 22.52 | 140205.86 | 136055.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 01:20:00 | Operating | 1332.8 | -18.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -11.507 | 24.8 | 8 | 24.5 | 1 | 166.1 | 6 | 166.6 | 1 | 0.3 | 0.82 | 24.5 | 140205.86 | 136057.54 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 01:25:00 | Operating | 1337.7 | 4.3 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 5.715 | 24.9 | 8 | 24.5 | 1 | 166.7 | 6 | 167.2 | 1 | 0.4 | 0.94 | 25.16 | 140205.98 | 136058.2 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 01:35:00 | Operating | 1344.7 | 5.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 7.795 | 24.9 | 8 | 24.5 | 6 | 167.6 | 6 | 168 | 2 | 0.4 | 2.96 | 25.32 | 140208 | 136058.36 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 01:40:00 | Operating | 1346.6 | 11.8 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | 15.947 | 24.9 | 8 | 24.5 | 6 | 167.9 | 6 | 168.3 | 1 | 0.3 | 3.94 | 25.34 | 140209.04 | 136058.38 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 01:45:00 | Operating | 1352.2 | 17.2 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 23.231 | 24.9 | 8 | 24.5 | 6 | 168.6 | 6 | 169 | 1 | 0.4 | 6.24 | 25.34 | 140211.36 | 136058.38 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 01:50:00 | Operating | 1354.1 | 18.2 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 24.707 | 24.9 | 8 | 24.5 | 7 | 168.8 | 6 | 169.2 | 1 | 0.4 | 8.44 | 25.34 | 140213.48 | 136058.38 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 01:55:00 | Operating | 1350 | -3.1 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -4.193 | 24.8 | 3 | 24.6 | 1 | 168.3 | 6 | 168.7 | 1 | 0.4 | 9.22 | 25.34 | 140214.26 | 136058.4 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:00:00 | Operating | 1344.4 | -16.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -22.583 | 24.9 | 8 | 24.6 | 1 | 167.7 | 6 | 168 | 1 | 0.3 | 9.38 | 25.92 | 140214.42 | 136059.02 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:05:00 | Operating | 1344.7 | -2.2 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -2.971 | 24.9 | 8 | 24.6 | 1 | 167.7 | 6 | 168 | 1 | 0.3 | 9.4 | 27.02 | 140214.44 | 136060.06 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:10:00 | Operating | 1346 | 4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.436 | 24.9 | 8 | 24.6 | 1 | 167.8 | 6 | 168.2 | 1 | 0.3 | 10.18 | 27.24 | 140215.22 | 136060.32 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:15:00 | Operating | 1343.3 | -13.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -18.462 | 24.9 | 8 | 24.6 | 1 | 167.5 | 6 | 167.9 | 2 | 0.4 | 10.24 | 27.78 | 140215.28 | 136060.86 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:20:00 | Operating | 1344.3 | 5.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 7.628 | 24.9 | 8 | 24.6 | 1 | 167.6 | 6 | 167.9 | 1 | 0.3 | 10.26 | 28.7 | 140215.3 | 136061.74 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:25:00 | Operating | 1346 | -4.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -6.258 | 25 | 8 | 24.6 | 1 | 167.8 | 6 | 168.2 | 1 | 0.3 | 10.9 | 28.7 | 140215.94 | 136061.74 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:30:00 | Operating | 1344 | -3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -3.977 | 25 | 8 | 24.6 | 1 | 167.6 | 6 | 167.9 | 1 | 0.4 | 10.94 | 29.18 | 140215.98 | 136062.22 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:35:00 | Operating | 1345.2 | 4.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 6.014 | 24.9 | 3 | 24.7 | 1 | 167.7 | 6 | 168.1 | 1 | 0.3 | 11.02 | 29.54 | 140216.08 | 136062.58 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:40:00 | Operating | 1347.7 | 4.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 6.492 | 25 | 8 | 24.7 | 1 | 168 | 6 | 168.4 | 1 | 0.2 | 11.74 | 29.58 | 140216.78 | 136062.62 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:45:00 | Operating | 1346.5 | 2.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 3.659 | 24.9 | 3 | 24.7 | 1 | 167.9 | 6 | 168.2 | 1 | 0.3 | 11.92 | 29.82 | 140216.98 | 136062.86 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:50:00 | Operating | 1344.5 | -8.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -11.249 | 25 | 8 | 24.7 | 1 | 167.6 | 6 | 168 | 1 | 0.3 | 12.3 | 30.08 | 140217.34 | 136063.16 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 02:55:00 | Operating | 1345 | 6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 8.065 | 25 | 8 | 24.7 | 1 | 167.7 | 6 | 168.1 | 1 | 0.3 | 12.46 | 30.68 | 140217.5 | 136063.72 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:00:00 | Operating | 1347.2 | 8.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 11.943 | 25.1 | 8 | 24.7 | 1 | 168 | 6 | 168.3 | 1 | 0.3 | 12.8 | 30.94 | 140217.86 | 136063.98 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:05:00 | Operating | 1345.2 | -1.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -2.253 | 25.1 | 8 | 24.7 | 1 | 167.8 | 6 | 168.1 | 1 | 0.3 | 13.1 | 31.52 | 140218.16 | 136064.56 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:10:00 | Operating | 1343.5 | -4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -5.205 | 25 | 8 | 24.7 | 1 | 167.5 | 6 | 168 | 2 | 0.3 | 13.22 | 31.88 | 140218.26 | 136064.94 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:15:00 | Operating | 1342.8 | -3.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -4.533 | 25 | 8 | 24.7 | 1 | 167.4 | 6 | 167.8 | 2 | 0.3 | 13.26 | 32.54 | 140218.3 | 136065.58 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:20:00 | Operating | 1343.3 | 4.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 6.035 | 25 | 3 | 24.7 | 1 | 167.4 | 6 | 167.8 | 2 | 0.3 | 13.42 | 33.1 | 140218.46 | 136066.16 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:25:00 | Operating | 1353.9 | 23.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 31.795 | 25.1 | 8 | 24.7 | 1 | 168.8 | 6 | 169.2 | 1 | 0.4 | 15.82 | 33.12 | 140220.86 | 136066.16 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:30:00 | Operating | 1350 | 2.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 3.825 | 25.1 | 8 | 24.7 | 1 | 168.3 | 6 | 168.7 | 1 | 0.4 | 16.6 | 33.28 | 140221.64 | 136066.32 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:35:00 | Operating | 1349.2 | 1.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 2.4 | 25.1 | 8 | 24.7 | 1 | 168.2 | 6 | 168.6 | 1 | 0.3 | 17 | 33.38 | 140222.04 | 136066.42 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:40:00 | Operating | 1357.8 | 28.4 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | 38.436 | 25.1 | 8 | 24.8 | 1 | 169.3 | 6 | 169.6 | 1 | 0.2 | 19.1 | 33.38 | 140224.14 | 136066.42 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:45:00 | Operating | 1366.3 | 57.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 78.62 | 25.1 | 8 | 24.8 | 1 | 170.4 | 5 | 170.7 | 1 | 0.2 | 24.16 | 33.38 | 140229.2 | 136066.42 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:50:00 | Operating | 1370.8 | 57.8 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 79.196 | 25.1 | 8 | 24.8 | 1 | 170.9 | 6 | 171.3 | 1 | 0.3 | 31.54 | 33.38 | 140236.58 | 136066.42 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 03:55:00 | Operating | 1369.1 | 45.3 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 62.032 | 25.2 | 8 | 24.8 | 1 | 170.7 | 6 | 171.1 | 1 | 0.3 | 36.7 | 33.38 | 140241.88 | 136066.42 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:00:00 | Operating | 1375.6 | 61.6 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 84.685 | 25.2 | 8 | 24.9 | 1 | 171.5 | 6 | 171.8 | 1 | 0.3 | 43.34 | 33.38 | 140248.68 | 136066.42 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:05:00 | Operating | 1363.4 | -10.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -14.303 | 25.2 | 8 | 24.9 | 1 | 170 | 6 | 170.4 | 1 | 0.3 | 45.98 | 33.52 | 140251.02 | 136066.64 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:10:00 | Operating | 1354.6 | -35.8 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -48.539 | 25.2 | 8 | 24.9 | 1 | 168.9 | 5 | 169.3 | 1 | 0.3 | 45.98 | 35.98 | 140251.02 | 136069.16 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:15:00 | Operating | 1354.3 | -19.9 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -26.909 | 25.2 | 8 | 24.9 | 1 | 168.9 | 5 | 169.3 | 1 | 0.3 | 45.98 | 38.56 | 140251.02 | 136071.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:20:00 | Operating | 1351.7 | -18.4 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | -24.914 | 25.3 | 8 | 24.9 | 1 | 168.5 | 5 | 169 | 1 | 0.4 | 45.98 | 41.04 | 140251.02 | 136074.08 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:25:00 | Operating | 1344.5 | -42.6 | 17 | 99 | 15 | 90 | 627.314 | 110.702 | -57.369 | 25.3 | 8 | 25 | 1 | 167.7 | 5 | 168.1 | 1 | 0.2 | 45.98 | 44.26 | 140251.02 | 136077.46 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:30:00 | Operating | 1336.9 | -51.6 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -69.023 | 25.4 | 8 | 25.1 | 1 | 166.7 | 5 | 167.1 | 1 | 0.4 | 45.98 | 49.92 | 140251.02 | 136082.96 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:35:00 | Operating | 1333 | -60.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -80.978 | 25.4 | 8 | 25.1 | 1 | 166.4 | 6 | 166.7 | 4 | 0.3 | 45.98 | 54.82 | 140251.02 | 136088.06 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:40:00 | Operating | 1333.6 | -35.5 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | -47.326 | 25.4 | 3 | 25.2 | 1 | 166.3 | 6 | 166.7 | 2 | 0.2 | 45.98 | 59.5 | 140251.02 | 136092.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:45:00 | Operating | 1333.5 | -25.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -33.977 | 25.5 | 8 | 25.2 | 1 | 166.2 | 6 | 166.7 | 2 | 0.3 | 45.98 | 62.98 | 140251.02 | 136096.02 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:50:00 | Operating | 1334.3 | -13.1 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -17.409 | 25.6 | 8 | 25.3 | 1 | 166.3 | 6 | 166.8 | 2 | 0.2 | 45.98 | 66.02 | 140251.02 | 136099.1 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 04:55:00 | Operating | 1337.3 | -5.8 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -7.779 | 25.5 | 3 | 25.3 | 1 | 166.7 | 6 | 167.1 | 2 | 0.2 | 45.98 | 66.78 | 140251.02 | 136099.82 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:00:00 | Operating | 1339.6 | -0.8 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -1.042 | 25.5 | 3 | 25.3 | 1 | 167 | 6 | 167.4 | 2 | 0.2 | 46.26 | 67 | 140251.3 | 136100.04 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:05:00 | Operating | 1335.8 | -10.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -14.461 | 25.6 | 8 | 25.3 | 1 | 166.5 | 6 | 166.8 | 2 | 0.3 | 46.32 | 68.12 | 140251.36 | 136101.24 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:10:00 | Operating | 1328.1 | -43.4 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -57.629 | 25.5 | 3 | 25.3 | 1 | 165.6 | 6 | 166.1 | 2 | 0.3 | 46.32 | 70.66 | 140251.36 | 136103.7 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:15:00 | Operating | 1336.7 | 1.6 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 2.328 | 25.6 | 4 | 25.4 | 1 | 166.5 | 6 | 167 | 2 | 0.2 | 46.38 | 72.32 | 140251.42 | 136105.36 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:20:00 | Operating | 1336.4 | -7.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -10.385 | 25.6 | 3 | 25.4 | 1 | 166.5 | 6 | 166.9 | 2 | 0.2 | 46.38 | 72.74 | 140251.42 | 136105.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:25:00 | Operating | 1336.5 | -7.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -10.234 | 25.6 | 3 | 25.4 | 1 | 166.5 | 6 | 167 | 2 | 0.3 | 46.4 | 73.38 | 140251.44 | 136106.44 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:30:00 | Operating | 1333.9 | -9.5 | 13 | 99 | 11 | 90 | 656.835 | 81.181 | -12.629 | 25.6 | 2 | 25.4 | 1 | 166.2 | 6 | 166.7 | 2 | 0.2 | 46.4 | 74.44 | 140251.44 | 136107.48 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:35:00 | Operating | 1337.3 | 3.4 | 13 | 99 | 11 | 90 | 656.835 | 81.181 | 4.598 | 25.6 | 3 | 25.4 | 1 | 166.6 | 6 | 167.1 | 2 | 0.2 | 46.44 | 74.94 | 140251.5 | 136107.98 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:40:00 | Operating | 1336.1 | -6.5 | 13 | 99 | 11 | 90 | 656.835 | 81.181 | -8.695 | 25.6 | 3 | 25.4 | 1 | 166.4 | 6 | 166.9 | 2 | 0.2 | 46.5 | 75.38 | 140251.54 | 136108.42 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:45:00 | Operating | 1336.3 | -5.5 | 13 | 99 | 11 | 90 | 656.835 | 81.181 | -7.317 | 25.6 | 2 | 25.4 | 1 | 166.4 | 6 | 167 | 2 | 0.2 | 46.5 | 75.86 | 140251.54 | 136108.92 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:50:00 | Operating | 1336.4 | -2.1 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -2.763 | 25.7 | 8 | 25.4 | 1 | 166.4 | 6 | 167 | 2 | 0.3 | 46.5 | 76.54 | 140251.54 | 136109.58 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 05:55:00 | Operating | 1335.1 | -3.3 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -4.427 | 25.6 | 2 | 25.4 | 1 | 166.3 | 6 | 166.8 | 2 | 0.2 | 46.5 | 77.26 | 140251.54 | 136110.32 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:00:00 | Operating | 1334.9 | -3.8 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -5.008 | 25.7 | 3 | 25.4 | 5 | 166.3 | 6 | 166.8 | 2 | 0.3 | 46.54 | 77.92 | 140251.58 | 136110.96 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:05:00 | Operating | 1343.9 | 27.4 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | 36.81 | 25.7 | 8 | 25.5 | 1 | 167.5 | 6 | 168 | 1 | 0.2 | 47.58 | 78.2 | 140252.62 | 136111.24 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:10:00 | Operating | 1348.7 | 25.3 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 34.19 | 25.7 | 3 | 25.4 | 6 | 168 | 6 | 168.5 | 1 | 0.3 | 50.24 | 78.2 | 140255.28 | 136111.24 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:15:00 | Operating | 1353.8 | 24 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 32.536 | 25.7 | 3 | 25.4 | 7 | 168.7 | 6 | 169.2 | 1 | 0.3 | 54.04 | 78.2 | 140259.18 | 136111.24 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:20:00 | Operating | 1358.5 | 35.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 48.705 | 25.8 | 8 | 25.5 | 1 | 169.3 | 6 | 169.8 | 1 | 0.3 | 58.34 | 78.2 | 140263.38 | 136111.24 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:25:00 | Operating | 1354.8 | 15.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 20.893 | 25.7 | 4 | 25.5 | 1 | 168.9 | 6 | 169.3 | 1 | 0.2 | 60.52 | 78.2 | 140265.56 | 136111.24 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:30:00 | Operating | 1355.5 | 17.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 23.771 | 25.7 | 3 | 25.5 | 1 | 169 | 6 | 169.4 | 1 | 0.3 | 61.66 | 78.2 | 140266.7 | 136111.24 | 1.055
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:35:00 | Operating | 1359.6 | 30 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | 40.773 | 25.7 | 3 | 25.5 | 1 | 169.5 | 6 | 169.9 | 1 | 0.3 | 64.4 | 78.2 | 140269.56 | 136111.24 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:40:00 | Operating | 1360.6 | 27.3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 37.092 | 25.8 | 8 | 25.5 | 1 | 169.7 | 6 | 170 | 1 | 0.3 | 67.22 | 78.2 | 140272.26 | 136111.24 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:45:00 | Operating | 1364.2 | 33.2 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | 45.358 | 25.8 | 8 | 25.5 | 1 | 170.1 | 6 | 170.5 | 1 | 0.3 | 71.28 | 78.2 | 140276.32 | 136111.24 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:50:00 | Operating | 1363.7 | 25.5 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 34.837 | 25.8 | 8 | 25.5 | 1 | 170 | 6 | 170.4 | 1 | 0.3 | 74.2 | 78.2 | 140279.24 | 136111.24 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 06:55:00 | Operating | 1357.8 | -8.6 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -11.687 | 25.8 | 8 | 25.5 | 1 | 169.4 | 6 | 169.7 | 1 | 0.3 | 75.48 | 78.26 | 140280.52 | 136111.34 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:00:00 | Operating | 1352.8 | -23.6 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -31.928 | 25.8 | 8 | 25.5 | 1 | 168.7 | 6 | 169.1 | 1 | 0.3 | 75.54 | 79.1 | 140280.58 | 136112.14 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:05:00 | Operating | 1352.8 | -5.1 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -6.922 | 25.9 | 8 | 25.6 | 1 | 168.7 | 5 | 169.1 | 1 | 0.3 | 75.54 | 80.68 | 140280.58 | 136113.72 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:10:00 | Operating | 1351.1 | -0.5 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -0.606 | 25.9 | 8 | 25.6 | 1 | 168.5 | 5 | 168.9 | 1 | 0.2 | 75.54 | 82.24 | 140280.58 | 136115.28 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:15:00 | Operating | 1353 | -6.7 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -9.023 | 25.9 | 8 | 25.6 | 1 | 168.8 | 6 | 169.1 | 1 | 0.3 | 76.22 | 82.28 | 140281.26 | 136115.32 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:20:00 | Operating | 1352.4 | -8.8 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -11.945 | 25.9 | 8 | 25.6 | 1 | 168.6 | 6 | 169 | 1 | 0.3 | 76.5 | 82.52 | 140281.54 | 136115.56 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:25:00 | Operating | 1346.5 | -17.3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -23.326 | 25.9 | 8 | 25.6 | 1 | 167.9 | 5 | 168.3 | 1 | 0.3 | 76.5 | 84.38 | 140281.54 | 136117.5 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:30:00 | Operating | 1348.1 | -8.9 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -11.973 | 26 | 8 | 25.6 | 1 | 168.1 | 5 | 168.5 | 1 | 0.3 | 76.5 | 85.26 | 140281.54 | 136118.3 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:35:00 | Operating | 1345.4 | -16.6 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -22.208 | 26 | 8 | 25.6 | 1 | 167.8 | 5 | 168.2 | 1 | 0.4 | 76.8 | 86.32 | 140281.84 | 136119.44 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:40:00 | Operating | 1348.4 | 1.7 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 2.295 | 26 | 8 | 25.7 | 1 | 168.1 | 5 | 168.5 | 1 | 0.3 | 76.86 | 87.4 | 140281.9 | 136120.44 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:45:00 | Operating | 1351.1 | 5.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 6.933 | 26 | 8 | 25.7 | 1 | 168.5 | 6 | 168.9 | 1 | 0.2 | 77.5 | 87.48 | 140282.56 | 136120.52 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:50:00 | Operating | 1354.2 | 10.4 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 14.061 | 26 | 8 | 25.7 | 1 | 168.9 | 6 | 169.2 | 1 | 0.4 | 78.48 | 87.48 | 140283.52 | 136120.52 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 07:55:00 | Operating | 1352.4 | 2.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 3.409 | 26 | 8 | 25.7 | 1 | 168.6 | 6 | 169 | 1 | 0.4 | 78.92 | 87.52 | 140283.96 | 136120.56 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:00:00 | Operating | 1353.2 | 6.2 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 8.431 | 26.1 | 8 | 25.7 | 1 | 168.8 | 6 | 169.1 | 1 | 0.4 | 79.26 | 87.56 | 140284.3 | 136120.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:05:00 | Operating | 1353 | -2.1 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -2.84 | 26 | 3 | 25.7 | 1 | 168.7 | 6 | 169.1 | 1 | 0.3 | 79.9 | 87.56 | 140284.94 | 136120.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:10:00 | Operating | 1350 | -3.2 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -4.307 | 26.1 | 8 | 25.7 | 1 | 168.4 | 6 | 168.7 | 1 | 0.4 | 79.9 | 88.5 | 140284.94 | 136121.54 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:15:00 | Operating | 1351.4 | 4.3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 5.771 | 26.1 | 8 | 25.7 | 1 | 168.5 | 6 | 168.9 | 1 | 0.2 | 80.08 | 88.96 | 140285.14 | 136122 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:20:00 | Operating | 1349.1 | -0.4 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -0.477 | 26.1 | 8 | 25.7 | 1 | 168.2 | 6 | 168.6 | 1 | 0.3 | 80.14 | 89.64 | 140285.18 | 136122.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:25:00 | Operating | 1351.3 | 1.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 2.058 | 26.2 | 8 | 25.8 | 1 | 168.5 | 6 | 168.9 | 1 | 0.3 | 80.5 | 89.64 | 140285.54 | 136122.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:30:00 | Operating | 1356.5 | 18.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 25.118 | 26.1 | 8 | 25.8 | 1 | 169.1 | 6 | 169.5 | 1 | 0.3 | 81.72 | 89.64 | 140286.76 | 136122.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:35:00 | Operating | 1358.6 | 23.1 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | 31.439 | 26.2 | 8 | 25.8 | 1 | 169.4 | 6 | 169.7 | 1 | 0.3 | 82.88 | 89.64 | 140287.92 | 136122.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:40:00 | Operating | 1362.5 | 27.5 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 37.426 | 26.2 | 8 | 25.8 | 1 | 169.9 | 6 | 170.3 | 1 | 0.4 | 84.96 | 89.64 | 140290 | 136122.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:45:00 | Operating | 1361.6 | 14 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 19.111 | 26.2 | 8 | 25.8 | 1 | 169.7 | 6 | 170.1 | 1 | 0.4 | 87.12 | 89.64 | 140292.2 | 136122.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:50:00 | Operating | 1368.2 | 36.8 | 17 | 99 | 15 | 90 | 627.314 | 110.702 | 50.392 | 26.3 | 8 | 25.8 | 1 | 170.6 | 6 | 171 | 1 | 0.5 | 90.36 | 89.64 | 140295.58 | 136122.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 08:55:00 | Operating | 1371.1 | 39.5 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 54.207 | 26.3 | 8 | 25.9 | 1 | 170.9 | 6 | 171.3 | 1 | 0.4 | 94.72 | 89.64 | 140299.94 | 136122.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:00:00 | Operating | 1374.4 | 45.4 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 62.386 | 26.3 | 8 | 25.9 | 1 | 171.2 | 6 | 171.6 | 1 | 0.4 | 99.66 | 89.64 | 140304.7 | 136122.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:05:00 | Operating | 1373.7 | 35.1 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 48.186 | 26.3 | 8 | 25.9 | 1 | 171.2 | 6 | 171.5 | 1 | 0.4 | 104.94 | 89.64 | 140309.98 | 136122.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:10:00 | Operating | 1371.7 | 26 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 35.672 | 26.4 | 8 | 25.9 | 1 | 171 | 6 | 171.4 | 1 | 0.5 | 107.32 | 89.66 | 140312.46 | 136122.7 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:15:00 | Operating | 1372.3 | 31.3 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 42.958 | 26.5 | 8 | 25.9 | 1 | 171.1 | 6 | 171.4 | 1 | 0.4 | 109.5 | 89.66 | 140314.68 | 136122.7 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:20:00 | Operating | 1365.3 | -15.9 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -21.716 | 26.5 | 8 | 26 | 1 | 170.3 | 6 | 170.6 | 1 | 0.5 | 110.68 | 89.7 | 140315.72 | 136122.74 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:25:00 | Operating | 1371.9 | 43.6 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 59.874 | 26.5 | 8 | 26 | 1 | 171.1 | 6 | 171.4 | 1 | 0.5 | 111.94 | 92.06 | 140317.18 | 136125.1 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:30:00 | Operating | 1369.8 | 26.2 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 35.875 | 26.5 | 8 | 26 | 1 | 170.8 | 6 | 171.1 | 1 | 0.5 | 113.4 | 92.56 | 140318.44 | 136125.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:35:00 | Operating | 1375.2 | 43.5 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 59.829 | 26.6 | 8 | 26.1 | 1 | 171.4 | 6 | 171.7 | 4 | 0.5 | 118.4 | 92.56 | 140323.44 | 136125.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:40:00 | Operating | 1381 | 52.5 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | 72.558 | 26.6 | 8 | 26.1 | 1 | 172.2 | 6 | 172.5 | 1 | 0.5 | 126.7 | 92.56 | 140331.96 | 136125.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:45:00 | Operating | 1378.9 | 49.7 | 22 | 99 | 21 | 90 | 583.033 | 154.983 | 68.464 | 26.7 | 8 | 26.1 | 1 | 171.9 | 6 | 172.2 | 1 | 0.6 | 129.94 | 92.74 | 140334.98 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:50:00 | Operating | 1384.7 | 75.6 | 23 | 99 | 21 | 90 | 583.033 | 154.983 | 104.728 | 26.8 | 8 | 26.2 | 1 | 172.6 | 6 | 172.9 | 4 | 0.6 | 135.78 | 92.74 | 140340.82 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 09:55:00 | Operating | 1387.8 | 75.8 | 24 | 99 | 23 | 90 | 568.273 | 169.743 | 105.137 | 26.9 | 8 | 26.3 | 1 | 173.1 | 6 | 173.3 | 4 | 0.6 | 145.84 | 92.74 | 140350.88 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:00:00 | Operating | 1381.5 | 30.5 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | 42.193 | 26.9 | 8 | 26.3 | 1 | 172.3 | 6 | 172.5 | 2 | 0.5 | 150.92 | 92.74 | 140355.96 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:05:00 | Operating | 1381.2 | 26.9 | 25 | 99 | 24 | 90 | 560.893 | 177.124 | 37.12 | 26.9 | 8 | 26.3 | 1 | 172.3 | 6 | 172.5 | 1 | 0.6 | 155.1 | 92.74 | 140360.14 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:10:00 | Operating | 1378.1 | 7.1 | 26 | 99 | 24 | 90 | 560.893 | 177.124 | 9.784 | 26.9 | 8 | 26.3 | 1 | 172 | 6 | 172.1 | 4 | 0.7 | 157.36 | 92.74 | 140362.42 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:15:00 | Operating | 1382.1 | 36.7 | 26 | 99 | 25 | 90 | 553.512 | 184.504 | 50.705 | 26.9 | 8 | 26.3 | 1 | 172.5 | 6 | 172.6 | 1 | 0.6 | 160.08 | 92.74 | 140365.12 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:20:00 | Operating | 1387.6 | 62 | 27 | 99 | 26 | 90 | 546.132 | 191.884 | 86.092 | 27 | 8 | 26.4 | 1 | 173.1 | 6 | 173.2 | 1 | 0.6 | 166.46 | 92.74 | 140371.82 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:25:00 | Operating | 1384.2 | 42.1 | 27 | 99 | 26 | 90 | 546.132 | 191.884 | 58.205 | 27 | 8 | 26.4 | 1 | 172.7 | 6 | 172.8 | 1 | 0.7 | 170.2 | 92.74 | 140375.42 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:30:00 | Operating | 1386.1 | 50 | 28 | 99 | 27 | 90 | 538.752 | 199.264 | 69.306 | 27.1 | 8 | 26.4 | 1 | 172.9 | 6 | 173 | 1 | 0.7 | 175.52 | 92.74 | 140380.56 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:35:00 | Operating | 1388.2 | 57.9 | 29 | 99 | 28 | 90 | 531.372 | 206.644 | 80.365 | 27.2 | 8 | 26.5 | 1 | 173.2 | 6 | 173.3 | 8 | 0.7 | 182.24 | 92.74 | 140387.28 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:40:00 | Operating | 1383 | 26.7 | 30 | 99 | 29 | 90 | 523.992 | 214.025 | 36.958 | 27.2 | 8 | 26.5 | 1 | 172.6 | 6 | 172.7 | 8 | 0.7 | 186.2 | 92.74 | 140391.24 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:45:00 | Operating | 1388.4 | 63 | 30 | 99 | 29 | 90 | 523.992 | 214.025 | 87.51 | 27.3 | 8 | 26.6 | 1 | 173.3 | 6 | 173.3 | 8 | 0.6 | 191 | 92.74 | 140396.04 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:50:00 | Operating | 1388.9 | 63.7 | 31 | 99 | 30 | 90 | 516.612 | 221.405 | 88.692 | 27.4 | 8 | 26.7 | 1 | 173.3 | 4 | 173.4 | 8 | 0.7 | 198.2 | 92.74 | 140403.24 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 10:55:00 | Operating | 1386.8 | 49.2 | 32 | 99 | 31 | 90 | 509.231 | 228.785 | 68.211 | 27.5 | 8 | 26.8 | 1 | 173.1 | 7 | 173.1 | 8 | 0.7 | 204.14 | 92.74 | 140409.4 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:00:00 | Operating | 1393.8 | 102.2 | 33 | 99 | 32 | 90 | 501.851 | 236.165 | 142.382 | 27.7 | 8 | 26.9 | 1 | 173.9 | 7 | 174 | 6 | 0.8 | 212.32 | 92.74 | 140417.76 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:05:00 | Operating | 1394.3 | 101.5 | 35 | 99 | 34 | 90 | 487.091 | 250.925 | 141.484 | 28 | 8 | 27.2 | 1 | 174 | 7 | 174.1 | 6 | 0.8 | 225.52 | 92.74 | 140431 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:10:00 | Operating | 1401.5 | 169.3 | 37 | 99 | 36 | 90 | 472.331 | 265.686 | 237.276 | 28.3 | 8 | 27.5 | 1 | 174.8 | 7 | 174.9 | 6 | 0.8 | 238.72 | 92.74 | 140444.5 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:15:00 | Operating | 1398.9 | 141.6 | 40 | 99 | 38 | 90 | 457.57 | 280.446 | 198.1 | 28.9 | 8 | 28.1 | 1 | 174.7 | 2 | 174.6 | 1 | 0.8 | 258.94 | 92.74 | 140464.6 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:20:00 | Operating | 1393.4 | 98.2 | 41 | 99 | 40 | 90 | 442.81 | 295.206 | 136.868 | 29 | 8 | 28.3 | 1 | 173.9 | 7 | 173.9 | 1 | 0.8 | 272.2 | 92.74 | 140477.68 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:25:00 | Operating | 1395.1 | 114.7 | 43 | 99 | 41 | 90 | 435.43 | 302.587 | 160.029 | 29.1 | 8 | 28.3 | 1 | 174.1 | 7 | 174.1 | 6 | 0.8 | 283.8 | 92.74 | 140488.84 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:30:00 | Operating | 1399.5 | 147.2 | 45 | 99 | 44 | 90 | 413.289 | 324.727 | 206.016 | 29.3 | 8 | 28.5 | 1 | 174.5 | 7 | 174.6 | 1 | 0.8 | 299.76 | 92.74 | 140504.8 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:35:00 | Operating | 1403.5 | 176.3 | 48 | 99 | 46 | 90 | 398.529 | 339.487 | 247.357 | 29.6 | 8 | 28.8 | 1 | 175.1 | 7 | 175.2 | 1 | 0.9 | 319 | 92.74 | 140524.04 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:40:00 | Operating | 1404.3 | 172.3 | 51 | 99 | 49 | 90 | 376.388 | 361.628 | 242.031 | 30.1 | 8 | 29.2 | 1 | 175.2 | 7 | 175.3 | 1 | 0.9 | 339.42 | 92.74 | 140545.22 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:45:00 | Operating | 1388.6 | 48.1 | 52 | 99 | 51 | 90 | 361.628 | 376.388 | 66.76 | 30.1 | 8 | 29.2 | 1 | 173.3 | 5 | 173.4 | 1 | 0.9 | 351.5 | 92.74 | 140556.76 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:50:00 | Operating | 1392.7 | 87.5 | 53 | 99 | 52 | 90 | 354.248 | 383.768 | 121.786 | 29.9 | 8 | 28.9 | 1 | 173.8 | 7 | 173.9 | 1 | 0.9 | 357.1 | 92.74 | 140562.14 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 11:55:00 | Operating | 1402.3 | 155.8 | 55 | 99 | 54 | 90 | 339.487 | 398.529 | 218.511 | 29.9 | 8 | 29 | 1 | 174.8 | 3 | 175 | 4 | 0.9 | 370.1 | 92.74 | 140575.72 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:00:00 | Operating | 1402.9 | 133.6 | 57 | 99 | 56 | 90 | 324.727 | 413.289 | 187.368 | 30.3 | 8 | 29.4 | 1 | 175 | 7 | 175.2 | 1 | 0.9 | 389.38 | 92.74 | 140595 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:05:00 | Operating | 1401.9 | 123.1 | 59 | 99 | 58 | 90 | 309.967 | 428.05 | 172.529 | 30.4 | 8 | 29.5 | 1 | 174.9 | 7 | 175.1 | 1 | 1 | 403.06 | 92.74 | 140608.64 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:10:00 | Operating | 1402.9 | 118.1 | 61 | 99 | 60 | 90 | 295.206 | 442.81 | 165.713 | 30.4 | 8 | 29.5 | 1 | 175 | 7 | 175.2 | 1 | 0.9 | 416.38 | 92.74 | 140621.92 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:15:00 | Operating | 1400.9 | 92.8 | 63 | 99 | 61 | 90 | 287.826 | 450.19 | 130.016 | 30.5 | 8 | 29.4 | 1 | 174.8 | 7 | 175 | 1 | 0.9 | 428.02 | 92.74 | 140633.48 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:20:00 | Operating | 1410.9 | 162.9 | 64 | 99 | 63 | 90 | 273.066 | 464.95 | 229.729 | 30.4 | 8 | 29.5 | 1 | 176 | 7 | 176.1 | 1 | 1 | 439.44 | 92.74 | 140645.12 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:25:00 | Operating | 1408.1 | 120 | 67 | 99 | 66 | 90 | 250.925 | 487.091 | 169.018 | 30.7 | 8 | 29.7 | 1 | 175.7 | 6 | 175.8 | 1 | 1 | 457.2 | 92.74 | 140662.8 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:30:00 | Operating | 1409 | 131.3 | 68 | 99 | 68 | 90 | 236.165 | 501.851 | 185.025 | 30.6 | 8 | 29.6 | 1 | 175.8 | 7 | 175.9 | 1 | 1 | 470.42 | 92.74 | 140676.04 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:35:00 | Operating | 1406 | 91.4 | 70 | 99 | 70 | 90 | 221.405 | 516.612 | 128.499 | 30.7 | 8 | 29.6 | 1 | 175.5 | 6 | 175.5 | 1 | 1.1 | 486.32 | 92.74 | 140691.36 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:40:00 | Operating | 1399 | 40.4 | 72 | 99 | 71 | 90 | 214.025 | 523.992 | 56.557 | 30.4 | 8 | 29.4 | 1 | 174.7 | 6 | 174.7 | 1 | 1 | 494.4 | 92.74 | 140699.62 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:45:00 | Operating | 1403.6 | 86.3 | 72 | 99 | 71 | 90 | 214.025 | 523.992 | 121.138 | 30.2 | 8 | 29.2 | 1 | 175.2 | 6 | 175.2 | 1 | 1 | 498.08 | 92.74 | 140703.46 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:50:00 | Operating | 1403 | 61.5 | 73 | 99 | 73 | 90 | 199.264 | 538.752 | 86.317 | 30.1 | 8 | 29 | 1 | 175.1 | 6 | 175.2 | 1 | 1.1 | 508.34 | 92.74 | 140713.38 | 136125.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 12:55:00 | Operating | 1387.6 | -36.4 | 74 | 99 | 73 | 90 | 199.264 | 538.752 | -50.027 | 30 | 8 | 28.9 | 1 | 173.3 | 6 | 173.3 | 8 | 1.1 | 510.94 | 93.2 | 140715.98 | 136126.24 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:00:00 | Operating | 1391.4 | 1.3 | 74 | 99 | 73 | 90 | 199.264 | 538.752 | 1.799 | 29.7 | 8 | 28.6 | 1 | 173.7 | 6 | 173.8 | 8 | 1.1 | 511.44 | 94.04 | 140716.5 | 136127.08 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:05:00 | Operating | 1393.9 | 22.4 | 74 | 99 | 73 | 90 | 199.264 | 538.752 | 31.224 | 29.5 | 8 | 28.4 | 1 | 174 | 6 | 174.1 | 1 | 1.1 | 512 | 94.42 | 140717.14 | 136127.46 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:10:00 | Operating | 1415 | 134.3 | 75 | 99 | 74 | 90 | 191.884 | 546.132 | 189.95 | 29.4 | 8 | 28.3 | 1 | 176.6 | 7 | 176.6 | 1 | 1.1 | 520.84 | 94.42 | 140726.46 | 136127.46 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:15:00 | Operating | 1413.4 | 109.1 | 77 | 99 | 76 | 90 | 177.124 | 560.893 | 154.155 | 29.5 | 8 | 28.4 | 1 | 176.3 | 6 | 176.3 | 1 | 1.1 | 535.8 | 94.42 | 140741.34 | 136127.46 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:20:00 | Operating | 1406.7 | 72.5 | 79 | 99 | 78 | 90 | 162.363 | 575.653 | 102.044 | 29.4 | 8 | 28.3 | 1 | 175.6 | 6 | 175.6 | 1 | 1.1 | 546.92 | 94.42 | 140751.96 | 136127.46 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:25:00 | Operating | 1411.3 | 99.9 | 80 | 99 | 79 | 90 | 154.983 | 583.033 | 140.968 | 29.2 | 8 | 28.1 | 1 | 176.1 | 8 | 176.2 | 1 | 1.1 | 556.94 | 94.42 | 140762.42 | 136127.46 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:30:00 | Operating | 1408.7 | 81.8 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | 115.276 | 29.2 | 8 | 28.1 | 1 | 175.8 | 6 | 175.9 | 1 | 1.1 | 567.58 | 94.42 | 140772.62 | 136127.46 | 1.055
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:35:00 | Operating | 1403.4 | 43.9 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 61.538 | 29 | 8 | 27.9 | 1 | 175.2 | 6 | 175.3 | 1 | 1.1 | 576.84 | 94.42 | 140782.1 | 136127.46 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:40:00 | Operating | 1391.9 | 6.7 | 82 | 99 | 82 | 90 | 132.843 | 605.174 | 9.345 | 28.9 | 8 | 27.8 | 1 | 173.8 | 6 | 173.8 | 1 | 1.1 | 578.02 | 96.32 | 140783.06 | 136129.36 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:45:00 | Operating | 1394.9 | 15.1 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 21.017 | 28.7 | 8 | 27.4 | 1 | 174.1 | 6 | 174.2 | 1 | 1.1 | 579.26 | 96.32 | 140784.3 | 136129.36 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:50:00 | Operating | 1386.5 | -39 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -54.03 | 28.5 | 8 | 27.3 | 1 | 173.1 | 6 | 173.2 | 7 | 1.2 | 580.78 | 96.88 | 140785.82 | 136130.1 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 13:55:00 | Operating | 1386.2 | -16.9 | 82 | 99 | 82 | 90 | 132.843 | 605.174 | -23.406 | 28.3 | 8 | 27.1 | 1 | 173.1 | 6 | 173.1 | 8 | 1.2 | 580.78 | 99.92 | 140785.82 | 136132.96 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:00:00 | Operating | 1404.5 | 80.2 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | 112.606 | 28.1 | 8 | 26.9 | 1 | 175.2 | 6 | 175.3 | 1 | 1.1 | 582.88 | 101.22 | 140787.92 | 136134.26 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:05:00 | Operating | 1410.3 | 72.9 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | 102.856 | 28 | 8 | 26.8 | 1 | 176 | 6 | 176.1 | 1 | 1.2 | 591.76 | 101.22 | 140796.8 | 136134.26 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:10:00 | Operating | 1406 | 40.7 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | 57.2 | 27.8 | 8 | 26.7 | 1 | 175.5 | 6 | 175.6 | 1 | 1.2 | 600.44 | 101.22 | 140805.48 | 136134.26 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:15:00 | Operating | 1405.2 | 41.5 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | 58.299 | 27.7 | 8 | 26.6 | 1 | 175.4 | 6 | 175.5 | 1 | 1.2 | 604.82 | 101.22 | 140809.86 | 136134.26 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:20:00 | Operating | 1391 | -23.1 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -32.11 | 27.5 | 8 | 26.4 | 1 | 173.7 | 6 | 173.7 | 1 | 1.2 | 606.44 | 101.52 | 140811.48 | 136134.64 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:25:00 | Operating | 1393.5 | 16.5 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | 23.004 | 27.3 | 8 | 26.2 | 1 | 173.9 | 6 | 174 | 7 | 1.1 | 606.62 | 103.42 | 140811.66 | 136136.46 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:30:00 | Operating | 1396.2 | 4.8 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 6.715 | 27.1 | 8 | 25.9 | 1 | 174.3 | 6 | 174.4 | 1 | 1.1 | 608.84 | 103.42 | 140813.88 | 136136.46 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:35:00 | Operating | 1380.9 | -40.5 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | -55.971 | 26.8 | 8 | 25.8 | 1 | 172.4 | 6 | 172.5 | 8 | 1.2 | 609.02 | 106.6 | 140814.06 | 136139.84 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:40:00 | Operating | 1406.8 | 64.4 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 90.572 | 26.6 | 8 | 25.6 | 1 | 175.5 | 6 | 175.6 | 1 | 1.1 | 612.2 | 107.26 | 140817.52 | 136140.3 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:45:00 | Operating | 1407.7 | 37.5 | 86 | 99 | 86 | 90 | 103.322 | 634.694 | 52.445 | 26.5 | 8 | 25.5 | 1 | 175.7 | 6 | 175.8 | 1 | 1 | 618.84 | 107.26 | 140823.88 | 136140.3 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:50:00 | Operating | 1403.3 | 29 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 40.713 | 26.3 | 8 | 25.3 | 1 | 175.1 | 6 | 175.2 | 1 | 1.1 | 621.44 | 107.26 | 140826.48 | 136140.3 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 14:55:00 | Operating | 1392.3 | -12.5 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -17.345 | 26 | 8 | 25 | 1 | 173.8 | 6 | 173.9 | 1 | 1.1 | 623.12 | 107.82 | 140828.16 | 136140.86 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:00:00 | Operating | 1386.5 | -24.2 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -33.531 | 25.8 | 8 | 24.8 | 1 | 173.1 | 6 | 173.1 | 7 | 1 | 623.12 | 109.3 | 140828.16 | 136142.44 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:05:00 | Operating | 1394.2 | 16.6 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 23.179 | 25.6 | 8 | 24.6 | 1 | 174 | 6 | 174.1 | 1 | 1.1 | 623.6 | 109.92 | 140828.64 | 136142.96 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:10:00 | Operating | 1400.7 | 18.7 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 26.13 | 25.4 | 8 | 24.4 | 1 | 174.8 | 6 | 174.9 | 1 | 1.1 | 626.32 | 109.92 | 140831.36 | 136142.96 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:15:00 | Operating | 1397.1 | 4.1 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 5.794 | 25.2 | 8 | 24.1 | 1 | 174.4 | 6 | 174.5 | 1 | 1.1 | 627.94 | 109.92 | 140832.98 | 136142.96 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:20:00 | Operating | 1384.9 | -31 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -42.908 | 25 | 8 | 23.9 | 1 | 172.9 | 6 | 173 | 8 | 1 | 627.98 | 111.48 | 140833.02 | 136144.64 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:25:00 | Operating | 1379.4 | -38.6 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -53.22 | 24.8 | 8 | 23.8 | 1 | 172.2 | 6 | 172.3 | 8 | 1 | 627.98 | 116.04 | 140833.02 | 136149.2 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:30:00 | Operating | 1378.8 | -32.2 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -44.392 | 24.7 | 8 | 23.7 | 1 | 172.1 | 6 | 172.2 | 8 | 1 | 627.98 | 120.68 | 140833.02 | 136153.72 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:35:00 | Operating | 1380.9 | -23.5 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | -32.493 | 24.5 | 8 | 23.7 | 1 | 172.4 | 4 | 172.4 | 8 | 0.9 | 627.98 | 123.84 | 140833.02 | 136156.88 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:40:00 | Operating | 1388.4 | 11.6 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | 16.152 | 24.5 | 8 | 23.7 | 1 | 173.3 | 2 | 173.4 | 8 | 0.9 | 628.9 | 124.12 | 140833.94 | 136157.16 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:45:00 | Operating | 1391 | 20.5 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 28.449 | 24.5 | 8 | 23.7 | 1 | 173.6 | 2 | 173.7 | 8 | 0.8 | 629.7 | 124.12 | 140834.74 | 136157.16 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:50:00 | Operating | 1390.3 | 19.5 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 27.046 | 24.5 | 8 | 23.6 | 1 | 173.5 | 2 | 173.6 | 8 | 0.8 | 630.1 | 124.52 | 140835.14 | 136157.56 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 15:55:00 | Operating | 1383.5 | -25.6 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -35.386 | 24.5 | 8 | 23.7 | 1 | 172.7 | 4 | 172.8 | 8 | 0.9 | 630.54 | 125.38 | 140835.58 | 136158.54 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:00:00 | Operating | 1380 | -25.7 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | -35.51 | 24.4 | 8 | 23.7 | 1 | 172.3 | 4 | 172.3 | 8 | 0.9 | 630.54 | 129.78 | 140835.58 | 136162.82 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:05:00 | Operating | 1381.3 | -18.9 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | -26.161 | 24.4 | 8 | 23.7 | 1 | 172.4 | 6 | 172.5 | 8 | 0.9 | 630.54 | 132.36 | 140835.58 | 136165.48 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:10:00 | Operating | 1381.8 | -17.9 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -24.698 | 24.5 | 8 | 23.7 | 1 | 172.5 | 4 | 172.6 | 8 | 0.8 | 630.54 | 134.3 | 140835.58 | 136167.34 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:15:00 | Operating | 1382 | -17.4 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -24.005 | 24.4 | 8 | 23.6 | 1 | 172.5 | 6 | 172.6 | 8 | 0.8 | 630.54 | 135.92 | 140835.58 | 136169.02 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:20:00 | Operating | 1382.7 | -17.3 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -23.958 | 24.4 | 8 | 23.7 | 1 | 172.6 | 4 | 172.7 | 8 | 0.8 | 630.54 | 137.28 | 140835.58 | 136170.38 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:25:00 | Operating | 1382.5 | -15.4 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -21.238 | 24.5 | 8 | 23.7 | 1 | 172.7 | 4 | 172.7 | 8 | 0.8 | 630.54 | 139.18 | 140835.58 | 136172.26 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:30:00 | Operating | 1383.1 | -14.2 | 83 | 99 | 83 | 90 | 125.462 | 612.554 | -19.651 | 24.4 | 8 | 23.7 | 1 | 172.7 | 4 | 172.7 | 8 | 0.8 | 630.6 | 140.28 | 140835.64 | 136173.32 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:35:00 | Operating | 1387.6 | 14.3 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 19.896 | 24.5 | 8 | 23.7 | 1 | 173.2 | 2 | 173.2 | 3 | 0.8 | 630.74 | 141.3 | 140835.84 | 136174.34 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:40:00 | Operating | 1392.6 | 21 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | 29.207 | 24.4 | 8 | 23.8 | 1 | 173.8 | 2 | 173.8 | 6 | 0.7 | 633.02 | 141.3 | 140838.06 | 136174.34 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:45:00 | Operating | 1393.6 | 15.6 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | 21.732 | 24.5 | 8 | 23.8 | 1 | 173.9 | 2 | 174 | 8 | 0.7 | 634.84 | 141.3 | 140839.94 | 136174.34 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:50:00 | Operating | 1385.3 | -22.6 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -31.362 | 24.5 | 8 | 23.8 | 1 | 172.9 | 4 | 173 | 8 | 0.7 | 635.52 | 141.88 | 140840.56 | 136175 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 16:55:00 | Operating | 1382.9 | -16.7 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -23.069 | 24.5 | 8 | 23.9 | 1 | 172.8 | 2 | 172.8 | 8 | 0.7 | 635.54 | 144.52 | 140840.58 | 136177.56 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:00:00 | Operating | 1375.2 | -58.5 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -80.463 | 24.6 | 8 | 23.9 | 1 | 171.6 | 5 | 171.7 | 8 | 0.7 | 635.54 | 148.76 | 140840.58 | 136182.3 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:05:00 | Operating | 1384.9 | 12.3 | 82 | 99 | 82 | 90 | 132.843 | 605.174 | 16.994 | 24.6 | 8 | 23.9 | 1 | 172.9 | 6 | 172.9 | 8 | 0.7 | 635.62 | 152.56 | 140840.72 | 136185.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:10:00 | Operating | 1386 | 7.9 | 82 | 99 | 82 | 90 | 132.843 | 605.174 | 10.906 | 24.6 | 8 | 24 | 1 | 173 | 2 | 173 | 8 | 0.6 | 635.94 | 152.86 | 140840.98 | 136185.9 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:15:00 | Operating | 1380.1 | -30 | 82 | 99 | 82 | 90 | 132.843 | 605.174 | -41.392 | 24.6 | 8 | 24 | 1 | 172.3 | 6 | 172.3 | 8 | 0.6 | 636.14 | 154.74 | 140841.18 | 136187.9 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:20:00 | Operating | 1380.7 | -23.2 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -32.015 | 24.6 | 8 | 24 | 1 | 172.3 | 6 | 172.4 | 8 | 0.6 | 636.14 | 157.6 | 140841.18 | 136190.74 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:25:00 | Operating | 1380.6 | -23 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -31.957 | 24.6 | 8 | 24.1 | 1 | 172.3 | 6 | 172.4 | 8 | 0.7 | 636.14 | 160.32 | 140841.18 | 136193.36 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:30:00 | Operating | 1381.5 | -16.5 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -22.861 | 24.6 | 8 | 24.1 | 1 | 172.5 | 6 | 172.5 | 3 | 0.5 | 636.14 | 163.02 | 140841.18 | 136196.14 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:35:00 | Operating | 1383.6 | -7 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -9.708 | 24.6 | 8 | 24.1 | 1 | 172.7 | 6 | 172.8 | 8 | 0.6 | 636.14 | 164.42 | 140841.18 | 136197.46 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:40:00 | Operating | 1382.7 | -16.8 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -23.018 | 24.7 | 8 | 24.1 | 1 | 172.6 | 6 | 172.7 | 8 | 0.6 | 636.14 | 165.78 | 140841.18 | 136198.88 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:45:00 | Operating | 1376.5 | -44 | 80 | 99 | 79 | 90 | 154.983 | 583.033 | -60.624 | 24.7 | 8 | 24.2 | 1 | 171.8 | 6 | 171.8 | 1 | 0.5 | 636.14 | 170.26 | 140841.18 | 136203.52 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:50:00 | Operating | 1377 | -45.6 | 79 | 99 | 79 | 90 | 154.983 | 583.033 | -62.735 | 24.7 | 8 | 24.2 | 1 | 171.9 | 6 | 171.9 | 1 | 0.5 | 636.14 | 175.18 | 140841.18 | 136208.4 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 17:55:00 | Operating | 1377.8 | -36.2 | 79 | 99 | 78 | 90 | 162.363 | 575.653 | -49.935 | 24.8 | 8 | 24.3 | 1 | 172 | 6 | 172 | 1 | 0.5 | 636.14 | 180.88 | 140841.18 | 136213.92 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:00:00 | Operating | 1376.3 | -45.6 | 78 | 99 | 77 | 90 | 169.743 | 568.273 | -62.698 | 24.9 | 8 | 24.3 | 1 | 171.8 | 6 | 171.9 | 1 | 0.6 | 636.14 | 187.06 | 140841.18 | 136220.32 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:05:00 | Operating | 1377.7 | -40.3 | 77 | 99 | 77 | 90 | 169.743 | 568.273 | -55.516 | 24.9 | 8 | 24.4 | 1 | 172 | 6 | 172 | 1 | 0.5 | 636.14 | 191.42 | 140841.18 | 136224.62 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:10:00 | Operating | 1377.4 | -41.8 | 77 | 99 | 76 | 90 | 177.124 | 560.893 | -57.58 | 24.9 | 8 | 24.4 | 1 | 171.9 | 6 | 172 | 1 | 0.5 | 636.14 | 195.82 | 140841.18 | 136229.04 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:15:00 | Operating | 1375.6 | -55.8 | 76 | 99 | 75 | 90 | 184.504 | 553.512 | -76.767 | 25 | 8 | 24.5 | 1 | 171.7 | 6 | 171.8 | 1 | 0.4 | 636.14 | 201.3 | 140841.18 | 136234.58 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:20:00 | Operating | 1372.4 | -79.4 | 75 | 99 | 74 | 90 | 191.884 | 546.132 | -108.934 | 24.9 | 8 | 24.5 | 1 | 171.3 | 6 | 171.4 | 1 | 0.5 | 636.14 | 207.98 | 140841.18 | 136241.02 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:25:00 | Operating | 1368.9 | -93.6 | 73 | 99 | 72 | 90 | 206.644 | 531.372 | -128.164 | 25.1 | 8 | 24.6 | 1 | 171 | 6 | 171 | 1 | 0.5 | 636.14 | 217.9 | 140841.18 | 136251.34 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:30:00 | Operating | 1368 | -92.4 | 72 | 99 | 71 | 90 | 214.025 | 523.992 | -126.439 | 25.2 | 3 | 24.8 | 1 | 170.7 | 6 | 170.9 | 2 | 0.4 | 636.14 | 229.42 | 140841.18 | 136262.86 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:35:00 | Operating | 1366.7 | -96.2 | 70 | 99 | 69 | 90 | 228.785 | 509.231 | -131.478 | 25.4 | 8 | 24.9 | 1 | 170.5 | 6 | 170.8 | 2 | 0.5 | 636.14 | 239.98 | 140841.18 | 136273.02 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:40:00 | Operating | 1363 | -111.8 | 69 | 99 | 68 | 90 | 236.165 | 501.851 | -152.292 | 25.5 | 8 | 25.1 | 1 | 170 | 6 | 170.4 | 2 | 0.4 | 636.14 | 251.58 | 140841.18 | 136284.62 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:45:00 | Operating | 1360.1 | -104.6 | 67 | 99 | 66 | 90 | 250.925 | 487.091 | -142.281 | 25.6 | 8 | 25.2 | 1 | 169.7 | 6 | 170 | 2 | 0.4 | 636.14 | 263.14 | 140841.18 | 136296.62 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:50:00 | Operating | 1357.8 | -104.9 | 65 | 99 | 64 | 90 | 265.686 | 472.331 | -142.349 | 25.8 | 8 | 25.3 | 1 | 169.4 | 6 | 169.7 | 1 | 0.5 | 636.14 | 274.96 | 140841.18 | 136308.42 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 18:55:00 | Operating | 1354.1 | -128.2 | 64 | 99 | 63 | 90 | 273.066 | 464.95 | -173.582 | 25.8 | 8 | 25.4 | 1 | 169 | 6 | 169.2 | 2 | 0.4 | 636.14 | 286.96 | 140841.18 | 136320 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:00:00 | Operating | 1350.9 | -143.2 | 62 | 99 | 60 | 90 | 295.206 | 442.81 | -193.39 | 25.9 | 8 | 25.5 | 1 | 168.7 | 6 | 168.8 | 2 | 0.4 | 636.14 | 302.1 | 140841.18 | 136335.14 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:05:00 | Operating | 1349.6 | -149.4 | 59 | 99 | 57 | 90 | 317.347 | 420.669 | -201.236 | 26 | 8 | 25.6 | 1 | 168.5 | 6 | 168.6 | 2 | 0.4 | 636.14 | 317.82 | 140841.18 | 136350.86 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:10:00 | Operating | 1349.7 | -146.3 | 57 | 99 | 55 | 90 | 332.107 | 405.909 | -197.43 | 26.1 | 3 | 25.8 | 1 | 168.5 | 6 | 168.6 | 7 | 0.4 | 636.14 | 336.02 | 140841.18 | 136369.66 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:15:00 | Operating | 1347.8 | -162 | 54 | 99 | 53 | 90 | 346.868 | 391.149 | -218.389 | 26.2 | 3 | 25.8 | 1 | 168.3 | 6 | 168.4 | 7 | 0.4 | 636.14 | 353.12 | 140841.18 | 136386.82 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:20:00 | Operating | 1346.4 | -169.7 | 52 | 99 | 49 | 90 | 376.388 | 361.628 | -228.474 | 26.4 | 8 | 25.8 | 7 | 168.1 | 6 | 168.3 | 2 | 0.4 | 636.14 | 371.34 | 140841.18 | 136405.08 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:25:00 | Operating | 1343.8 | -187.4 | 49 | 99 | 46 | 90 | 398.529 | 339.487 | -251.789 | 26.5 | 3 | 26 | 5 | 167.8 | 6 | 168 | 7 | 0.5 | 636.14 | 391.14 | 140841.18 | 136424.9 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:30:00 | Operating | 1340 | -212.5 | 46 | 99 | 43 | 90 | 420.669 | 317.347 | -284.717 | 26.7 | 8 | 26.2 | 5 | 167.3 | 6 | 167.5 | 7 | 0.5 | 636.14 | 414.38 | 140841.18 | 136447.42 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:35:00 | Operating | 1338.4 | -214.5 | 42 | 99 | 40 | 90 | 442.81 | 295.206 | -287.097 | 27.1 | 3 | 26.5 | 5 | 167.2 | 6 | 167.3 | 2 | 0.6 | 636.14 | 438.44 | 140841.18 | 136472.32 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:40:00 | Operating | 1337.2 | -210.4 | 39 | 99 | 37 | 90 | 464.95 | 273.066 | -281.26 | 27.3 | 3 | 26.7 | 5 | 167 | 6 | 167.2 | 2 | 0.6 | 636.14 | 461.54 | 140841.18 | 136495.44 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:45:00 | Operating | 1336.4 | -206.4 | 35 | 99 | 33 | 90 | 494.471 | 243.545 | -275.576 | 27.7 | 3 | 27.1 | 1 | 166.7 | 6 | 167 | 2 | 0.6 | 636.14 | 485.64 | 140841.18 | 136518.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:50:00 | Operating | 1328.6 | -239 | 32 | 99 | 30 | 90 | 516.612 | 221.405 | -319.016 | 28.3 | 3 | 27.5 | 7 | 165.9 | 6 | 166.2 | 2 | 0.8 | 636.14 | 511.74 | 140841.18 | 136544.78 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 19:55:00 | Operating | 1336.6 | -154.9 | 28 | 99 | 27 | 90 | 538.752 | 199.264 | -206.898 | 28.7 | 3 | 28 | 7 | 166.7 | 6 | 167 | 2 | 0.7 | 636.14 | 535.66 | 140841.18 | 136568.7 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:00:00 | Operating | 1343.3 | -90.5 | 26 | 99 | 26 | 90 | 546.132 | 191.884 | -121.574 | 28.6 | 3 | 28 | 1 | 167.7 | 6 | 167.9 | 2 | 0.6 | 636.14 | 549.06 | 140841.18 | 136582.1 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:05:00 | Operating | 1348.2 | -47.1 | 25 | 99 | 24 | 90 | 560.893 | 177.124 | -63.513 | 28.4 | 3 | 28 | 1 | 168.2 | 6 | 168.5 | 2 | 0.4 | 636.14 | 558.42 | 140841.18 | 136591.7 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:10:00 | Operating | 1358 | 2.3 | 25 | 99 | 24 | 90 | 560.893 | 177.124 | 3.128 | 28.3 | 3 | 27.8 | 1 | 169.4 | 6 | 169.6 | 1 | 0.5 | 636.4 | 560.02 | 140841.44 | 136593.1 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:15:00 | Operating | 1354 | -33.1 | 25 | 99 | 24 | 90 | 560.893 | 177.124 | -44.812 | 28.1 | 3 | 27.7 | 7 | 169 | 6 | 169.2 | 1 | 0.4 | 636.44 | 561.66 | 140841.48 | 136594.84 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:20:00 | Operating | 1349.5 | -50.4 | 24 | 99 | 23 | 90 | 568.273 | 169.743 | -68.054 | 28.1 | 3 | 27.7 | 7 | 168.4 | 6 | 168.6 | 1 | 0.4 | 636.44 | 566.94 | 140841.48 | 136600.16 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:25:00 | Operating | 1348.1 | -46.9 | 23 | 99 | 22 | 90 | 575.653 | 162.363 | -63.295 | 28.2 | 8 | 27.8 | 1 | 168.2 | 6 | 168.5 | 2 | 0.4 | 636.44 | 572.52 | 140841.48 | 136605.56 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:30:00 | Operating | 1347.1 | -51.2 | 23 | 99 | 21 | 90 | 583.033 | 154.983 | -68.979 | 28.2 | 3 | 27.8 | 1 | 168.1 | 6 | 168.3 | 2 | 0.4 | 636.44 | 577.6 | 140841.48 | 136610.64 | 1.055
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:35:00 | Operating | 1348.1 | -37.6 | 22 | 99 | 21 | 90 | 583.033 | 154.983 | -50.718 | 28.1 | 3 | 27.7 | 1 | 168.2 | 6 | 168.4 | 2 | 0.4 | 636.44 | 581.98 | 140841.48 | 136615.18 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:40:00 | Operating | 1347.3 | -35.7 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | -48.176 | 28 | 3 | 27.6 | 1 | 168.1 | 6 | 168.3 | 2 | 0.4 | 636.44 | 586.48 | 140841.48 | 136619.52 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:45:00 | Operating | 1347.1 | -33.9 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | -45.733 | 27.9 | 4 | 27.4 | 1 | 168.1 | 6 | 168.3 | 1 | 0.4 | 636.44 | 590.36 | 140841.48 | 136623.52 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:50:00 | Operating | 1348.1 | -23 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -31.014 | 27.7 | 4 | 27.2 | 1 | 168.2 | 6 | 168.4 | 1 | 0.5 | 636.44 | 593.92 | 140841.48 | 136626.96 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 20:55:00 | Operating | 1345.4 | -33.7 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -45.292 | 27.6 | 8 | 27 | 1 | 167.8 | 6 | 168.1 | 2 | 0.4 | 636.44 | 598.2 | 140841.48 | 136631.38 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:00:00 | Operating | 1345.7 | -28.6 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -38.435 | 27.4 | 4 | 26.9 | 1 | 167.9 | 6 | 168.2 | 2 | 0.5 | 636.44 | 601.14 | 140841.48 | 136634.18 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:05:00 | Operating | 1349.1 | -12.1 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -16.28 | 27.2 | 4 | 26.7 | 1 | 168.3 | 6 | 168.6 | 1 | 0.5 | 636.44 | 602.8 | 140841.48 | 136635.88 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:10:00 | Operating | 1352.3 | 7.5 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 10.087 | 26.9 | 4 | 26.5 | 1 | 168.7 | 6 | 169 | 1 | 0.4 | 636.46 | 603.52 | 140841.5 | 136636.56 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:15:00 | Operating | 1350.9 | -4.3 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -5.843 | 26.6 | 3 | 26.3 | 1 | 168.5 | 6 | 168.8 | 1 | 0.4 | 636.6 | 604.02 | 140841.64 | 136637.08 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:20:00 | Operating | 1349.2 | -14.5 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -19.533 | 26.5 | 4 | 26 | 1 | 168.3 | 6 | 168.6 | 1 | 0.5 | 636.76 | 604.62 | 140841.8 | 136637.72 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:25:00 | Operating | 1352.1 | 3.7 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 4.976 | 26.3 | 4 | 25.8 | 1 | 168.6 | 6 | 168.9 | 1 | 0.5 | 636.84 | 605.62 | 140841.88 | 136638.66 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:30:00 | Operating | 1353.6 | 5.4 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 7.306 | 26.1 | 8 | 25.6 | 1 | 168.8 | 6 | 169.1 | 1 | 0.5 | 637.32 | 605.62 | 140842.36 | 136638.66 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:35:00 | Operating | 1350.8 | -5.4 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | -7.289 | 25.9 | 4 | 25.4 | 1 | 168.5 | 6 | 168.8 | 1 | 0.5 | 637.34 | 606.5 | 140842.38 | 136639.54 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:40:00 | Operating | 1350.3 | -5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -6.749 | 25.6 | 4 | 25.2 | 1 | 168.4 | 6 | 168.7 | 1 | 0.5 | 637.34 | 607.4 | 140842.38 | 136640.44 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:45:00 | Operating | 1350.4 | -3.4 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -4.59 | 25.5 | 4 | 25 | 1 | 168.5 | 6 | 168.7 | 1 | 0.4 | 637.36 | 607.94 | 140842.4 | 136640.98 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:50:00 | Operating | 1351.7 | 2.6 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 3.51 | 25.4 | 4 | 24.9 | 1 | 168.6 | 6 | 168.9 | 1 | 0.4 | 637.38 | 608.28 | 140842.42 | 136641.32 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 21:55:00 | Operating | 1349.5 | -5.2 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -7.075 | 25.2 | 4 | 24.7 | 1 | 168.3 | 6 | 168.6 | 1 | 0.4 | 637.68 | 609.12 | 140842.72 | 136642.18 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:00:00 | Operating | 1347.7 | -17.8 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -24.022 | 25.1 | 4 | 24.6 | 1 | 168 | 6 | 168.4 | 1 | 0.5 | 637.8 | 609.88 | 140842.84 | 136642.92 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:05:00 | Operating | 1349.8 | -1.1 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -1.496 | 24.9 | 4 | 24.4 | 1 | 168.3 | 6 | 168.7 | 1 | 0.5 | 637.8 | 610.84 | 140842.84 | 136643.88 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:10:00 | Operating | 1351.8 | 6.8 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | 9.157 | 24.8 | 4 | 24.3 | 1 | 168.6 | 6 | 168.9 | 1 | 0.5 | 637.9 | 611.12 | 140842.94 | 136644.16 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:15:00 | Operating | 1351.9 | 0.8 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | 1.046 | 24.7 | 4 | 24.2 | 1 | 168.6 | 6 | 168.9 | 1 | 0.5 | 638.24 | 611.14 | 140843.28 | 136644.18 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:20:00 | Operating | 1354.2 | 8.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 11.575 | 24.5 | 4 | 24.1 | 1 | 168.9 | 6 | 169.2 | 1 | 0.6 | 638.76 | 611.18 | 140843.82 | 136644.22 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:25:00 | Operating | 1359.1 | 23.6 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 32.082 | 24.4 | 4 | 23.9 | 1 | 169.5 | 6 | 169.8 | 1 | 0.5 | 640.34 | 611.18 | 140845.48 | 136644.22 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:30:00 | Operating | 1366.1 | 49.2 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 67.341 | 24.3 | 4 | 23.8 | 1 | 170.3 | 6 | 170.6 | 1 | 0.5 | 643.54 | 611.18 | 140848.78 | 136644.22 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:35:00 | Operating | 1360.6 | 10.7 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 14.606 | 24.2 | 4 | 23.8 | 1 | 169.7 | 6 | 170 | 1 | 0.4 | 645.58 | 611.18 | 140850.62 | 136644.22 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:40:00 | Operating | 1359.6 | 10.3 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 14.066 | 24.2 | 4 | 23.7 | 1 | 169.6 | 6 | 169.9 | 1 | 0.4 | 645.92 | 611.56 | 140851.02 | 136644.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:45:00 | Operating | 1364.4 | 27.5 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 37.502 | 24.2 | 4 | 23.7 | 1 | 170.2 | 6 | 170.4 | 1 | 0.4 | 647.96 | 611.56 | 140853.12 | 136644.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:50:00 | Operating | 1366.4 | 19 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 25.975 | 24.2 | 8 | 23.7 | 1 | 170.4 | 5 | 170.7 | 1 | 0.5 | 651.5 | 611.56 | 140856.62 | 136644.6 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 22:55:00 | Operating | 1360.7 | -4.2 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -5.704 | 24.1 | 4 | 23.6 | 1 | 169.7 | 6 | 170 | 1 | 0.4 | 652.14 | 611.62 | 140857.18 | 136644.68 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:00:00 | Operating | 1356.6 | -7.8 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -10.64 | 24.1 | 4 | 23.6 | 1 | 169.2 | 6 | 169.5 | 1 | 0.4 | 652.14 | 612.82 | 140857.18 | 136645.86 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:05:00 | Operating | 1360.9 | 6.5 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 8.869 | 24.1 | 4 | 23.6 | 1 | 169.7 | 6 | 170 | 1 | 0.5 | 652.66 | 612.96 | 140857.74 | 136646 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:10:00 | Operating | 1360.3 | 0.6 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 0.792 | 24.2 | 8 | 23.7 | 1 | 169.7 | 6 | 169.9 | 1 | 0.5 | 653.56 | 613.08 | 140858.6 | 136646.12 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:15:00 | Operating | 1360.3 | 0.8 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 1.07 | 24.1 | 4 | 23.7 | 1 | 169.7 | 6 | 169.9 | 1 | 0.5 | 654.14 | 613.16 | 140859.18 | 136646.2 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:20:00 | Operating | 1362.7 | 10.3 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 14.086 | 24.1 | 8 | 23.7 | 1 | 170 | 6 | 170.2 | 1 | 0.4 | 654.92 | 613.16 | 140859.96 | 136646.2 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:25:00 | Operating | 1366.3 | 21.4 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 29.305 | 24.2 | 8 | 23.7 | 1 | 170.4 | 6 | 170.6 | 1 | 0.4 | 656.52 | 613.16 | 140861.56 | 136646.2 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:30:00 | Operating | 1368 | 23.1 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | 31.589 | 24.2 | 8 | 23.7 | 1 | 170.6 | 6 | 170.8 | 1 | 0.4 | 658.64 | 613.16 | 140863.78 | 136646.2 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:35:00 | Operating | 1363.5 | -1.3 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | -1.712 | 24.1 | 4 | 23.7 | 1 | 170.1 | 6 | 170.3 | 1 | 0.5 | 659.98 | 613.24 | 140865.02 | 136646.28 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:40:00 | Operating | 1363.6 | 2.3 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | 3.164 | 24.2 | 8 | 23.7 | 1 | 170.1 | 6 | 170.3 | 1 | 0.5 | 660.34 | 613.54 | 140865.38 | 136646.58 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:45:00 | Operating | 1361.5 | -3.1 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | -4.255 | 24.2 | 8 | 23.7 | 1 | 169.9 | 6 | 170.1 | 1 | 0.5 | 660.72 | 613.78 | 140865.76 | 136646.82 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:50:00 | Operating | 1365.4 | 11.6 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | 15.82 | 24.2 | 8 | 23.8 | 1 | 170.3 | 6 | 170.5 | 1 | 0.4 | 661.34 | 614.1 | 140866.46 | 136647.14 | 1.061
Amleang 136MW-01 | / | SACU-03/B03-ESS03/ESR-HV2510089684 | 2026-06-03 23:55:00 | Operating | 1368 | 15.5 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | 21.205 | 24.2 | 8 | 23.8 | 1 | 170.7 | 6 | 170.8 | 1 | 0.4 | 663.76 | 614.1 | 140868.8 | 136647.14 | 1.061