## 5 minutes
Time range: | 2026-06-03 00:00:00 - 2026-06-03 23:59:59
Export time: | 2026-06-04 00:34:28
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Device status | Voltage(V) | Current(A) | SOC(%) | SOH(%) | SOE(%) | DOD(%) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge Power(kW) | Module with the highest temperature(°C) | Position of the module with the highest temperature | Module with the lowest temperature(°C) | Position of the module with the lowest temperature | Lowest battery pack voltage(V) | Position where the lowest battery pack voltage was detected | Highest battery pack voltage(V) | Position where the highest battery pack voltage was detected | Average Temperature(°C) | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge(kWh) | Total discharge(kWh) | ISO insulation resistance(MΩ)
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:00:00 | Operating | 1335.2 | -23.3 | 17 | 99 | 15 | 90 | 627.314 | 110.702 | -31.077 | 24.7 | 2 | 24.2 | 1 | 167.1 | 7 | 167.2 | 5 | 0.5 | 0 | 0 | 138676.76 | 134303.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:05:00 | Operating | 1337.6 | -3.2 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -4.264 | 24.7 | 2 | 24.2 | 7 | 167.3 | 7 | 167.4 | 5 | 0.5 | 0 | 1.42 | 138676.76 | 134304.66 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:10:00 | Operating | 1337.2 | -20.9 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -27.907 | 24.7 | 2 | 24.2 | 7 | 167.4 | 7 | 167.5 | 5 | 0.5 | 0.58 | 2.08 | 138677.34 | 134305.26 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:15:00 | Operating | 1332.8 | -17.1 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -22.763 | 24.8 | 2 | 24.2 | 7 | 166.8 | 7 | 166.9 | 5 | 0.6 | 0.58 | 4.44 | 138677.34 | 134307.62 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:20:00 | Operating | 1331.8 | -22.5 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -29.979 | 24.8 | 2 | 24.3 | 7 | 166.6 | 7 | 166.7 | 5 | 0.5 | 0.58 | 6.54 | 138677.34 | 134309.72 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:25:00 | Operating | 1333 | -10.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -13.988 | 24.8 | 2 | 24.3 | 7 | 166.8 | 7 | 166.9 | 5 | 0.5 | 0.58 | 8.84 | 138677.34 | 134312.02 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:30:00 | Operating | 1334.2 | -20.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -27.709 | 24.8 | 2 | 24.3 | 7 | 166.9 | 7 | 167 | 5 | 0.5 | 0.66 | 9.5 | 138677.42 | 134312.74 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:35:00 | Operating | 1332.8 | -12.9 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -17.157 | 24.9 | 2 | 24.4 | 4 | 166.8 | 7 | 166.9 | 5 | 0.5 | 0.66 | 11.18 | 138677.42 | 134314.36 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:40:00 | Operating | 1333.6 | -2.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -3.67 | 24.9 | 3 | 24.4 | 4 | 166.8 | 7 | 166.9 | 5 | 0.5 | 0.66 | 12.96 | 138677.42 | 134316.14 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:45:00 | Operating | 1334.1 | -7.2 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -9.658 | 24.9 | 2 | 24.3 | 7 | 167 | 7 | 167.1 | 5 | 0.6 | 0.76 | 14.12 | 138677.52 | 134317.3 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:50:00 | Operating | 1334 | -8.2 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | -10.932 | 24.9 | 2 | 24.4 | 7 | 166.9 | 7 | 167 | 5 | 0.5 | 0.78 | 14.78 | 138677.54 | 134318 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 00:55:00 | Operating | 1330.2 | -14.1 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -18.812 | 24.9 | 8 | 24.5 | 4 | 166.4 | 7 | 166.5 | 5 | 0.4 | 0.78 | 16.58 | 138677.54 | 134319.76 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:00:00 | Operating | 1330.3 | -16.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -22.267 | 24.9 | 2 | 24.5 | 4 | 166.4 | 7 | 166.5 | 5 | 0.4 | 0.8 | 17.62 | 138677.56 | 134320.88 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:05:00 | Operating | 1329.1 | -13.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -17.741 | 25 | 3 | 24.4 | 7 | 166.3 | 7 | 166.4 | 5 | 0.6 | 0.8 | 19.78 | 138677.56 | 134322.96 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:10:00 | Operating | 1330.1 | -13.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -18.234 | 25 | 2 | 24.5 | 7 | 166.5 | 7 | 166.6 | 5 | 0.5 | 0.82 | 21.02 | 138677.58 | 134324.2 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:15:00 | Operating | 1327 | -22.5 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -29.887 | 25 | 2 | 24.6 | 4 | 166 | 7 | 166.1 | 5 | 0.4 | 0.82 | 22.56 | 138677.58 | 134325.84 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:20:00 | Operating | 1327.9 | -7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -9.255 | 25 | 2 | 24.5 | 7 | 166.2 | 7 | 166.3 | 5 | 0.5 | 0.82 | 24.5 | 138677.58 | 134327.68 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:25:00 | Operating | 1331.7 | -8.6 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -11.495 | 25.1 | 2 | 24.6 | 7 | 166.6 | 7 | 166.7 | 5 | 0.5 | 0.94 | 25.02 | 138677.7 | 134328.2 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:30:00 | Operating | 1338.8 | 14.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 19.698 | 25 | 2 | 24.6 | 7 | 167.5 | 4 | 167.6 | 5 | 0.4 | 1.88 | 25.18 | 138678.64 | 134328.36 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:35:00 | Operating | 1339.6 | 11.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 15.659 | 25 | 2 | 24.6 | 4 | 167.5 | 4 | 167.6 | 5 | 0.4 | 2.98 | 25.18 | 138679.76 | 134328.36 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:40:00 | Operating | 1341.4 | 18.3 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | 24.515 | 25.1 | 2 | 24.6 | 7 | 167.8 | 4 | 167.9 | 5 | 0.5 | 4.04 | 25.2 | 138680.8 | 134328.38 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:45:00 | Operating | 1346.5 | 16.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 22.826 | 25.1 | 2 | 24.6 | 7 | 168.4 | 4 | 168.6 | 5 | 0.5 | 6.24 | 25.2 | 138683.08 | 134328.38 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:50:00 | Operating | 1348.8 | 18.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 24.716 | 25.1 | 2 | 24.6 | 7 | 168.7 | 4 | 168.8 | 3 | 0.5 | 8.38 | 25.2 | 138685.14 | 134328.38 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 01:55:00 | Operating | 1344.5 | -3.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -4.484 | 25.1 | 2 | 24.6 | 7 | 168.2 | 1 | 168.3 | 5 | 0.5 | 9.16 | 25.2 | 138685.94 | 134328.4 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:00:00 | Operating | 1339.2 | -16.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -22.498 | 25.1 | 2 | 24.6 | 7 | 167.6 | 3 | 167.7 | 8 | 0.5 | 9.32 | 25.84 | 138686.08 | 134329.02 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:05:00 | Operating | 1339.5 | 3.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.24 | 25.2 | 2 | 24.7 | 1 | 167.6 | 7 | 167.7 | 5 | 0.5 | 9.34 | 26.86 | 138686.1 | 134330.06 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:10:00 | Operating | 1341.2 | 4.2 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.622 | 25.1 | 2 | 24.6 | 7 | 167.7 | 7 | 167.8 | 8 | 0.6 | 10.12 | 27.12 | 138686.88 | 134330.3 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:15:00 | Operating | 1337.7 | -13.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -18.018 | 25.2 | 8 | 24.6 | 7 | 167.4 | 7 | 167.5 | 5 | 0.4 | 10.18 | 27.62 | 138686.94 | 134330.86 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:20:00 | Operating | 1338.9 | 5.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 7.477 | 25.2 | 2 | 24.7 | 7 | 167.5 | 7 | 167.6 | 5 | 0.4 | 10.2 | 28.52 | 138686.96 | 134331.72 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:25:00 | Operating | 1340.3 | -4.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -6.374 | 25.2 | 2 | 24.7 | 7 | 167.7 | 7 | 167.8 | 5 | 0.5 | 10.82 | 28.54 | 138687.58 | 134331.74 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:30:00 | Operating | 1338.6 | -2.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -3.436 | 25.2 | 2 | 24.7 | 7 | 167.5 | 7 | 167.6 | 5 | 0.5 | 10.86 | 29.02 | 138687.62 | 134332.2 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:35:00 | Operating | 1339.7 | 4.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.955 | 25.1 | 2 | 24.7 | 7 | 167.6 | 7 | 167.7 | 5 | 0.4 | 10.96 | 29.36 | 138687.72 | 134332.54 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:40:00 | Operating | 1341.9 | 4.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 6.372 | 25.2 | 2 | 24.7 | 7 | 167.9 | 4 | 168 | 5 | 0.5 | 11.66 | 29.42 | 138688.42 | 134332.6 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:45:00 | Operating | 1340.8 | 2.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 3.631 | 25.2 | 2 | 24.7 | 7 | 167.8 | 7 | 167.9 | 5 | 0.4 | 11.84 | 29.64 | 138688.6 | 134332.82 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:50:00 | Operating | 1339.1 | -8.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -11.572 | 25.2 | 2 | 24.7 | 7 | 167.5 | 7 | 167.6 | 5 | 0.5 | 12.2 | 29.92 | 138688.96 | 134333.14 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 02:55:00 | Operating | 1339.9 | 6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 7.905 | 25.1 | 2 | 24.7 | 7 | 167.6 | 7 | 167.8 | 5 | 0.5 | 12.36 | 30.5 | 138689.12 | 134333.68 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:00:00 | Operating | 1341.6 | 8.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 11.334 | 25.2 | 2 | 24.7 | 7 | 167.9 | 7 | 168 | 5 | 0.5 | 12.72 | 30.76 | 138689.48 | 134333.94 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:05:00 | Operating | 1339.6 | -1.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -1.831 | 25.2 | 2 | 24.7 | 7 | 167.6 | 7 | 167.7 | 5 | 0.5 | 13 | 31.32 | 138689.78 | 134334.5 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:10:00 | Operating | 1337.9 | -4.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -5.828 | 25.2 | 2 | 24.7 | 7 | 167.4 | 7 | 167.5 | 5 | 0.4 | 13.12 | 31.7 | 138689.88 | 134334.9 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:15:00 | Operating | 1337.1 | -3.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -4.613 | 25.3 | 2 | 24.8 | 7 | 167.3 | 7 | 167.4 | 5 | 0.5 | 13.16 | 32.34 | 138689.92 | 134335.54 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:20:00 | Operating | 1337.7 | 4.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 6.175 | 25.2 | 2 | 24.8 | 7 | 167.4 | 7 | 167.5 | 5 | 0.4 | 13.3 | 32.94 | 138690.06 | 134336.12 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:25:00 | Operating | 1348.8 | 23.2 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 31.361 | 25.2 | 2 | 24.8 | 4 | 168.7 | 4 | 168.8 | 3 | 0.4 | 15.7 | 32.94 | 138692.46 | 134336.12 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:30:00 | Operating | 1344.5 | 2.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 3.879 | 25.2 | 2 | 24.7 | 7 | 168.2 | 4 | 168.3 | 5 | 0.5 | 16.48 | 33.1 | 138693.26 | 134336.28 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:35:00 | Operating | 1343.7 | 1.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 1.864 | 25.2 | 2 | 24.8 | 7 | 168.1 | 1 | 168.2 | 8 | 0.5 | 16.88 | 33.2 | 138693.64 | 134336.4 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:40:00 | Operating | 1352.3 | 28.6 | 15 | 99 | 13 | 90 | 642.075 | 95.942 | 38.688 | 25.2 | 2 | 24.8 | 7 | 169.1 | 4 | 169.3 | 3 | 0.4 | 18.98 | 33.22 | 138695.74 | 134336.4 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:45:00 | Operating | 1361.1 | 57.9 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 78.781 | 25.3 | 2 | 24.8 | 7 | 170.2 | 4 | 170.4 | 3 | 0.6 | 24.08 | 33.22 | 138700.84 | 134336.4 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:50:00 | Operating | 1365.2 | 58 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 79.173 | 25.3 | 2 | 24.8 | 7 | 170.7 | 4 | 170.9 | 3 | 0.4 | 31.22 | 33.22 | 138708.3 | 134336.4 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 03:55:00 | Operating | 1363.6 | 45 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 61.292 | 25.4 | 2 | 24.9 | 1 | 170.5 | 4 | 170.7 | 3 | 0.5 | 36.6 | 33.22 | 138713.36 | 134336.4 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:00:00 | Operating | 1369.9 | 61.8 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 84.667 | 25.4 | 2 | 24.9 | 7 | 171.4 | 4 | 171.5 | 3 | 0.5 | 43.32 | 33.22 | 138720.08 | 134336.4 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:05:00 | Operating | 1357.5 | -9.7 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -13.115 | 25.4 | 2 | 24.9 | 7 | 169.9 | 4 | 170 | 3 | 0.5 | 45.78 | 33.38 | 138722.54 | 134336.62 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:10:00 | Operating | 1349.3 | -35.7 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -48.249 | 25.4 | 2 | 24.9 | 7 | 168.7 | 4 | 169 | 3 | 0.5 | 45.78 | 35.84 | 138722.54 | 134339.02 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:15:00 | Operating | 1348.7 | -20.2 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -27.2 | 25.5 | 2 | 24.9 | 7 | 168.7 | 4 | 168.9 | 3 | 0.4 | 45.78 | 38.3 | 138722.54 | 134341.56 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:20:00 | Operating | 1345.8 | -18.3 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | -24.785 | 25.4 | 2 | 24.9 | 7 | 168.3 | 4 | 168.6 | 3 | 0.6 | 45.78 | 40.86 | 138722.54 | 134344.04 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:25:00 | Operating | 1338.7 | -42.4 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | -56.799 | 25.5 | 2 | 25 | 7 | 167.4 | 4 | 167.7 | 3 | 0.5 | 45.78 | 44.08 | 138722.54 | 134347.42 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:30:00 | Operating | 1331.1 | -51.4 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -68.486 | 25.6 | 2 | 25 | 7 | 166.6 | 7 | 166.7 | 3 | 0.4 | 45.78 | 49.52 | 138722.54 | 134352.9 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:35:00 | Operating | 1327.5 | -59.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -79.448 | 25.6 | 2 | 25.1 | 7 | 166.1 | 7 | 166.3 | 8 | 0.5 | 45.78 | 54.54 | 138722.54 | 134357.72 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:40:00 | Operating | 1328.2 | -34.7 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -46.081 | 25.7 | 2 | 25.2 | 7 | 166.2 | 3 | 166.3 | 5 | 0.5 | 45.78 | 59.14 | 138722.54 | 134362.44 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:45:00 | Operating | 1328 | -25.2 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -33.483 | 25.7 | 2 | 25.2 | 7 | 166.2 | 3 | 166.3 | 5 | 0.6 | 45.78 | 62.54 | 138722.54 | 134365.72 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:50:00 | Operating | 1328.6 | -12.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -17.141 | 25.8 | 2 | 25.3 | 7 | 166.2 | 7 | 166.3 | 5 | 0.4 | 45.78 | 65.56 | 138722.54 | 134368.74 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 04:55:00 | Operating | 1331.5 | -5.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -7.92 | 25.8 | 2 | 25.3 | 7 | 166.6 | 7 | 166.7 | 5 | 0.4 | 45.78 | 66.32 | 138722.54 | 134369.5 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:00:00 | Operating | 1334 | -0.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -1.063 | 25.7 | 2 | 25.3 | 7 | 166.9 | 7 | 167 | 5 | 0.5 | 46.04 | 66.54 | 138722.8 | 134369.72 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:05:00 | Operating | 1330 | -10.5 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -14.025 | 25.8 | 3 | 25.3 | 7 | 166.3 | 7 | 166.4 | 5 | 0.4 | 46.12 | 67.68 | 138722.88 | 134370.94 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:10:00 | Operating | 1322 | -42.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -56.53 | 25.8 | 2 | 25.3 | 7 | 165.4 | 7 | 165.5 | 5 | 0.5 | 46.12 | 70.16 | 138722.88 | 134373.48 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:15:00 | Operating | 1330 | -2.9 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -3.868 | 25.8 | 2 | 25.4 | 7 | 166.4 | 7 | 166.5 | 5 | 0.5 | 46.16 | 71.78 | 138722.94 | 134374.96 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:20:00 | Operating | 1329.8 | -7.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -10.393 | 25.9 | 2 | 25.4 | 7 | 166.4 | 7 | 166.5 | 5 | 0.6 | 46.18 | 72.18 | 138722.94 | 134375.36 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:25:00 | Operating | 1329.8 | -7.5 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -9.984 | 25.9 | 2 | 25.4 | 7 | 166.4 | 7 | 166.5 | 8 | 0.5 | 46.18 | 72.82 | 138722.94 | 134376.02 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:30:00 | Operating | 1328.4 | -6.4 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -8.537 | 25.9 | 2 | 25.4 | 7 | 166.2 | 7 | 166.3 | 5 | 0.4 | 46.18 | 73.8 | 138722.94 | 134377 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:35:00 | Operating | 1330.3 | -4.6 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -6.069 | 25.9 | 2 | 25.4 | 7 | 166.5 | 7 | 166.7 | 5 | 0.5 | 46.22 | 74.34 | 138723 | 134377.52 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:40:00 | Operating | 1329.2 | -10.2 | 13 | 99 | 11 | 90 | 656.835 | 81.181 | -13.496 | 25.9 | 2 | 25.4 | 7 | 166.4 | 7 | 166.5 | 5 | 0.5 | 46.28 | 74.72 | 138723.04 | 134377.9 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:45:00 | Operating | 1329.7 | -4.8 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -6.348 | 25.8 | 2 | 25.4 | 7 | 166.3 | 7 | 166.5 | 5 | 0.5 | 46.28 | 75.22 | 138723.04 | 134378.44 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:50:00 | Operating | 1329.4 | -2.8 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -3.764 | 25.9 | 2 | 25.4 | 7 | 166.3 | 7 | 166.4 | 5 | 0.4 | 46.28 | 75.94 | 138723.04 | 134379.12 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 05:55:00 | Operating | 1327.9 | -8.3 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -11.054 | 25.8 | 2 | 25.5 | 7 | 166.2 | 7 | 166.3 | 5 | 0.6 | 46.3 | 76.64 | 138723.06 | 134379.82 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:00:00 | Operating | 1328.3 | -3.9 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -5.204 | 25.9 | 2 | 25.4 | 7 | 166.2 | 7 | 166.3 | 5 | 0.4 | 46.34 | 77.28 | 138723.1 | 134380.48 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:05:00 | Operating | 1337.7 | 27.5 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | 36.769 | 25.9 | 2 | 25.4 | 7 | 167.4 | 4 | 167.4 | 5 | 0.5 | 47.16 | 77.6 | 138723.92 | 134380.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:10:00 | Operating | 1342.9 | 25.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 34.522 | 26 | 2 | 25.4 | 7 | 168 | 4 | 168.1 | 5 | 0.6 | 49.84 | 77.6 | 138726.6 | 134380.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:15:00 | Operating | 1348.3 | 27.3 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 36.85 | 25.9 | 2 | 25.5 | 6 | 168.6 | 4 | 168.8 | 6 | 0.4 | 53.6 | 77.6 | 138730.48 | 134380.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:20:00 | Operating | 1352.4 | 32.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 43.847 | 25.9 | 2 | 25.4 | 7 | 169.2 | 4 | 169.3 | 3 | 0.4 | 57.82 | 77.6 | 138734.72 | 134380.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:25:00 | Operating | 1348.2 | 7.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 10.165 | 26 | 2 | 25.5 | 7 | 168.7 | 4 | 168.8 | 6 | 0.5 | 60.18 | 77.6 | 138736.94 | 134380.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:30:00 | Operating | 1349.6 | 17.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 23.788 | 26 | 2 | 25.4 | 7 | 168.8 | 4 | 169 | 6 | 0.4 | 61.4 | 77.6 | 138738.22 | 134380.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:35:00 | Operating | 1353.9 | 24.7 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 33.425 | 26 | 2 | 25.5 | 6 | 169.3 | 4 | 169.5 | 3 | 0.4 | 64.12 | 77.6 | 138740.98 | 134380.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:40:00 | Operating | 1355.1 | 27.2 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 36.8 | 26 | 2 | 25.5 | 7 | 169.5 | 4 | 169.7 | 3 | 0.5 | 66.92 | 77.6 | 138743.68 | 134380.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:45:00 | Operating | 1358.9 | 29.3 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | 39.878 | 26 | 2 | 25.5 | 7 | 170 | 4 | 170.2 | 3 | 0.5 | 70.98 | 77.6 | 138747.74 | 134380.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:50:00 | Operating | 1358.3 | 25.5 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 34.696 | 26 | 2 | 25.5 | 7 | 169.9 | 4 | 170 | 3 | 0.5 | 73.86 | 77.6 | 138750.72 | 134380.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 06:55:00 | Operating | 1351.8 | -8.7 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -11.768 | 26 | 2 | 25.5 | 7 | 169.1 | 4 | 169.3 | 3 | 0.5 | 75.14 | 77.7 | 138751.9 | 134380.88 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:00:00 | Operating | 1346.9 | -23.5 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -31.614 | 26 | 2 | 25.5 | 7 | 168.5 | 4 | 168.7 | 3 | 0.6 | 75.22 | 78.48 | 138751.98 | 134381.76 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:05:00 | Operating | 1346.9 | -5.1 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -6.913 | 26 | 2 | 25.5 | 7 | 168.5 | 4 | 168.7 | 6 | 0.6 | 75.22 | 80.08 | 138751.98 | 134383.26 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:10:00 | Operating | 1345.5 | -3.8 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -5.098 | 26.1 | 2 | 25.6 | 7 | 168.3 | 4 | 168.5 | 6 | 0.6 | 75.22 | 81.6 | 138751.98 | 134384.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:15:00 | Operating | 1347.1 | -6.6 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -9.147 | 26 | 2 | 25.6 | 7 | 168.6 | 4 | 168.7 | 3 | 0.5 | 75.88 | 81.64 | 138752.64 | 134384.84 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:20:00 | Operating | 1346.5 | -8.9 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -11.945 | 26.1 | 3 | 25.5 | 7 | 168.5 | 4 | 168.6 | 3 | 0.5 | 76.14 | 81.9 | 138752.9 | 134385.1 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:25:00 | Operating | 1341 | -17.9 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -24.05 | 26.1 | 2 | 25.6 | 7 | 167.8 | 4 | 167.9 | 2 | 0.5 | 76.14 | 83.84 | 138752.9 | 134387.02 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:30:00 | Operating | 1342.3 | -9 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -12.085 | 26.1 | 3 | 25.6 | 7 | 168 | 4 | 168.1 | 6 | 0.5 | 76.14 | 84.66 | 138752.9 | 134387.84 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:35:00 | Operating | 1339.9 | -16.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -22.137 | 26.1 | 2 | 25.6 | 7 | 167.7 | 4 | 167.8 | 5 | 0.5 | 76.44 | 85.72 | 138753.2 | 134388.98 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:40:00 | Operating | 1342.9 | 1.6 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 2.153 | 26.1 | 2 | 25.6 | 7 | 168 | 4 | 168.1 | 5 | 0.5 | 76.52 | 86.78 | 138753.28 | 134389.96 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:45:00 | Operating | 1345.6 | 5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 6.752 | 26.1 | 2 | 25.6 | 7 | 168.4 | 4 | 168.5 | 6 | 0.5 | 77.14 | 86.86 | 138753.92 | 134390.04 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:50:00 | Operating | 1348.9 | 10.4 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 13.969 | 26.2 | 2 | 25.7 | 7 | 168.7 | 4 | 168.8 | 3 | 0.4 | 78.12 | 86.86 | 138754.88 | 134390.04 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 07:55:00 | Operating | 1346.6 | 2.4 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 3.279 | 26.1 | 2 | 25.6 | 7 | 168.5 | 4 | 168.6 | 6 | 0.5 | 78.54 | 86.9 | 138755.3 | 134390.08 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:00:00 | Operating | 1347.7 | 6.2 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 8.378 | 26.2 | 2 | 25.7 | 7 | 168.6 | 4 | 168.7 | 5 | 0.6 | 78.86 | 86.94 | 138755.64 | 134390.12 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:05:00 | Operating | 1346.8 | -6.4 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -8.596 | 26.2 | 3 | 25.7 | 7 | 168.7 | 4 | 168.7 | 6 | 0.5 | 79.5 | 86.94 | 138756.26 | 134390.14 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:10:00 | Operating | 1344.5 | -3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -4.019 | 26.2 | 2 | 25.7 | 7 | 168.2 | 4 | 168.3 | 5 | 0.5 | 79.5 | 87.9 | 138756.26 | 134391.08 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:15:00 | Operating | 1345.8 | 4.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 6.078 | 26.1 | 2 | 25.7 | 7 | 168.4 | 4 | 168.5 | 5 | 0.5 | 79.68 | 88.34 | 138756.46 | 134391.52 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:20:00 | Operating | 1343.5 | -0.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -0.129 | 26.3 | 2 | 25.7 | 7 | 168.1 | 4 | 168.2 | 5 | 0.5 | 79.74 | 89.04 | 138756.5 | 134392.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:25:00 | Operating | 1345.5 | 1.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 2.442 | 26.3 | 2 | 25.7 | 7 | 168.4 | 4 | 168.5 | 6 | 0.5 | 80.08 | 89.04 | 138756.86 | 134392.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:30:00 | Operating | 1350.4 | 13.9 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 18.807 | 26.2 | 2 | 25.7 | 7 | 169 | 4 | 169.1 | 3 | 0.5 | 81.26 | 89.04 | 138758.02 | 134392.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:35:00 | Operating | 1353 | 23.1 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | 31.196 | 26.3 | 2 | 25.7 | 7 | 169.2 | 4 | 169.4 | 3 | 0.5 | 82.4 | 89.04 | 138759.24 | 134392.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:40:00 | Operating | 1356.7 | 27.5 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 37.295 | 26.2 | 2 | 25.8 | 7 | 169.7 | 4 | 169.9 | 3 | 0.5 | 84.54 | 89.04 | 138761.3 | 134392.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:45:00 | Operating | 1355.7 | 13.9 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 18.901 | 26.3 | 2 | 25.8 | 7 | 169.6 | 4 | 169.7 | 3 | 0.6 | 86.68 | 89.04 | 138763.44 | 134392.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:50:00 | Operating | 1362.4 | 36.8 | 17 | 99 | 15 | 90 | 619.934 | 118.082 | 50.023 | 26.3 | 2 | 25.8 | 7 | 170.4 | 4 | 170.6 | 3 | 0.6 | 89.96 | 89.04 | 138766.72 | 134392.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 08:55:00 | Operating | 1365.3 | 39.6 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 54.03 | 26.3 | 3 | 25.8 | 1 | 170.8 | 4 | 170.9 | 3 | 0.6 | 94.26 | 89.04 | 138771.2 | 134392.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:00:00 | Operating | 1368.1 | 45.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 62.769 | 26.3 | 2 | 25.8 | 7 | 171.1 | 4 | 171.2 | 3 | 0.5 | 98.74 | 89.04 | 138775.9 | 134392.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:05:00 | Operating | 1367.8 | 34.9 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 47.732 | 26.5 | 8 | 25.8 | 7 | 171.1 | 4 | 171.2 | 3 | 0.6 | 104.38 | 89.04 | 138781.14 | 134392.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:10:00 | Operating | 1366.1 | 25.9 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 35.346 | 26.5 | 8 | 25.9 | 7 | 171 | 4 | 171.1 | 3 | 0.6 | 106.72 | 89.06 | 138783.58 | 134392.24 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:15:00 | Operating | 1367.1 | 31.1 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 42.54 | 26.4 | 8 | 25.9 | 7 | 171.1 | 4 | 171.2 | 3 | 0.7 | 108.88 | 89.06 | 138785.76 | 134392.24 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:20:00 | Operating | 1359.4 | -15.9 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -21.596 | 26.4 | 8 | 25.9 | 1 | 170.2 | 4 | 170.3 | 3 | 0.5 | 110.02 | 89.1 | 138786.78 | 134392.28 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:25:00 | Operating | 1366.6 | 43.6 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 59.581 | 26.5 | 8 | 25.9 | 7 | 171 | 4 | 171.1 | 3 | 0.6 | 111.36 | 91.44 | 138788.32 | 134394.62 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:30:00 | Operating | 1364.3 | 25.9 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 35.385 | 26.6 | 8 | 25.9 | 7 | 170.7 | 4 | 170.8 | 3 | 0.6 | 112.66 | 91.94 | 138789.54 | 134395.12 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:35:00 | Operating | 1369.4 | 43.6 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 59.818 | 26.6 | 8 | 26 | 1 | 171.4 | 1 | 171.4 | 6 | 0.6 | 117.6 | 91.94 | 138794.5 | 134395.12 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:40:00 | Operating | 1376 | 52.5 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | 72.318 | 26.7 | 8 | 26.1 | 1 | 172.2 | 1 | 172.2 | 5 | 0.5 | 126.16 | 91.94 | 138802.92 | 134395.12 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:45:00 | Operating | 1373.8 | 49.9 | 22 | 99 | 20 | 90 | 590.413 | 147.603 | 64.622 | 26.6 | 8 | 26 | 7 | 171.9 | 1 | 172 | 5 | 0.6 | 129.14 | 92.14 | 138806.1 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:50:00 | Operating | 1379.6 | 73.8 | 23 | 99 | 21 | 90 | 583.033 | 154.983 | 101.787 | 26.7 | 8 | 26.1 | 1 | 172.6 | 1 | 172.7 | 5 | 0.6 | 134.9 | 92.14 | 138811.66 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 09:55:00 | Operating | 1383.2 | 75.4 | 24 | 99 | 22 | 90 | 575.653 | 162.363 | 104.34 | 26.8 | 8 | 26.2 | 1 | 173 | 1 | 173.1 | 5 | 0.6 | 144.98 | 92.14 | 138821.74 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:00:00 | Operating | 1376.8 | 30.3 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | 41.77 | 26.8 | 8 | 26.2 | 7 | 172.3 | 3 | 172.4 | 5 | 0.6 | 150.12 | 92.14 | 138826.88 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:05:00 | Operating | 1376.8 | 26.6 | 25 | 99 | 24 | 90 | 560.893 | 177.124 | 36.625 | 26.9 | 8 | 26.2 | 7 | 172.3 | 3 | 172.4 | 5 | 0.6 | 154.26 | 92.14 | 138831.14 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:10:00 | Operating | 1373.6 | 7.3 | 26 | 99 | 24 | 90 | 560.893 | 177.124 | 10.051 | 26.9 | 8 | 26.3 | 1 | 172 | 3 | 172 | 8 | 0.7 | 156.5 | 92.14 | 138833.28 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:15:00 | Operating | 1378.1 | 36.6 | 26 | 99 | 24 | 90 | 560.893 | 177.124 | 50.507 | 26.9 | 8 | 26.2 | 7 | 172.5 | 3 | 172.5 | 6 | 0.6 | 159.22 | 92.14 | 138835.98 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:20:00 | Operating | 1383.6 | 61.7 | 27 | 99 | 25 | 90 | 553.512 | 184.504 | 85.394 | 27 | 8 | 26.3 | 7 | 173.1 | 3 | 173.2 | 5 | 0.6 | 165.78 | 92.14 | 138842.54 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:25:00 | Operating | 1380 | 41.7 | 27 | 99 | 26 | 90 | 546.132 | 191.884 | 57.565 | 27 | 8 | 26.3 | 7 | 172.7 | 3 | 172.8 | 5 | 0.7 | 169.38 | 92.14 | 138846.14 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:30:00 | Operating | 1382.1 | 50 | 28 | 99 | 26 | 90 | 546.132 | 191.884 | 69.078 | 27 | 8 | 26.3 | 7 | 173 | 3 | 173 | 5 | 0.6 | 174.44 | 92.14 | 138851.42 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:35:00 | Operating | 1384.2 | 57.6 | 29 | 99 | 27 | 90 | 538.752 | 199.264 | 79.797 | 27.1 | 8 | 26.4 | 7 | 173.2 | 3 | 173.3 | 5 | 0.7 | 181.1 | 92.14 | 138858.1 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:40:00 | Operating | 1378.9 | 26.4 | 29 | 99 | 28 | 90 | 531.372 | 206.644 | 36.397 | 27.1 | 8 | 26.4 | 7 | 172.6 | 3 | 172.7 | 6 | 0.7 | 185.12 | 92.14 | 138862 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:45:00 | Operating | 1384.6 | 63.3 | 30 | 99 | 29 | 90 | 523.992 | 214.025 | 87.713 | 27.1 | 8 | 26.4 | 7 | 173.3 | 3 | 173.3 | 2 | 0.8 | 190.04 | 92.14 | 138866.8 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:50:00 | Operating | 1385.1 | 63.6 | 31 | 99 | 30 | 90 | 516.612 | 221.405 | 87.985 | 27.2 | 8 | 26.5 | 7 | 173.3 | 3 | 173.4 | 2 | 0.8 | 197.26 | 92.14 | 138874.02 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 10:55:00 | Operating | 1383.4 | 49.2 | 32 | 99 | 30 | 90 | 516.612 | 221.405 | 68.091 | 27.3 | 8 | 26.6 | 7 | 173.1 | 3 | 173.2 | 2 | 0.6 | 203.02 | 92.14 | 138879.98 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:00:00 | Operating | 1390.2 | 102.1 | 33 | 99 | 32 | 90 | 501.851 | 236.165 | 142.025 | 27.6 | 8 | 26.7 | 7 | 174 | 8 | 174 | 7 | 0.8 | 210.74 | 92.14 | 138887.92 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:05:00 | Operating | 1390.8 | 101.6 | 35 | 99 | 33 | 90 | 494.471 | 243.545 | 141.416 | 27.8 | 8 | 27 | 7 | 174 | 8 | 174.1 | 2 | 0.9 | 224.28 | 92.14 | 138901.46 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:10:00 | Operating | 1398 | 167.9 | 37 | 99 | 35 | 90 | 479.711 | 258.306 | 234.735 | 28.2 | 8 | 27.4 | 1 | 174.9 | 8 | 175 | 7 | 0.8 | 238.14 | 92.14 | 138914.9 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:15:00 | Operating | 1395.1 | 133.7 | 40 | 99 | 38 | 90 | 457.57 | 280.446 | 186.516 | 28.7 | 8 | 28 | 1 | 174.5 | 8 | 174.6 | 2 | 0.8 | 257.62 | 92.14 | 138935.02 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:20:00 | Operating | 1389.6 | 98.4 | 41 | 99 | 40 | 90 | 442.81 | 295.206 | 136.874 | 29 | 8 | 28.2 | 1 | 173.9 | 8 | 174 | 2 | 0.8 | 270.76 | 92.14 | 138947.98 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:25:00 | Operating | 1391.8 | 119.4 | 43 | 99 | 41 | 90 | 435.43 | 302.587 | 166.268 | 29.1 | 8 | 28.2 | 7 | 174.1 | 8 | 174.2 | 2 | 0.9 | 282.24 | 92.14 | 138959.54 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:30:00 | Operating | 1395.3 | 146.8 | 45 | 99 | 43 | 90 | 420.669 | 317.347 | 204.86 | 29.3 | 8 | 28.4 | 7 | 174.6 | 8 | 174.6 | 6 | 1 | 298.32 | 92.14 | 138975.08 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:35:00 | Operating | 1399.5 | 176.1 | 48 | 99 | 46 | 90 | 398.529 | 339.487 | 246.597 | 29.8 | 8 | 28.7 | 7 | 175.1 | 8 | 175.2 | 7 | 1 | 317.42 | 92.14 | 138994.18 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:40:00 | Operating | 1400.1 | 172 | 51 | 99 | 49 | 90 | 376.388 | 361.628 | 241.019 | 30.1 | 8 | 29.1 | 4 | 175.2 | 8 | 175.3 | 6 | 1.1 | 337.62 | 92.14 | 139015.14 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:45:00 | Operating | 1384.5 | 47.9 | 52 | 99 | 51 | 90 | 361.628 | 376.388 | 66.393 | 30.2 | 8 | 29.2 | 4 | 173.3 | 8 | 173.4 | 6 | 1.1 | 349.94 | 92.14 | 139026.7 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:50:00 | Operating | 1388.6 | 87.1 | 53 | 99 | 51 | 90 | 361.628 | 376.388 | 120.993 | 30 | 8 | 28.9 | 7 | 173.8 | 8 | 173.8 | 2 | 1 | 355.18 | 92.14 | 139031.94 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 11:55:00 | Operating | 1398 | 154.7 | 55 | 99 | 53 | 90 | 346.868 | 391.149 | 216.315 | 30.2 | 8 | 29 | 4 | 174.7 | 8 | 174.8 | 6 | 1.1 | 368.48 | 92.14 | 139045.24 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:00:00 | Operating | 1398.4 | 133.3 | 57 | 99 | 56 | 90 | 324.727 | 413.289 | 186.527 | 30.5 | 8 | 29.3 | 4 | 175 | 8 | 175.1 | 5 | 1.2 | 387.66 | 92.14 | 139064.42 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:05:00 | Operating | 1397.6 | 122.9 | 59 | 99 | 58 | 90 | 309.967 | 428.05 | 171.742 | 30.7 | 8 | 29.4 | 7 | 174.9 | 8 | 175 | 5 | 1.3 | 401.2 | 92.14 | 139077.96 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:10:00 | Operating | 1398.2 | 120.8 | 61 | 99 | 59 | 90 | 295.206 | 442.81 | 168.967 | 30.7 | 8 | 29.5 | 4 | 175 | 4 | 175.1 | 5 | 1.2 | 414.46 | 92.14 | 139091.22 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:15:00 | Operating | 1395.9 | 92.5 | 63 | 99 | 61 | 90 | 287.826 | 450.19 | 129.176 | 30.8 | 8 | 29.5 | 4 | 174.7 | 4 | 174.8 | 5 | 1.3 | 425.98 | 92.14 | 139103.12 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:20:00 | Operating | 1406.2 | 162.4 | 64 | 99 | 63 | 90 | 273.066 | 464.95 | 228.373 | 30.7 | 8 | 29.5 | 7 | 175.9 | 4 | 176.1 | 5 | 1.3 | 437.38 | 92.14 | 139114.8 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:25:00 | Operating | 1403.8 | 120.1 | 67 | 99 | 65 | 90 | 258.306 | 479.711 | 168.639 | 31.1 | 8 | 29.8 | 1 | 175.7 | 8 | 175.8 | 5 | 1.3 | 454.94 | 92.14 | 139132.22 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:30:00 | Operating | 1402 | 102.3 | 68 | 99 | 67 | 90 | 243.545 | 494.471 | 143.52 | 31 | 8 | 29.7 | 4 | 175.5 | 8 | 175.5 | 3 | 1.4 | 467.02 | 92.14 | 139144.22 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:35:00 | Operating | 1403 | 95.1 | 71 | 99 | 69 | 90 | 228.785 | 509.231 | 133.388 | 31.1 | 8 | 29.8 | 4 | 175.6 | 8 | 175.7 | 3 | 1.4 | 482.5 | 92.14 | 139159.7 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:40:00 | Operating | 1396.3 | 50.2 | 72 | 99 | 70 | 90 | 221.405 | 516.612 | 70.086 | 31 | 8 | 29.6 | 4 | 174.8 | 8 | 174.8 | 2 | 1.3 | 491.36 | 92.14 | 139168.36 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:45:00 | Operating | 1397.5 | 68.7 | 72 | 99 | 71 | 90 | 214.025 | 523.992 | 95.994 | 30.8 | 8 | 29.4 | 4 | 174.9 | 8 | 175 | 3 | 1.3 | 495.06 | 92.14 | 139171.82 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:50:00 | Operating | 1400.2 | 66.2 | 74 | 99 | 72 | 90 | 206.644 | 531.372 | 92.711 | 30.6 | 8 | 29.4 | 1 | 175.3 | 8 | 175.3 | 3 | 1.3 | 504.94 | 92.14 | 139181.7 | 134395.32 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 12:55:00 | Operating | 1384.8 | -27.5 | 74 | 99 | 72 | 90 | 206.644 | 531.372 | -38.151 | 30.5 | 8 | 29.1 | 1 | 173.5 | 5 | 173.5 | 2 | 1.3 | 508.14 | 92.28 | 139184.9 | 134395.58 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:00:00 | Operating | 1387 | -2.8 | 74 | 99 | 72 | 90 | 206.644 | 531.372 | -3.839 | 30.2 | 8 | 28.9 | 1 | 173.7 | 8 | 173.7 | 2 | 1.4 | 508.62 | 93.44 | 139185.4 | 134396.62 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:05:00 | Operating | 1389.4 | 22.1 | 74 | 99 | 72 | 90 | 206.644 | 531.372 | 30.674 | 30 | 8 | 28.7 | 1 | 174 | 8 | 174 | 2 | 1.3 | 509.06 | 93.82 | 139185.82 | 134397 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:10:00 | Operating | 1410.8 | 133.4 | 75 | 99 | 74 | 90 | 191.884 | 546.132 | 188.158 | 29.8 | 8 | 28.5 | 4 | 176.5 | 1 | 176.6 | 3 | 1.4 | 517.14 | 93.82 | 139193.9 | 134397 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:15:00 | Operating | 1409 | 115.1 | 77 | 99 | 76 | 90 | 177.124 | 560.893 | 162.264 | 30 | 8 | 28.6 | 1 | 176.3 | 8 | 176.4 | 3 | 1.3 | 532.08 | 93.82 | 139208.84 | 134397 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:20:00 | Operating | 1402.9 | 72.3 | 79 | 99 | 77 | 90 | 169.743 | 568.273 | 101.412 | 29.8 | 8 | 28.5 | 1 | 175.6 | 8 | 175.6 | 2 | 1.3 | 543.32 | 93.82 | 139220.08 | 134397 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:25:00 | Operating | 1407.1 | 99 | 80 | 99 | 79 | 90 | 154.983 | 583.033 | 139.372 | 29.7 | 8 | 28.4 | 1 | 176.1 | 8 | 176.1 | 2 | 1.4 | 553.16 | 93.82 | 139229.92 | 134397 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:30:00 | Operating | 1404.8 | 81.6 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | 114.639 | 29.6 | 8 | 28.3 | 4 | 175.8 | 8 | 175.9 | 2 | 1.4 | 564.46 | 93.82 | 139241.22 | 134397 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:35:00 | Operating | 1399.4 | 43.6 | 83 | 99 | 81 | 90 | 140.223 | 597.793 | 61.061 | 29.6 | 8 | 28.2 | 4 | 175.2 | 8 | 175.2 | 6 | 1.3 | 573.54 | 93.82 | 139250.5 | 134397 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:40:00 | Operating | 1388 | 6.6 | 82 | 99 | 82 | 90 | 132.843 | 605.174 | 9.174 | 29.3 | 8 | 28 | 4 | 173.8 | 8 | 173.8 | 3 | 1.4 | 574.56 | 95.72 | 139251.34 | 134398.9 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:45:00 | Operating | 1390.8 | 15 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 20.866 | 29.1 | 8 | 27.7 | 4 | 174.1 | 8 | 174.2 | 3 | 1.3 | 575.82 | 95.72 | 139252.58 | 134398.9 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:50:00 | Operating | 1382.5 | -38.9 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -53.798 | 29 | 8 | 27.5 | 4 | 173.1 | 5 | 173.2 | 2 | 1.4 | 577.3 | 96.36 | 139254.06 | 134399.54 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 13:55:00 | Operating | 1382.6 | -16.9 | 82 | 99 | 82 | 90 | 132.843 | 605.174 | -23.429 | 28.8 | 8 | 27.3 | 4 | 173.1 | 5 | 173.1 | 2 | 1.4 | 577.3 | 99.28 | 139254.06 | 134402.54 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:00:00 | Operating | 1400.7 | 79.8 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | 111.803 | 28.5 | 8 | 27.1 | 4 | 175.3 | 8 | 175.4 | 3 | 1.4 | 579.46 | 100.64 | 139256.22 | 134403.82 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:05:00 | Operating | 1406.3 | 71.4 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | 100.358 | 28.4 | 8 | 27.1 | 1 | 175.9 | 8 | 176 | 3 | 1.5 | 588.28 | 100.64 | 139265.04 | 134403.82 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:10:00 | Operating | 1402.1 | 40.2 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | 56.442 | 28.3 | 8 | 26.9 | 1 | 175.5 | 8 | 175.5 | 2 | 1.4 | 596.82 | 100.64 | 139273.58 | 134403.82 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:15:00 | Operating | 1400.8 | 34.2 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | 47.891 | 28.1 | 8 | 26.8 | 1 | 175.4 | 8 | 175.4 | 2 | 1.5 | 601.16 | 100.64 | 139277.92 | 134403.82 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:20:00 | Operating | 1386.8 | -23.2 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -32.225 | 28 | 8 | 26.6 | 1 | 173.6 | 8 | 173.7 | 2 | 1.3 | 602.68 | 100.96 | 139279.44 | 134404.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:25:00 | Operating | 1389.5 | 16.9 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | 23.558 | 27.8 | 8 | 26.4 | 1 | 173.9 | 8 | 174 | 3 | 1.4 | 602.88 | 102.82 | 139279.64 | 134406 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:30:00 | Operating | 1392.2 | 4.5 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 6.28 | 27.5 | 8 | 26.1 | 1 | 174.3 | 8 | 174.3 | 3 | 1.4 | 605.06 | 102.82 | 139281.82 | 134406 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:35:00 | Operating | 1377.2 | -40.5 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | -55.841 | 27.3 | 8 | 25.9 | 4 | 172.4 | 7 | 172.5 | 4 | 1.4 | 605.24 | 106.04 | 139282 | 134409.4 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:40:00 | Operating | 1402.9 | 62.5 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 87.778 | 27.1 | 8 | 25.7 | 4 | 175.5 | 8 | 175.6 | 3 | 1.4 | 608.44 | 106.68 | 139285.48 | 134409.86 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:45:00 | Operating | 1403.6 | 36.9 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 51.76 | 26.8 | 8 | 25.6 | 1 | 175.7 | 8 | 175.7 | 3 | 1.2 | 614.98 | 106.68 | 139291.74 | 134409.86 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:50:00 | Operating | 1399.1 | 28.6 | 87 | 99 | 87 | 90 | 95.942 | 642.075 | 39.969 | 26.7 | 8 | 25.3 | 4 | 175.1 | 8 | 175.2 | 3 | 1.3 | 617.48 | 106.68 | 139294.36 | 134409.86 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 14:55:00 | Operating | 1388.2 | -12.5 | 87 | 99 | 87 | 90 | 95.942 | 642.075 | -17.292 | 26.4 | 8 | 25.1 | 1 | 173.8 | 8 | 173.8 | 1 | 1.3 | 619.18 | 107.26 | 139295.94 | 134410.44 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:00:00 | Operating | 1382.8 | -24 | 87 | 99 | 87 | 90 | 95.942 | 642.075 | -33.152 | 26.2 | 8 | 24.9 | 1 | 173.1 | 5 | 173.1 | 2 | 1.4 | 619.18 | 108.74 | 139295.94 | 134412.02 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:05:00 | Operating | 1390.4 | 16.5 | 87 | 99 | 87 | 90 | 95.942 | 642.075 | 22.992 | 25.9 | 8 | 24.6 | 4 | 174 | 8 | 174.1 | 3 | 1.4 | 619.68 | 109.32 | 139296.44 | 134412.5 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:10:00 | Operating | 1396.6 | 18.7 | 87 | 99 | 87 | 90 | 95.942 | 642.075 | 26.055 | 25.8 | 8 | 24.5 | 1 | 174.8 | 8 | 174.9 | 3 | 1.3 | 622.34 | 109.32 | 139299.18 | 134412.5 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:15:00 | Operating | 1392.8 | 4.1 | 87 | 99 | 87 | 90 | 95.942 | 642.075 | 5.734 | 25.6 | 8 | 24.3 | 4 | 174.3 | 8 | 174.4 | 3 | 1.2 | 623.94 | 109.32 | 139300.7 | 134412.5 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:20:00 | Operating | 1381.2 | -30.9 | 87 | 99 | 87 | 90 | 95.942 | 642.075 | -42.625 | 25.4 | 8 | 24.2 | 1 | 172.9 | 3 | 172.9 | 4 | 1.3 | 623.96 | 110.98 | 139300.72 | 134414.28 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:25:00 | Operating | 1376 | -38.7 | 87 | 99 | 87 | 90 | 95.942 | 642.075 | -53.246 | 25.4 | 8 | 24.2 | 1 | 172.2 | 3 | 172.3 | 4 | 1.2 | 623.96 | 115.52 | 139300.72 | 134418.7 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:30:00 | Operating | 1375.7 | -31.8 | 86 | 99 | 86 | 90 | 103.322 | 634.694 | -43.809 | 25.3 | 8 | 24.1 | 1 | 172.2 | 7 | 172.2 | 8 | 1.3 | 623.96 | 120.04 | 139300.72 | 134423.36 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:35:00 | Operating | 1377.7 | -23.2 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | -31.922 | 25.3 | 8 | 24.2 | 1 | 172.4 | 7 | 172.5 | 4 | 1.1 | 623.96 | 123.28 | 139300.72 | 134426.46 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:40:00 | Operating | 1384.9 | 11.4 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 15.74 | 25.3 | 8 | 24.1 | 4 | 173.4 | 7 | 173.4 | 4 | 1.2 | 624.86 | 123.54 | 139301.62 | 134426.72 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:45:00 | Operating | 1387.8 | 19.7 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 27.407 | 25.3 | 8 | 24.2 | 1 | 173.7 | 7 | 173.7 | 4 | 1.2 | 625.72 | 123.54 | 139302.48 | 134426.72 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:50:00 | Operating | 1387.1 | 29.6 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | 40.362 | 25.3 | 8 | 24.2 | 1 | 173.6 | 7 | 173.6 | 2 | 1 | 626.04 | 123.94 | 139302.84 | 134427.12 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 15:55:00 | Operating | 1379.9 | -25.5 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -35.204 | 25.2 | 8 | 24.1 | 1 | 172.7 | 3 | 172.8 | 4 | 1.2 | 626.5 | 124.84 | 139303.26 | 134428.02 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:00:00 | Operating | 1376.6 | -25.9 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | -35.728 | 25.2 | 8 | 24.1 | 4 | 172.3 | 3 | 172.3 | 2 | 1.1 | 626.5 | 129.12 | 139303.26 | 134432.4 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:05:00 | Operating | 1378.1 | -19.3 | 85 | 99 | 85 | 90 | 110.702 | 627.314 | -26.568 | 25.2 | 8 | 24.2 | 1 | 172.5 | 7 | 172.5 | 2 | 1 | 626.5 | 131.82 | 139303.26 | 134435 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:10:00 | Operating | 1378.5 | -17.6 | 84 | 99 | 84 | 90 | 118.082 | 619.934 | -24.27 | 25.1 | 8 | 24.1 | 4 | 172.6 | 7 | 172.6 | 4 | 1 | 626.5 | 133.78 | 139303.26 | 134436.96 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:15:00 | Operating | 1378.5 | -17.5 | 84 | 99 | 84 | 90 | 118.082 | 619.934 | -24.168 | 25.1 | 8 | 24.1 | 1 | 172.6 | 5 | 172.6 | 2 | 1 | 626.5 | 135.42 | 139303.26 | 134438.66 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:20:00 | Operating | 1379.1 | -17.4 | 84 | 99 | 84 | 90 | 118.082 | 619.934 | -23.966 | 25.1 | 8 | 24.2 | 1 | 172.7 | 5 | 172.7 | 2 | 0.9 | 626.5 | 136.78 | 139303.26 | 134440.02 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:25:00 | Operating | 1379 | -15.5 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -21.317 | 25.1 | 8 | 24.2 | 1 | 172.6 | 7 | 172.7 | 2 | 0.9 | 626.5 | 138.64 | 139303.26 | 134441.86 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:30:00 | Operating | 1379.6 | -14.2 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -19.579 | 25.1 | 8 | 24.1 | 4 | 172.7 | 7 | 172.7 | 4 | 1 | 626.54 | 139.76 | 139303.3 | 134443 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:35:00 | Operating | 1384.1 | 14.4 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 19.918 | 25.1 | 8 | 24.2 | 1 | 173.2 | 8 | 173.3 | 4 | 0.9 | 626.74 | 140.78 | 139303.5 | 134443.96 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:40:00 | Operating | 1388.5 | 13.9 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | 19.371 | 25.1 | 8 | 24.2 | 1 | 173.9 | 1 | 173.9 | 3 | 0.9 | 628.92 | 140.78 | 139305.68 | 134443.96 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:45:00 | Operating | 1390.1 | 15.5 | 84 | 99 | 84 | 90 | 118.082 | 619.934 | 21.566 | 25.1 | 8 | 24.3 | 1 | 174 | 1 | 174 | 3 | 0.9 | 630.8 | 140.78 | 139307.56 | 134443.96 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:50:00 | Operating | 1381.7 | -22.8 | 84 | 99 | 84 | 90 | 118.082 | 619.934 | -31.452 | 25.1 | 8 | 24.2 | 1 | 173 | 7 | 173 | 4 | 0.8 | 631.4 | 141.42 | 139308.16 | 134444.6 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 16:55:00 | Operating | 1379.5 | -16.9 | 84 | 99 | 83 | 90 | 132.843 | 605.174 | -23.273 | 25.1 | 8 | 24.3 | 1 | 172.7 | 7 | 172.7 | 4 | 0.8 | 631.42 | 144 | 139308.18 | 134447.2 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:00:00 | Operating | 1371.1 | -58.4 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -80.125 | 25.1 | 8 | 24.3 | 1 | 171.6 | 7 | 171.7 | 2 | 0.8 | 631.42 | 148.72 | 139308.18 | 134451.9 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:05:00 | Operating | 1381.5 | 12.2 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | 16.806 | 25.2 | 8 | 24.4 | 1 | 172.9 | 8 | 172.9 | 2 | 0.8 | 631.5 | 152.04 | 139308.3 | 134455.22 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:10:00 | Operating | 1382.8 | 7.7 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | 10.702 | 25.1 | 8 | 24.4 | 1 | 173.1 | 7 | 173.1 | 4 | 0.7 | 631.82 | 152.32 | 139308.58 | 134455.5 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:15:00 | Operating | 1376.6 | -30.1 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -41.446 | 25.1 | 8 | 24.4 | 1 | 172.3 | 7 | 172.3 | 2 | 0.7 | 632.02 | 154.26 | 139308.78 | 134457.56 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:20:00 | Operating | 1377 | -23.5 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -32.366 | 25.2 | 8 | 24.4 | 1 | 172.4 | 5 | 172.4 | 4 | 0.8 | 632.02 | 157.16 | 139308.78 | 134460.34 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:25:00 | Operating | 1377.1 | -23.1 | 81 | 99 | 81 | 90 | 140.223 | 597.793 | -31.763 | 25.2 | 8 | 24.4 | 7 | 172.4 | 5 | 172.4 | 2 | 0.7 | 632.02 | 159.82 | 139308.78 | 134463.08 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:30:00 | Operating | 1378.2 | -16.6 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -22.95 | 25.2 | 8 | 24.4 | 1 | 172.5 | 5 | 172.5 | 3 | 0.8 | 632.02 | 162.58 | 139308.78 | 134465.76 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:35:00 | Operating | 1380 | -7.1 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -9.841 | 25.1 | 8 | 24.4 | 1 | 172.7 | 5 | 172.8 | 6 | 0.7 | 632.02 | 163.96 | 139308.78 | 134467.16 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:40:00 | Operating | 1379 | -16.9 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -23.251 | 25.2 | 8 | 24.4 | 7 | 172.6 | 7 | 172.7 | 4 | 0.7 | 632.02 | 165.3 | 139308.78 | 134468.54 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:45:00 | Operating | 1373.3 | -44.1 | 80 | 99 | 79 | 90 | 154.983 | 583.033 | -60.539 | 25.1 | 8 | 24.5 | 1 | 171.9 | 2 | 171.9 | 4 | 0.8 | 632.02 | 169.88 | 139308.78 | 134473.3 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:50:00 | Operating | 1373.5 | -45.4 | 79 | 99 | 79 | 90 | 154.983 | 583.033 | -62.438 | 25.2 | 8 | 24.5 | 7 | 171.9 | 5 | 171.9 | 2 | 0.7 | 632.02 | 174.74 | 139308.78 | 134478.1 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 17:55:00 | Operating | 1374.1 | -36.4 | 79 | 99 | 78 | 90 | 162.363 | 575.653 | -50.072 | 25.2 | 8 | 24.6 | 1 | 172 | 5 | 172 | 2 | 0.8 | 632.02 | 180.42 | 139308.78 | 134483.6 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:00:00 | Operating | 1372.8 | -45.4 | 78 | 99 | 77 | 90 | 169.743 | 568.273 | -62.331 | 25.3 | 8 | 24.6 | 7 | 171.8 | 5 | 171.8 | 8 | 0.7 | 632.02 | 186.8 | 139308.78 | 134489.98 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:05:00 | Operating | 1373.9 | -39.9 | 77 | 99 | 77 | 90 | 169.743 | 568.273 | -54.827 | 25.3 | 8 | 24.7 | 1 | 172 | 5 | 172 | 2 | 0.7 | 632.02 | 190.96 | 139308.78 | 134494.3 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:10:00 | Operating | 1373.7 | -41.4 | 76 | 99 | 76 | 90 | 177.124 | 560.893 | -56.847 | 25.3 | 8 | 24.7 | 1 | 172 | 5 | 172 | 3 | 0.6 | 632.02 | 195.34 | 139308.78 | 134498.52 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:15:00 | Operating | 1371.7 | -55.8 | 76 | 99 | 75 | 90 | 184.504 | 553.512 | -76.507 | 25.3 | 8 | 24.7 | 7 | 171.7 | 5 | 171.7 | 8 | 0.7 | 632.02 | 200.98 | 139308.78 | 134504.16 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:20:00 | Operating | 1368.6 | -79.3 | 75 | 99 | 74 | 90 | 191.884 | 546.132 | -108.593 | 25.5 | 8 | 24.8 | 1 | 171.4 | 5 | 171.4 | 8 | 0.6 | 632.02 | 207.16 | 139308.78 | 134510.62 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:25:00 | Operating | 1364.7 | -93.2 | 73 | 99 | 72 | 90 | 206.644 | 531.372 | -127.241 | 25.5 | 8 | 24.9 | 1 | 170.9 | 7 | 170.9 | 8 | 0.7 | 632.02 | 217.34 | 139308.78 | 134520.92 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:30:00 | Operating | 1363.6 | -92.3 | 72 | 99 | 70 | 90 | 221.405 | 516.612 | -125.924 | 25.6 | 8 | 25 | 1 | 170.7 | 7 | 170.8 | 8 | 0.7 | 632.02 | 228.74 | 139308.78 | 134532.3 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:35:00 | Operating | 1361.1 | -96.6 | 70 | 99 | 69 | 90 | 228.785 | 509.231 | -131.603 | 25.8 | 8 | 25.1 | 1 | 170.4 | 7 | 170.5 | 8 | 0.7 | 632.02 | 239.08 | 139308.78 | 134542.66 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:40:00 | Operating | 1356.4 | -111.8 | 69 | 99 | 67 | 90 | 243.545 | 494.471 | -151.655 | 25.9 | 8 | 25.3 | 1 | 169.8 | 7 | 170 | 3 | 0.6 | 632.02 | 250.7 | 139308.78 | 134554.3 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:45:00 | Operating | 1354.5 | -105 | 67 | 99 | 65 | 90 | 258.306 | 479.711 | -142.285 | 26 | 8 | 25.4 | 1 | 169.6 | 7 | 169.7 | 8 | 0.6 | 632.02 | 262.56 | 139308.78 | 134565.74 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:50:00 | Operating | 1353 | -104.8 | 65 | 99 | 64 | 90 | 265.686 | 472.331 | -141.76 | 26.1 | 8 | 25.5 | 1 | 169.4 | 7 | 169.5 | 8 | 0.6 | 632.02 | 274.2 | 139308.78 | 134577.8 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 18:55:00 | Operating | 1349.8 | -127.5 | 64 | 99 | 62 | 90 | 280.446 | 457.57 | -172.149 | 26.1 | 8 | 25.5 | 1 | 169 | 7 | 169.1 | 8 | 0.6 | 632.02 | 286.1 | 139308.78 | 134589.28 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:00:00 | Operating | 1347 | -142.3 | 61 | 99 | 59 | 90 | 302.587 | 435.43 | -191.709 | 26.2 | 8 | 25.6 | 1 | 168.7 | 7 | 168.8 | 8 | 0.6 | 632.02 | 301.16 | 139308.78 | 134604.34 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:05:00 | Operating | 1345.8 | -149 | 59 | 99 | 57 | 90 | 317.347 | 420.669 | -200.613 | 26.3 | 8 | 25.6 | 7 | 168.6 | 5 | 168.6 | 8 | 0.6 | 632.02 | 316.64 | 139308.78 | 134620.42 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:10:00 | Operating | 1345.8 | -146.1 | 57 | 99 | 55 | 90 | 332.107 | 405.909 | -196.624 | 26.4 | 8 | 25.8 | 1 | 168.5 | 5 | 168.6 | 4 | 0.6 | 632.02 | 334.82 | 139308.78 | 134638.6 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:15:00 | Operating | 1344 | -161.2 | 54 | 99 | 52 | 90 | 354.248 | 383.768 | -216.732 | 26.4 | 8 | 25.8 | 7 | 168.3 | 5 | 168.4 | 8 | 0.6 | 632.02 | 352.16 | 139308.78 | 134655.34 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:20:00 | Operating | 1342.4 | -169 | 52 | 99 | 49 | 90 | 376.388 | 361.628 | -226.972 | 26.5 | 8 | 26 | 1 | 168.1 | 5 | 168.2 | 2 | 0.5 | 632.02 | 370.16 | 139308.78 | 134673.34 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:25:00 | Operating | 1339.8 | -185.9 | 49 | 99 | 46 | 90 | 398.529 | 339.487 | -249.222 | 26.7 | 8 | 26.1 | 1 | 167.8 | 5 | 167.9 | 8 | 0.6 | 632.02 | 389.88 | 139308.78 | 134693.06 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:30:00 | Operating | 1335.8 | -210.1 | 46 | 99 | 43 | 90 | 420.669 | 317.347 | -280.663 | 26.8 | 8 | 26.3 | 1 | 167.4 | 5 | 167.4 | 8 | 0.5 | 632.02 | 410.92 | 139308.78 | 134714.1 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:35:00 | Operating | 1334.7 | -205.3 | 42 | 99 | 40 | 90 | 442.81 | 295.206 | -274.122 | 27.2 | 8 | 26.6 | 1 | 167.2 | 7 | 167.3 | 8 | 0.6 | 632.02 | 434.64 | 139308.78 | 134737.82 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:40:00 | Operating | 1332.6 | -209.1 | 39 | 99 | 36 | 90 | 472.331 | 265.686 | -278.798 | 27.4 | 8 | 26.9 | 1 | 167 | 7 | 167.1 | 8 | 0.5 | 632.02 | 457.58 | 139308.78 | 134760.76 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:45:00 | Operating | 1330.3 | -204.5 | 36 | 99 | 33 | 90 | 494.471 | 243.545 | -272.151 | 27.7 | 8 | 27.2 | 1 | 166.7 | 7 | 166.8 | 8 | 0.5 | 632.02 | 481.24 | 139308.78 | 134785.28 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:50:00 | Operating | 1323.1 | -244.7 | 32 | 99 | 29 | 90 | 523.992 | 214.025 | -323.921 | 28.2 | 8 | 27.7 | 1 | 165.8 | 7 | 165.9 | 8 | 0.5 | 632.02 | 506.62 | 139308.78 | 134810.8 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 19:55:00 | Operating | 1329.9 | -161 | 28 | 99 | 26 | 90 | 546.132 | 191.884 | -214.11 | 28.6 | 8 | 28.2 | 1 | 166.6 | 7 | 166.7 | 8 | 0.4 | 632.02 | 530.76 | 139308.78 | 134834.64 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:00:00 | Operating | 1337.9 | -90.5 | 26 | 99 | 25 | 90 | 553.512 | 184.504 | -121.081 | 28.7 | 8 | 28.3 | 1 | 167.6 | 7 | 167.6 | 8 | 0.4 | 632.02 | 545.24 | 139308.78 | 134848.42 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:05:00 | Operating | 1341.5 | -59.8 | 25 | 99 | 24 | 90 | 560.893 | 177.124 | -80.289 | 28.7 | 8 | 28.2 | 1 | 168 | 7 | 168.1 | 8 | 0.4 | 632.02 | 554.68 | 139308.78 | 134858.12 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:10:00 | Operating | 1351.7 | -6.7 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | -9.077 | 28.5 | 3 | 28 | 1 | 169.3 | 7 | 169.3 | 8 | 0.5 | 632.26 | 556.62 | 139309.02 | 134859.8 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:15:00 | Operating | 1348.4 | -36.9 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | -49.782 | 28.4 | 3 | 27.8 | 4 | 168.9 | 7 | 168.9 | 8 | 0.6 | 632.3 | 558.04 | 139309.06 | 134861.36 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:20:00 | Operating | 1344.1 | -50 | 24 | 99 | 23 | 90 | 568.273 | 169.743 | -67.451 | 28.3 | 3 | 27.6 | 4 | 168.3 | 7 | 168.3 | 8 | 0.7 | 632.3 | 563.18 | 139309.06 | 134866.56 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:25:00 | Operating | 1342.7 | -46.8 | 23 | 99 | 22 | 90 | 575.653 | 162.363 | -62.919 | 28.2 | 8 | 27.5 | 4 | 168.1 | 7 | 168.2 | 8 | 0.6 | 632.3 | 568.74 | 139309.06 | 134871.92 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:30:00 | Operating | 1341.5 | -46 | 22 | 99 | 21 | 90 | 583.033 | 154.983 | -61.729 | 28.1 | 8 | 27.4 | 4 | 167.9 | 7 | 168 | 8 | 0.7 | 632.3 | 574.08 | 139309.06 | 134877.44 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:35:00 | Operating | 1342.3 | -37.7 | 22 | 99 | 20 | 90 | 590.413 | 147.603 | -50.661 | 27.9 | 8 | 27.1 | 4 | 168.1 | 7 | 168.1 | 8 | 0.7 | 632.3 | 578.48 | 139309.06 | 134881.66 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:40:00 | Operating | 1341.6 | -35.2 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | -47.299 | 27.7 | 8 | 27 | 1 | 167.9 | 7 | 168 | 8 | 0.7 | 632.3 | 582.8 | 139309.06 | 134886.12 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:45:00 | Operating | 1341.2 | -33.4 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | -44.817 | 27.5 | 2 | 26.8 | 4 | 167.9 | 7 | 168 | 8 | 0.7 | 632.3 | 586.76 | 139309.06 | 134890.06 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:50:00 | Operating | 1342.2 | -22.8 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -30.586 | 27.3 | 8 | 26.6 | 4 | 168 | 7 | 168.1 | 8 | 0.7 | 632.3 | 590.22 | 139309.06 | 134893.4 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 20:55:00 | Operating | 1339.5 | -33.4 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -44.726 | 27.1 | 3 | 26.5 | 4 | 167.6 | 7 | 167.7 | 8 | 0.8 | 632.3 | 594.46 | 139309.06 | 134897.78 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:00:00 | Operating | 1339.9 | -28.2 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -37.8 | 27 | 8 | 26.3 | 4 | 167.7 | 7 | 167.8 | 8 | 0.6 | 632.3 | 597.3 | 139309.06 | 134900.6 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:05:00 | Operating | 1343.1 | -11.9 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | -15.93 | 26.7 | 8 | 26.1 | 4 | 168.1 | 7 | 168.2 | 8 | 0.7 | 632.3 | 598.98 | 139309.06 | 134902.2 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:10:00 | Operating | 1346.3 | 7.3 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 9.842 | 26.6 | 8 | 25.9 | 4 | 168.5 | 7 | 168.6 | 5 | 0.7 | 632.34 | 599.72 | 139309.12 | 134902.9 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:15:00 | Operating | 1345 | -3.9 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | -5.278 | 26.4 | 8 | 25.6 | 4 | 168.4 | 7 | 168.4 | 8 | 0.7 | 632.48 | 600.22 | 139309.24 | 134903.4 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:20:00 | Operating | 1343.4 | -14.4 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | -19.344 | 26.1 | 2 | 25.5 | 1 | 168.1 | 7 | 168.2 | 8 | 0.7 | 632.64 | 600.86 | 139309.4 | 134904.1 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:25:00 | Operating | 1345.9 | -0.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -0.724 | 26 | 8 | 25.3 | 4 | 168.5 | 7 | 168.6 | 5 | 0.7 | 632.7 | 601.8 | 139309.46 | 134904.98 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:30:00 | Operating | 1347.9 | 5.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 7.352 | 25.9 | 8 | 25.1 | 4 | 168.7 | 7 | 168.8 | 5 | 0.8 | 633.16 | 601.8 | 139309.94 | 134904.98 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:35:00 | Operating | 1345 | -5.1 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -6.812 | 25.8 | 8 | 25 | 4 | 168.3 | 7 | 168.4 | 8 | 0.7 | 633.2 | 602.68 | 139309.96 | 134905.86 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:40:00 | Operating | 1344.3 | -8.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -11.253 | 25.6 | 8 | 24.9 | 1 | 168.3 | 7 | 168.4 | 8 | 0.7 | 633.2 | 603.54 | 139309.96 | 134906.74 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:45:00 | Operating | 1344.6 | -3.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -4.662 | 25.5 | 8 | 24.7 | 1 | 168.2 | 7 | 168.3 | 8 | 0.8 | 633.22 | 604.1 | 139309.98 | 134907.28 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:50:00 | Operating | 1345.9 | 2.6 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 3.473 | 25.3 | 2 | 24.6 | 4 | 168.4 | 7 | 168.5 | 8 | 0.7 | 633.22 | 604.44 | 139309.98 | 134907.62 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 21:55:00 | Operating | 1344.1 | -5.4 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -7.214 | 25.2 | 8 | 24.4 | 4 | 168.2 | 7 | 168.3 | 8 | 0.7 | 633.52 | 605.28 | 139310.28 | 134908.46 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:00:00 | Operating | 1341.7 | -17.4 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -23.389 | 25.1 | 8 | 24.3 | 4 | 167.9 | 7 | 168 | 8 | 0.8 | 633.64 | 606 | 139310.4 | 134909.24 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:05:00 | Operating | 1344.4 | -1.2 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -1.572 | 25 | 8 | 24.2 | 4 | 168.2 | 7 | 168.3 | 8 | 0.8 | 633.64 | 607 | 139310.4 | 134910.2 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:10:00 | Operating | 1345.9 | 6.8 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | 9.219 | 24.9 | 8 | 24.1 | 4 | 168.4 | 7 | 168.5 | 5 | 0.8 | 633.74 | 607.28 | 139310.5 | 134910.46 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:15:00 | Operating | 1346 | 0.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 0.719 | 24.9 | 8 | 24 | 4 | 168.5 | 4 | 168.5 | 5 | 0.7 | 634.08 | 607.3 | 139310.84 | 134910.48 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:20:00 | Operating | 1348.8 | 8.9 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 11.945 | 24.8 | 8 | 24 | 1 | 168.7 | 4 | 168.8 | 5 | 0.8 | 634.6 | 607.34 | 139311.36 | 134910.52 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:25:00 | Operating | 1353.6 | 23.7 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 32.026 | 24.8 | 8 | 24 | 1 | 169.3 | 4 | 169.4 | 5 | 0.8 | 636.22 | 607.34 | 139313.08 | 134910.52 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:30:00 | Operating | 1360.5 | 49.4 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 67.212 | 24.7 | 8 | 24 | 4 | 170.2 | 4 | 170.3 | 6 | 0.8 | 639.32 | 607.34 | 139316.26 | 134910.52 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:35:00 | Operating | 1355.1 | 10.8 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 14.662 | 24.6 | 2 | 24 | 4 | 169.6 | 4 | 169.7 | 5 | 0.8 | 641.4 | 607.34 | 139318.16 | 134910.52 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:40:00 | Operating | 1354.1 | 10.8 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 14.583 | 24.7 | 8 | 23.9 | 4 | 169.5 | 4 | 169.6 | 5 | 0.8 | 641.76 | 607.74 | 139318.58 | 134910.92 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:45:00 | Operating | 1359 | 27.8 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 37.819 | 24.6 | 2 | 23.9 | 4 | 170 | 4 | 170.1 | 5 | 0.8 | 643.8 | 607.74 | 139320.56 | 134910.92 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:50:00 | Operating | 1361 | 18.9 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 25.754 | 24.7 | 8 | 24 | 1 | 170.3 | 4 | 170.4 | 6 | 0.8 | 647.3 | 607.74 | 139324.14 | 134910.92 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 22:55:00 | Operating | 1355.2 | -4.1 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -5.507 | 24.7 | 8 | 23.9 | 4 | 169.6 | 4 | 169.7 | 8 | 0.8 | 647.92 | 607.78 | 139324.68 | 134910.98 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:00:00 | Operating | 1351.2 | -7.9 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -10.748 | 24.6 | 3 | 24 | 4 | 169.1 | 3 | 169.2 | 8 | 0.6 | 647.92 | 609 | 139324.68 | 134912.2 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:05:00 | Operating | 1355.4 | 6.5 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 8.759 | 24.7 | 8 | 24 | 1 | 169.6 | 4 | 169.7 | 5 | 0.8 | 648.48 | 609.12 | 139325.24 | 134912.3 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:10:00 | Operating | 1354.9 | 0.4 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 0.585 | 24.7 | 8 | 24 | 1 | 169.6 | 4 | 169.6 | 8 | 0.7 | 649.32 | 609.26 | 139326.1 | 134912.44 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:15:00 | Operating | 1355 | 0.7 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 1.016 | 24.6 | 2 | 23.9 | 4 | 169.6 | 4 | 169.6 | 8 | 0.8 | 649.92 | 609.32 | 139326.68 | 134912.52 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:20:00 | Operating | 1357.5 | 10.5 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 14.155 | 24.7 | 8 | 24 | 4 | 169.9 | 4 | 170 | 5 | 0.7 | 650.68 | 609.34 | 139327.44 | 134912.52 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:25:00 | Operating | 1360.9 | 21.5 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 29.234 | 24.7 | 8 | 23.9 | 4 | 170.3 | 4 | 170.4 | 5 | 0.6 | 652.32 | 609.34 | 139329.16 | 134912.52 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:30:00 | Operating | 1363 | 23.2 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 31.692 | 24.6 | 2 | 23.9 | 4 | 170.5 | 4 | 170.6 | 6 | 0.6 | 654.4 | 609.34 | 139331.26 | 134912.52 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:35:00 | Operating | 1358.6 | -1.3 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | -1.815 | 24.6 | 2 | 24 | 1 | 170 | 4 | 170.1 | 6 | 0.6 | 655.74 | 609.42 | 139332.5 | 134912.6 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:40:00 | Operating | 1358.7 | 2.4 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | 3.215 | 24.7 | 2 | 24 | 1 | 170 | 4 | 170.1 | 5 | 0.7 | 656.12 | 609.72 | 139332.88 | 134912.9 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:45:00 | Operating | 1356.3 | -3.5 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | -4.73 | 24.6 | 3 | 24 | 4 | 169.8 | 3 | 169.8 | 8 | 0.6 | 656.46 | 609.96 | 139333.22 | 134913.14 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:50:00 | Operating | 1360.2 | 11.4 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | 15.579 | 24.6 | 2 | 24 | 4 | 170.2 | 4 | 170.3 | 6 | 0.7 | 657.12 | 610.26 | 139333.88 | 134913.44 | 1.087
Amleang 136MW-01 | / | SACU-01/B01-ESS03/ESR-HV2520040754 | 2026-06-03 23:55:00 | Operating | 1363.4 | 15.2 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | 20.739 | 24.6 | 2 | 24 | 7 | 170.6 | 4 | 170.6 | 6 | 0.6 | 659.46 | 610.26 | 139336.26 | 134913.44 | 1.087