## 5 minutes
Time range: | 2026-06-03 00:00:00 - 2026-06-03 23:59:59
Export time: | 2026-06-04 00:34:28
"N/A": Not available/Some counters are not recorded when the device is disconnected "-": This counter is not supported by the device. Content in gray italics: This is the supplementary data and is for reference only.
Plant Name | Management Domain | Device Name | Start Time | Device status | Voltage(V) | Current(A) | SOC(%) | SOH(%) | SOE(%) | DOD(%) | Chargeable capacity(kWh) | Dischargeable capacity(kWh) | Charge/Discharge Power(kW) | Module with the highest temperature(°C) | Position of the module with the highest temperature | Module with the lowest temperature(°C) | Position of the module with the lowest temperature | Lowest battery pack voltage(V) | Position where the lowest battery pack voltage was detected | Highest battery pack voltage(V) | Position where the highest battery pack voltage was detected | Average Temperature(°C) | Daily charge energy(kWh) | Daily discharge energy(kWh) | Total charge(kWh) | Total discharge(kWh) | ISO insulation resistance(MΩ)
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:00:00 | Operating | 1336.5 | -23.2 | 17 | 99 | 15 | 90 | 627.314 | 110.702 | -31.049 | 24.7 | 7 | 24 | 5 | 167.1 | 2 | 167.3 | 8 | 0.6 | 0 | 0 | 140017.68 | 135942.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:05:00 | Operating | 1339.2 | -3.2 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -4.268 | 24.7 | 3 | 24.1 | 5 | 167.4 | 2 | 167.6 | 8 | 0.6 | 0 | 1.44 | 140017.68 | 135943.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:10:00 | Operating | 1338.7 | -20.3 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -27.191 | 24.7 | 7 | 24.1 | 5 | 167.4 | 2 | 167.6 | 8 | 0.6 | 0.58 | 2.08 | 140018.26 | 135944.62 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:15:00 | Operating | 1334.2 | -17.6 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -23.554 | 24.7 | 3 | 24.1 | 5 | 166.8 | 2 | 167 | 8 | 0.6 | 0.58 | 4.42 | 140018.26 | 135947.06 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:20:00 | Operating | 1333.4 | -33 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -43.973 | 24.7 | 1 | 24.1 | 5 | 166.7 | 2 | 166.9 | 8 | 0.6 | 0.58 | 6.02 | 140018.26 | 135948.66 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:25:00 | Operating | 1333.4 | -16.9 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | -22.494 | 24.8 | 7 | 24.2 | 5 | 166.7 | 2 | 166.9 | 8 | 0.6 | 0.58 | 8.68 | 140018.26 | 135951.22 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:30:00 | Operating | 1336.8 | -10.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -13.462 | 24.8 | 3 | 24.2 | 5 | 167.2 | 2 | 167.4 | 8 | 0.6 | 0.66 | 9.42 | 140018.34 | 135952 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:35:00 | Operating | 1333.6 | -19 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -25.393 | 24.8 | 3 | 24.2 | 5 | 166.7 | 2 | 167 | 8 | 0.6 | 0.66 | 11.1 | 140018.34 | 135953.64 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:40:00 | Operating | 1334.1 | -8.9 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -11.874 | 24.8 | 3 | 24.2 | 5 | 166.8 | 2 | 167 | 8 | 0.6 | 0.66 | 12.92 | 140018.34 | 135955.5 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:45:00 | Operating | 1335.9 | -1.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -1.474 | 24.9 | 7 | 24.3 | 5 | 167 | 2 | 167.2 | 8 | 0.6 | 0.76 | 14.18 | 140018.44 | 135956.74 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:50:00 | Operating | 1335.2 | -8.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -10.846 | 24.9 | 7 | 24.3 | 5 | 167 | 2 | 167.2 | 8 | 0.6 | 0.78 | 14.8 | 140018.46 | 135957.34 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 00:55:00 | Operating | 1331.1 | -21.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -28.724 | 25 | 7 | 24.4 | 4 | 166.5 | 2 | 166.6 | 8 | 0.5 | 0.78 | 16.4 | 140018.46 | 135959.02 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:00:00 | Operating | 1331.2 | -24.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -32.517 | 25 | 3 | 24.4 | 4 | 166.5 | 2 | 166.7 | 8 | 0.7 | 0.8 | 17.6 | 140018.48 | 135960.14 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:05:00 | Operating | 1330.5 | -13.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -18.274 | 24.9 | 3 | 24.4 | 5 | 166.3 | 2 | 166.6 | 8 | 0.6 | 0.8 | 19.76 | 140018.48 | 135962.34 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:10:00 | Operating | 1331.5 | -13.2 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -17.568 | 25 | 7 | 24.4 | 5 | 166.5 | 2 | 166.7 | 8 | 0.6 | 0.82 | 21.06 | 140018.5 | 135963.6 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:15:00 | Operating | 1328.8 | -29 | 14 | 99 | 12 | 90 | 649.455 | 88.562 | -38.595 | 25 | 3 | 24.5 | 4 | 166.2 | 2 | 166.5 | 8 | 0.6 | 0.82 | 22.56 | 140018.5 | 135965.1 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:20:00 | Operating | 1329.4 | -8.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -11.582 | 25 | 3 | 24.5 | 4 | 166.2 | 2 | 166.4 | 6 | 0.5 | 0.82 | 24.48 | 140018.5 | 135967.08 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:25:00 | Operating | 1334.2 | 3.6 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 4.824 | 25.1 | 7 | 24.5 | 4 | 166.8 | 3 | 167.1 | 8 | 0.5 | 0.92 | 25.14 | 140018.62 | 135967.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:30:00 | Operating | 1340.9 | 23.2 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 31.207 | 25.1 | 7 | 24.5 | 4 | 167.5 | 1 | 167.8 | 8 | 0.5 | 1.74 | 25.3 | 140019.48 | 135967.84 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:35:00 | Operating | 1340.6 | 5.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 7.676 | 25 | 3 | 24.5 | 5 | 167.6 | 1 | 167.9 | 8 | 0.5 | 2.94 | 25.3 | 140020.62 | 135967.84 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:40:00 | Operating | 1342.9 | 11.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 15.664 | 25.1 | 7 | 24.5 | 5 | 167.8 | 1 | 168.1 | 8 | 0.5 | 3.96 | 25.32 | 140021.64 | 135967.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:45:00 | Operating | 1348.5 | 17.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 23.376 | 25.1 | 7 | 24.5 | 4 | 168.5 | 1 | 168.8 | 8 | 0.6 | 6.26 | 25.32 | 140024 | 135967.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:50:00 | Operating | 1350.3 | 18.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 24.728 | 25.1 | 7 | 24.5 | 5 | 168.7 | 1 | 169.1 | 8 | 0.6 | 8.46 | 25.32 | 140026.14 | 135967.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 01:55:00 | Operating | 1345.7 | -3.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -4.428 | 25.1 | 3 | 24.5 | 5 | 168.2 | 1 | 168.5 | 8 | 0.5 | 9.2 | 25.32 | 140026.88 | 135967.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:00:00 | Operating | 1340.1 | -16.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -22.443 | 25.1 | 3 | 24.6 | 4 | 167.5 | 1 | 167.8 | 8 | 0.5 | 9.34 | 25.9 | 140027.02 | 135968.52 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:05:00 | Operating | 1341.1 | 3.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.281 | 25.2 | 3 | 24.6 | 5 | 167.6 | 1 | 167.8 | 8 | 0.6 | 9.36 | 26.98 | 140027.04 | 135969.52 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:10:00 | Operating | 1343 | 3.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.089 | 25.2 | 7 | 24.6 | 5 | 167.8 | 1 | 168.1 | 8 | 0.7 | 10.12 | 27.22 | 140027.8 | 135969.78 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:15:00 | Operating | 1338.9 | -13.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -18.473 | 25.2 | 3 | 24.6 | 4 | 167.4 | 1 | 167.6 | 8 | 0.6 | 10.2 | 27.76 | 140027.88 | 135970.3 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:20:00 | Operating | 1340.2 | 5.7 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 7.697 | 25.1 | 3 | 24.6 | 5 | 167.5 | 1 | 167.8 | 8 | 0.6 | 10.2 | 28.64 | 140027.9 | 135971.2 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:25:00 | Operating | 1341.9 | -4.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -6.506 | 25.2 | 3 | 24.6 | 4 | 167.7 | 1 | 168 | 8 | 0.6 | 10.84 | 28.66 | 140028.52 | 135971.22 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:30:00 | Operating | 1339.9 | -2.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -3.474 | 25.2 | 3 | 24.6 | 5 | 167.5 | 1 | 167.8 | 8 | 0.5 | 10.88 | 29.14 | 140028.56 | 135971.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:35:00 | Operating | 1341.8 | 11.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 15.164 | 25.2 | 3 | 24.6 | 5 | 167.6 | 1 | 167.9 | 8 | 0.5 | 10.98 | 29.48 | 140028.66 | 135972.02 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:40:00 | Operating | 1343.5 | 4.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 6.357 | 25.2 | 7 | 24.7 | 2 | 167.9 | 1 | 168.2 | 8 | 0.7 | 11.68 | 29.52 | 140029.36 | 135972.06 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:45:00 | Operating | 1342.4 | 2.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 3.703 | 25.2 | 3 | 24.6 | 5 | 167.8 | 1 | 168.1 | 8 | 0.6 | 11.86 | 29.76 | 140029.54 | 135972.3 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:50:00 | Operating | 1340.1 | -8.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -11.575 | 25.2 | 3 | 24.7 | 2 | 167.5 | 1 | 167.8 | 8 | 0.6 | 12.22 | 30.04 | 140029.9 | 135972.6 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 02:55:00 | Operating | 1341.5 | 6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 8.12 | 25.2 | 3 | 24.6 | 5 | 167.7 | 1 | 167.9 | 8 | 0.5 | 12.38 | 30.62 | 140030.06 | 135973.16 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:00:00 | Operating | 1343.2 | 8.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 11.282 | 25.3 | 3 | 24.6 | 5 | 167.9 | 1 | 168.2 | 8 | 0.5 | 12.72 | 30.88 | 140030.42 | 135973.42 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:05:00 | Operating | 1340.8 | -1 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -1.391 | 25.3 | 3 | 24.7 | 5 | 167.6 | 1 | 167.9 | 8 | 0.5 | 13.04 | 31.44 | 140030.72 | 135973.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:10:00 | Operating | 1339.4 | -4.5 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -5.993 | 25.2 | 3 | 24.7 | 5 | 167.4 | 1 | 167.7 | 8 | 0.6 | 13.14 | 31.84 | 140030.82 | 135974.38 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:15:00 | Operating | 1338.6 | -3.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -4.607 | 25.2 | 3 | 24.7 | 5 | 167.3 | 1 | 167.6 | 8 | 0.5 | 13.16 | 32.46 | 140030.84 | 135975.02 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:20:00 | Operating | 1339.4 | 4.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 5.621 | 25.2 | 3 | 24.7 | 4 | 167.4 | 1 | 167.7 | 8 | 0.6 | 13.32 | 33.04 | 140031.02 | 135975.58 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:25:00 | Operating | 1350.2 | 23 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 31.124 | 25.3 | 7 | 24.7 | 5 | 168.7 | 1 | 169.1 | 8 | 0.6 | 15.7 | 33.04 | 140033.44 | 135975.58 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:30:00 | Operating | 1345.8 | 2.9 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 3.94 | 25.3 | 3 | 24.7 | 5 | 168.2 | 1 | 168.5 | 8 | 0.6 | 16.5 | 33.2 | 140034.2 | 135975.74 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:35:00 | Operating | 1345 | 1.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 1.802 | 25.3 | 7 | 24.7 | 5 | 168.1 | 1 | 168.4 | 8 | 0.5 | 16.9 | 33.32 | 140034.58 | 135975.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:40:00 | Operating | 1354.1 | 28.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 38.594 | 25.3 | 3 | 24.7 | 5 | 169.2 | 1 | 169.5 | 8 | 0.6 | 18.96 | 33.32 | 140036.76 | 135975.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:45:00 | Operating | 1363 | 57.3 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 78.134 | 25.3 | 3 | 24.8 | 4 | 170.2 | 3 | 170.6 | 8 | 0.5 | 24 | 33.32 | 140041.9 | 135975.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:50:00 | Operating | 1367.3 | 58.5 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 80.13 | 25.4 | 7 | 24.7 | 5 | 170.8 | 3 | 171.2 | 8 | 0.6 | 31.6 | 33.32 | 140049.28 | 135975.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 03:55:00 | Operating | 1365.6 | 44.6 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 60.986 | 25.4 | 7 | 24.9 | 2 | 170.6 | 3 | 171 | 8 | 0.6 | 36.62 | 33.32 | 140054.48 | 135975.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:00:00 | Operating | 1372.1 | 62.1 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 85.297 | 25.5 | 7 | 24.9 | 5 | 171.4 | 1 | 171.7 | 8 | 0.6 | 43.26 | 33.32 | 140061.22 | 135975.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:05:00 | Operating | 1360.4 | -1.4 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -1.93 | 25.5 | 3 | 24.9 | 4 | 170 | 3 | 170.3 | 8 | 0.7 | 45.82 | 33.52 | 140063.5 | 135976.1 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:10:00 | Operating | 1351.1 | -35.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -48.021 | 25.4 | 3 | 24.9 | 4 | 168.8 | 3 | 169.2 | 8 | 0.6 | 45.82 | 35.98 | 140063.5 | 135978.52 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:15:00 | Operating | 1350.5 | -20.1 | 18 | 99 | 16 | 90 | 619.934 | 118.082 | -27.231 | 25.5 | 3 | 24.9 | 5 | 168.7 | 3 | 169.1 | 8 | 0.6 | 45.82 | 38.42 | 140063.5 | 135980.96 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:20:00 | Operating | 1348 | -18.1 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | -24.4 | 25.5 | 3 | 25 | 2 | 168.3 | 3 | 168.8 | 8 | 0.6 | 45.82 | 40.9 | 140063.5 | 135983.52 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:25:00 | Operating | 1340.4 | -42.6 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | -57.055 | 25.5 | 3 | 25 | 4 | 167.5 | 3 | 167.9 | 8 | 0.7 | 45.82 | 44.22 | 140063.5 | 135986.76 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:30:00 | Operating | 1332.8 | -51.3 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -68.46 | 25.6 | 7 | 25 | 5 | 166.5 | 3 | 166.9 | 8 | 0.5 | 45.82 | 49.66 | 140063.5 | 135992.4 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:35:00 | Operating | 1329.8 | -52.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -69.346 | 25.7 | 7 | 25.1 | 4 | 166.3 | 1 | 166.5 | 8 | 0.6 | 45.82 | 54.7 | 140063.5 | 135997.24 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:40:00 | Operating | 1329.2 | -35.1 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -46.738 | 25.7 | 3 | 25.2 | 4 | 166.3 | 2 | 166.5 | 8 | 0.6 | 45.82 | 59.28 | 140063.5 | 136001.94 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:45:00 | Operating | 1329.2 | -25.4 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -33.781 | 25.8 | 3 | 25.2 | 4 | 166.2 | 2 | 166.4 | 8 | 0.6 | 45.82 | 62.72 | 140063.5 | 136005.26 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:50:00 | Operating | 1329.9 | -13 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -17.294 | 25.8 | 3 | 25.2 | 5 | 166.3 | 2 | 166.5 | 8 | 0.5 | 45.82 | 65.72 | 140063.5 | 136008.32 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 04:55:00 | Operating | 1333.2 | -5.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -7.797 | 25.8 | 3 | 25.2 | 5 | 166.7 | 2 | 166.9 | 8 | 0.5 | 45.82 | 66.5 | 140063.5 | 136009.04 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:00:00 | Operating | 1335.5 | -0.8 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | -1.071 | 25.8 | 3 | 25.3 | 5 | 167 | 1 | 167.2 | 8 | 0.5 | 46.1 | 66.72 | 140063.78 | 136009.26 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:05:00 | Operating | 1330.7 | -15.3 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -20.331 | 25.9 | 3 | 25.3 | 4 | 166.4 | 2 | 166.6 | 8 | 0.6 | 46.16 | 67.9 | 140063.84 | 136010.52 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:10:00 | Operating | 1324 | -42.8 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -56.771 | 25.9 | 3 | 25.2 | 5 | 165.6 | 2 | 165.8 | 8 | 0.5 | 46.16 | 70.3 | 140063.84 | 136012.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:15:00 | Operating | 1331.9 | 1.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 2.214 | 25.9 | 3 | 25.3 | 5 | 166.5 | 1 | 166.8 | 8 | 0.6 | 46.22 | 72.02 | 140063.9 | 136014.56 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:20:00 | Operating | 1331.3 | -7.7 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -10.327 | 25.9 | 3 | 25.4 | 4 | 166.5 | 1 | 166.7 | 8 | 0.6 | 46.22 | 72.44 | 140063.9 | 136014.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:25:00 | Operating | 1331.4 | -7.6 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -10.074 | 25.9 | 3 | 25.3 | 5 | 166.5 | 1 | 166.8 | 8 | 0.5 | 46.22 | 73.06 | 140063.9 | 136015.62 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:30:00 | Operating | 1329.5 | -10 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -13.293 | 25.9 | 7 | 25.3 | 5 | 166.2 | 2 | 166.5 | 8 | 0.6 | 46.24 | 74.16 | 140063.92 | 136016.7 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:35:00 | Operating | 1333.1 | 3.5 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 4.621 | 26 | 3 | 25.4 | 4 | 166.6 | 1 | 166.9 | 8 | 0.6 | 46.28 | 74.62 | 140063.98 | 136017.16 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:40:00 | Operating | 1330.8 | -6.6 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | -8.727 | 26 | 3 | 25.4 | 2 | 166.4 | 1 | 166.7 | 8 | 0.6 | 46.34 | 75.08 | 140064.02 | 136017.62 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:45:00 | Operating | 1331.1 | -5.5 | 13 | 99 | 11 | 90 | 656.835 | 81.181 | -7.286 | 25.9 | 3 | 25.4 | 4 | 166.5 | 1 | 166.7 | 8 | 0.5 | 46.34 | 75.56 | 140064.02 | 136018.12 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:50:00 | Operating | 1331.3 | -2.1 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -2.792 | 25.9 | 3 | 25.4 | 5 | 166.4 | 1 | 166.7 | 8 | 0.5 | 46.34 | 76.24 | 140064.02 | 136018.78 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 05:55:00 | Operating | 1330.2 | -3.4 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -4.526 | 26 | 3 | 25.4 | 5 | 166.3 | 3 | 166.6 | 8 | 0.6 | 46.34 | 76.96 | 140064.02 | 136019.54 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:00:00 | Operating | 1330.2 | -4 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | -5.276 | 26 | 7 | 25.4 | 5 | 166.3 | 3 | 166.6 | 8 | 0.6 | 46.38 | 77.6 | 140064.06 | 136020.16 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:05:00 | Operating | 1339.8 | 24.5 | 12 | 99 | 11 | 90 | 656.835 | 81.181 | 32.914 | 26 | 3 | 25.4 | 5 | 167.4 | 1 | 167.8 | 8 | 0.6 | 47.42 | 77.88 | 140065.1 | 136020.42 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:10:00 | Operating | 1344.6 | 25.3 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 34.045 | 25.9 | 3 | 25.4 | 5 | 168 | 1 | 168.4 | 8 | 0.5 | 50.04 | 77.88 | 140067.8 | 136020.42 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:15:00 | Operating | 1349.6 | 24 | 13 | 99 | 12 | 90 | 649.455 | 88.562 | 32.449 | 26 | 7 | 25.4 | 5 | 168.6 | 1 | 169.1 | 8 | 0.6 | 53.9 | 77.88 | 140071.58 | 136020.42 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:20:00 | Operating | 1354.5 | 35.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 48.267 | 25.9 | 3 | 25.4 | 5 | 169.2 | 3 | 169.6 | 8 | 0.5 | 58.14 | 77.88 | 140075.96 | 136020.42 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:25:00 | Operating | 1350.7 | 15.3 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 20.722 | 26 | 3 | 25.4 | 5 | 168.7 | 3 | 169.2 | 8 | 0.6 | 60.32 | 77.9 | 140078 | 136020.44 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:30:00 | Operating | 1351.6 | 17.6 | 14 | 99 | 13 | 90 | 642.075 | 95.942 | 23.783 | 26 | 7 | 25.4 | 5 | 168.8 | 3 | 169.3 | 8 | 0.6 | 61.58 | 77.9 | 140079.26 | 136020.44 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:35:00 | Operating | 1355 | 21.6 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 29.324 | 26 | 3 | 25.5 | 2 | 169.3 | 3 | 169.7 | 8 | 0.5 | 64.36 | 77.9 | 140082.14 | 136020.44 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:40:00 | Operating | 1357.5 | 31.4 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 42.71 | 26 | 3 | 25.4 | 5 | 169.6 | 3 | 170 | 8 | 0.6 | 67.16 | 77.9 | 140084.84 | 136020.44 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:45:00 | Operating | 1359.8 | 25.8 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 35.116 | 26 | 3 | 25.5 | 5 | 169.9 | 3 | 170.3 | 8 | 0.5 | 71.18 | 77.9 | 140088.86 | 136020.44 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:50:00 | Operating | 1359.1 | 17.7 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 24.038 | 26.1 | 3 | 25.5 | 5 | 169.8 | 1 | 170.2 | 8 | 0.6 | 74.02 | 77.9 | 140091.8 | 136020.44 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 06:55:00 | Operating | 1353.5 | -8.9 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -12.091 | 26.1 | 3 | 25.5 | 5 | 169.2 | 3 | 169.5 | 8 | 0.6 | 75.22 | 78.02 | 140092.9 | 136020.56 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:00:00 | Operating | 1348.7 | -23.8 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -32.081 | 26.1 | 7 | 25.5 | 5 | 168.6 | 3 | 169 | 8 | 0.6 | 75.28 | 78.7 | 140092.96 | 136021.3 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:05:00 | Operating | 1348.6 | -5.2 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -7.039 | 26.1 | 3 | 25.5 | 5 | 168.5 | 3 | 168.9 | 8 | 0.6 | 75.28 | 80.38 | 140092.96 | 136022.92 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:10:00 | Operating | 1347 | -0.5 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -0.695 | 26.2 | 3 | 25.6 | 5 | 168.3 | 3 | 168.7 | 8 | 0.5 | 75.28 | 81.92 | 140092.96 | 136024.46 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:15:00 | Operating | 1348.9 | -6.7 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -8.983 | 26.1 | 3 | 25.6 | 4 | 168.6 | 3 | 169 | 8 | 0.6 | 75.96 | 81.96 | 140093.64 | 136024.5 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:20:00 | Operating | 1348.3 | -8.7 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | -11.797 | 26.2 | 3 | 25.6 | 2 | 168.5 | 3 | 168.9 | 8 | 0.6 | 76.22 | 82.22 | 140093.9 | 136024.76 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:25:00 | Operating | 1342.3 | -17.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -23.876 | 26.2 | 3 | 25.6 | 5 | 167.7 | 3 | 168.1 | 8 | 0.5 | 76.22 | 84.1 | 140093.9 | 136026.72 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:30:00 | Operating | 1343.9 | -8.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -11.821 | 26.2 | 3 | 25.6 | 5 | 168 | 3 | 168.3 | 8 | 0.6 | 76.22 | 84.96 | 140093.9 | 136027.54 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:35:00 | Operating | 1341.3 | -16.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -22.139 | 26.2 | 3 | 25.6 | 5 | 167.6 | 3 | 168 | 8 | 0.5 | 76.54 | 86.06 | 140094.22 | 136028.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:40:00 | Operating | 1344.4 | 1.8 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 2.444 | 26.2 | 3 | 25.7 | 2 | 168 | 3 | 168.4 | 8 | 0.6 | 76.6 | 87.1 | 140094.28 | 136029.64 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:45:00 | Operating | 1347.2 | 5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 6.773 | 26.2 | 3 | 25.6 | 5 | 168.4 | 3 | 168.7 | 8 | 0.6 | 77.24 | 87.18 | 140094.94 | 136029.72 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:50:00 | Operating | 1350.2 | 10.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 14.148 | 26.2 | 3 | 25.7 | 2 | 168.7 | 1 | 169.1 | 8 | 0.5 | 78.2 | 87.18 | 140095.88 | 136029.72 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 07:55:00 | Operating | 1348.1 | -2.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -3.364 | 26.2 | 7 | 25.7 | 4 | 168.5 | 3 | 168.8 | 8 | 0.6 | 78.66 | 87.22 | 140096.34 | 136029.76 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:00:00 | Operating | 1349.3 | 6.2 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 8.375 | 26.2 | 3 | 25.6 | 5 | 168.6 | 1 | 168.9 | 8 | 0.6 | 78.98 | 87.26 | 140096.66 | 136029.8 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:05:00 | Operating | 1349 | -2.2 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -2.958 | 26.2 | 3 | 25.6 | 5 | 168.6 | 1 | 168.9 | 8 | 0.6 | 79.64 | 87.26 | 140097.32 | 136029.8 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:10:00 | Operating | 1345.9 | -2.9 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -3.849 | 26.2 | 3 | 25.7 | 2 | 168.2 | 1 | 168.5 | 8 | 0.6 | 79.64 | 88.2 | 140097.32 | 136030.74 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:15:00 | Operating | 1347.5 | 4.6 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 6.171 | 26.2 | 3 | 25.7 | 5 | 168.4 | 3 | 168.7 | 8 | 0.5 | 79.82 | 88.66 | 140097.5 | 136031.2 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:20:00 | Operating | 1345 | -0.4 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | -0.537 | 26.2 | 3 | 25.7 | 4 | 168.1 | 3 | 168.4 | 8 | 0.6 | 79.88 | 89.34 | 140097.56 | 136031.88 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:25:00 | Operating | 1347.2 | 2 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 2.581 | 26.3 | 7 | 25.7 | 4 | 168.4 | 1 | 168.7 | 8 | 0.5 | 80.24 | 89.34 | 140097.92 | 136031.88 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:30:00 | Operating | 1352.7 | 18.5 | 15 | 99 | 14 | 90 | 634.694 | 103.322 | 25.011 | 26.3 | 3 | 25.7 | 2 | 169 | 1 | 169.4 | 8 | 0.5 | 81.44 | 89.34 | 140099.12 | 136031.88 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:35:00 | Operating | 1354.6 | 23.1 | 16 | 99 | 14 | 90 | 634.694 | 103.322 | 31.378 | 26.3 | 3 | 25.7 | 5 | 169.3 | 1 | 169.6 | 8 | 0.6 | 82.54 | 89.34 | 140100.32 | 136031.88 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:40:00 | Operating | 1358.7 | 27.6 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 37.428 | 26.3 | 7 | 25.7 | 5 | 169.8 | 1 | 170.1 | 8 | 0.6 | 84.7 | 89.34 | 140102.38 | 136031.88 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:45:00 | Operating | 1357.8 | 14.5 | 16 | 99 | 15 | 90 | 627.314 | 110.702 | 19.68 | 26.3 | 3 | 25.7 | 5 | 169.6 | 1 | 170 | 8 | 0.6 | 86.88 | 89.34 | 140104.56 | 136031.88 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:50:00 | Operating | 1364.3 | 36.8 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 50.272 | 26.3 | 3 | 25.8 | 4 | 170.5 | 1 | 170.8 | 8 | 0.5 | 90.08 | 89.34 | 140107.94 | 136031.88 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 08:55:00 | Operating | 1367.4 | 39.6 | 17 | 99 | 16 | 90 | 619.934 | 118.082 | 54.244 | 26.4 | 3 | 25.8 | 2 | 170.9 | 1 | 171.2 | 8 | 0.6 | 94.58 | 89.34 | 140112.26 | 136031.88 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:00:00 | Operating | 1369.8 | 45.6 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 62.581 | 26.3 | 3 | 25.8 | 5 | 171.2 | 1 | 171.5 | 8 | 0.6 | 99.06 | 89.34 | 140116.94 | 136031.88 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:05:00 | Operating | 1369.6 | 35.1 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 48.178 | 26.4 | 7 | 25.8 | 5 | 171.2 | 1 | 171.5 | 8 | 0.6 | 104.6 | 89.34 | 140122.42 | 136031.88 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:10:00 | Operating | 1368.1 | 26.2 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 35.891 | 26.4 | 3 | 25.8 | 5 | 171 | 1 | 171.3 | 8 | 0.6 | 107.04 | 89.36 | 140124.72 | 136031.9 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:15:00 | Operating | 1369 | 31.2 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 42.719 | 26.4 | 3 | 25.8 | 5 | 171.1 | 1 | 171.4 | 8 | 0.5 | 109.2 | 89.36 | 140127.02 | 136031.9 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:20:00 | Operating | 1361.6 | -16 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -21.821 | 26.5 | 7 | 25.9 | 5 | 170.2 | 1 | 170.5 | 8 | 0.5 | 110.38 | 89.4 | 140128.06 | 136031.94 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:25:00 | Operating | 1368.4 | 43.7 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 59.863 | 26.5 | 7 | 26 | 2 | 171 | 1 | 171.3 | 8 | 0.6 | 111.64 | 91.76 | 140129.5 | 136034.3 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:30:00 | Operating | 1366.2 | 26 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 35.578 | 26.5 | 3 | 25.9 | 5 | 170.8 | 1 | 171 | 8 | 0.7 | 113.06 | 92.26 | 140130.74 | 136034.8 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:35:00 | Operating | 1371.1 | 33.1 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 45.463 | 26.6 | 7 | 26 | 2 | 171.4 | 1 | 171.6 | 8 | 0.6 | 117.98 | 92.26 | 140135.8 | 136034.8 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:40:00 | Operating | 1377.6 | 52.7 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | 72.712 | 26.6 | 3 | 26 | 5 | 172.2 | 1 | 172.4 | 8 | 0.6 | 126.34 | 92.26 | 140144.24 | 136034.8 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:45:00 | Operating | 1375.4 | 49.9 | 22 | 99 | 20 | 90 | 590.413 | 147.603 | 68.773 | 26.6 | 7 | 26 | 5 | 171.9 | 1 | 172.1 | 8 | 0.6 | 129.54 | 92.44 | 140147.22 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:50:00 | Operating | 1381.2 | 76 | 23 | 99 | 21 | 90 | 583.033 | 154.983 | 105.098 | 26.7 | 8 | 26.1 | 4 | 172.6 | 1 | 172.9 | 8 | 0.6 | 135.48 | 92.44 | 140153.16 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 09:55:00 | Operating | 1384.5 | 75.5 | 24 | 99 | 22 | 90 | 575.653 | 162.363 | 104.637 | 26.8 | 7 | 26.2 | 4 | 173 | 1 | 173.2 | 8 | 0.6 | 145.48 | 92.44 | 140163.16 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:00:00 | Operating | 1378.2 | 30.6 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | 42.148 | 26.9 | 8 | 26.2 | 5 | 172.3 | 1 | 172.5 | 8 | 0.7 | 150.46 | 92.44 | 140168.28 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:05:00 | Operating | 1378.1 | 26.8 | 25 | 99 | 24 | 90 | 560.893 | 177.124 | 36.934 | 26.8 | 7 | 26.2 | 5 | 172.3 | 1 | 172.5 | 8 | 0.5 | 154.74 | 92.44 | 140172.54 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:10:00 | Operating | 1374.8 | 7.4 | 26 | 99 | 24 | 90 | 560.893 | 177.124 | 10.215 | 26.9 | 8 | 26.3 | 4 | 172 | 1 | 172.1 | 8 | 0.7 | 157.06 | 92.44 | 140174.74 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:15:00 | Operating | 1379.1 | 37 | 26 | 99 | 24 | 90 | 560.893 | 177.124 | 51.073 | 26.9 | 8 | 26.2 | 5 | 172.4 | 1 | 172.5 | 8 | 0.7 | 159.64 | 92.44 | 140177.48 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:20:00 | Operating | 1384.6 | 61.8 | 27 | 99 | 26 | 90 | 546.132 | 191.884 | 85.558 | 27 | 8 | 26.3 | 4 | 173.1 | 1 | 173.2 | 8 | 0.6 | 166.32 | 92.44 | 140184 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:25:00 | Operating | 1381.3 | 42 | 27 | 99 | 26 | 90 | 546.132 | 191.884 | 58.042 | 27 | 8 | 26.3 | 5 | 172.7 | 1 | 172.8 | 8 | 0.7 | 169.88 | 92.44 | 140187.74 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:30:00 | Operating | 1383.1 | 50.4 | 28 | 99 | 27 | 90 | 538.752 | 199.264 | 69.809 | 27 | 8 | 26.3 | 5 | 172.9 | 1 | 173 | 8 | 0.7 | 175.18 | 92.44 | 140192.86 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:35:00 | Operating | 1385.2 | 57.8 | 29 | 99 | 28 | 90 | 531.372 | 206.644 | 80.121 | 27.2 | 8 | 26.4 | 5 | 173.2 | 1 | 173.3 | 8 | 0.8 | 181.78 | 92.44 | 140199.46 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:40:00 | Operating | 1380.2 | 26.6 | 30 | 99 | 28 | 90 | 531.372 | 206.644 | 36.682 | 27.2 | 8 | 26.4 | 5 | 172.6 | 1 | 172.7 | 8 | 0.8 | 185.8 | 92.44 | 140203.58 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:45:00 | Operating | 1385.6 | 63.1 | 30 | 99 | 29 | 90 | 523.992 | 214.025 | 87.508 | 27.3 | 8 | 26.5 | 4 | 173.3 | 1 | 173.3 | 8 | 0.8 | 190.64 | 92.44 | 140208.32 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:50:00 | Operating | 1386.1 | 63.9 | 31 | 99 | 30 | 90 | 516.612 | 221.405 | 88.726 | 27.4 | 8 | 26.6 | 4 | 173.3 | 1 | 173.4 | 4 | 0.8 | 197.82 | 92.44 | 140215.78 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 10:55:00 | Operating | 1384.1 | 49.3 | 32 | 99 | 31 | 90 | 509.231 | 228.785 | 68.366 | 27.5 | 8 | 26.6 | 5 | 173.1 | 1 | 173.1 | 4 | 0.9 | 203.74 | 92.44 | 140221.6 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:00:00 | Operating | 1391.2 | 102.6 | 33 | 99 | 32 | 90 | 501.851 | 236.165 | 142.886 | 27.6 | 8 | 26.8 | 4 | 173.9 | 1 | 174 | 4 | 0.9 | 212.16 | 92.44 | 140229.84 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:05:00 | Operating | 1391.8 | 101.6 | 35 | 99 | 34 | 90 | 487.091 | 250.925 | 141.61 | 28 | 8 | 27.1 | 4 | 174 | 1 | 174.1 | 5 | 0.9 | 225.24 | 92.44 | 140243.36 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:10:00 | Operating | 1398.9 | 169.1 | 37 | 99 | 35 | 90 | 479.711 | 258.306 | 236.769 | 28.3 | 8 | 27.4 | 4 | 174.9 | 7 | 174.9 | 4 | 0.9 | 238.56 | 92.44 | 140256.96 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:15:00 | Operating | 1396.4 | 141.9 | 40 | 99 | 38 | 90 | 457.57 | 280.446 | 198.267 | 28.8 | 8 | 28 | 5 | 174.6 | 1 | 174.6 | 5 | 0.9 | 258.48 | 92.44 | 140276.8 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:20:00 | Operating | 1390.9 | 98.3 | 41 | 99 | 40 | 90 | 442.81 | 295.206 | 136.836 | 29 | 8 | 28.1 | 5 | 173.9 | 1 | 174 | 4 | 1 | 271.74 | 92.44 | 140289.86 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:25:00 | Operating | 1392.5 | 114.7 | 43 | 99 | 41 | 90 | 435.43 | 302.587 | 159.904 | 29.2 | 8 | 28.2 | 5 | 174.1 | 2 | 174.2 | 8 | 1.1 | 283.62 | 92.44 | 140301.3 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:30:00 | Operating | 1396.9 | 147 | 45 | 99 | 44 | 90 | 413.289 | 324.727 | 205.594 | 29.5 | 8 | 28.4 | 5 | 174.6 | 2 | 174.6 | 8 | 1 | 299.52 | 92.44 | 140317.2 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:35:00 | Operating | 1400.8 | 176.7 | 48 | 99 | 46 | 90 | 398.529 | 339.487 | 247.826 | 29.8 | 8 | 28.6 | 5 | 175.1 | 2 | 175.2 | 8 | 1.1 | 318.56 | 92.44 | 140336.24 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:40:00 | Operating | 1401.6 | 172.7 | 51 | 99 | 49 | 90 | 376.388 | 361.628 | 242.324 | 30.1 | 8 | 29 | 5 | 175.2 | 1 | 175.3 | 8 | 1.1 | 339.5 | 92.44 | 140357.18 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:45:00 | Operating | 1385.7 | 48 | 52 | 99 | 51 | 90 | 361.628 | 376.388 | 66.638 | 30.2 | 8 | 29.1 | 5 | 173.3 | 1 | 173.4 | 8 | 1.1 | 351.24 | 92.44 | 140369.14 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:50:00 | Operating | 1389.9 | 87.5 | 53 | 99 | 51 | 90 | 361.628 | 376.388 | 121.699 | 30.1 | 8 | 29 | 3 | 173.8 | 1 | 173.9 | 8 | 1.1 | 356.76 | 92.44 | 140374.44 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 11:55:00 | Operating | 1399.4 | 155.8 | 55 | 99 | 53 | 90 | 346.868 | 391.149 | 218.04 | 30.2 | 8 | 29 | 5 | 174.8 | 1 | 174.9 | 8 | 1.2 | 369.92 | 92.44 | 140388.18 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:00:00 | Operating | 1400.1 | 133.9 | 57 | 99 | 56 | 90 | 324.727 | 413.289 | 187.709 | 30.5 | 8 | 29.3 | 5 | 175.1 | 1 | 175.2 | 8 | 1.2 | 388.6 | 92.44 | 140406.88 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:05:00 | Operating | 1398.9 | 123.9 | 59 | 99 | 58 | 90 | 309.967 | 428.05 | 173.502 | 30.6 | 8 | 29.4 | 5 | 174.9 | 1 | 175.1 | 8 | 1.2 | 402.7 | 92.44 | 140420.9 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:10:00 | Operating | 1399.9 | 118.3 | 61 | 99 | 60 | 90 | 295.206 | 442.81 | 165.711 | 30.6 | 8 | 29.5 | 4 | 175 | 1 | 175.2 | 8 | 1.2 | 416.42 | 92.44 | 140434.1 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:15:00 | Operating | 1397.9 | 93 | 63 | 99 | 61 | 90 | 287.826 | 450.19 | 130.075 | 30.7 | 8 | 29.5 | 5 | 174.8 | 1 | 175 | 8 | 1 | 428.04 | 92.44 | 140445.72 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:20:00 | Operating | 1407.8 | 163.7 | 64 | 99 | 63 | 90 | 273.066 | 464.95 | 230.158 | 30.7 | 8 | 29.5 | 5 | 175.9 | 1 | 176.1 | 8 | 1.1 | 439.5 | 92.44 | 140457.18 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:25:00 | Operating | 1405.4 | 120.2 | 67 | 99 | 65 | 90 | 258.306 | 479.711 | 169.079 | 30.9 | 8 | 29.8 | 3 | 175.7 | 1 | 175.8 | 8 | 1.1 | 457.1 | 92.44 | 140475.3 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:30:00 | Operating | 1406.7 | 130.9 | 69 | 99 | 67 | 90 | 243.545 | 494.471 | 184.333 | 30.8 | 8 | 29.7 | 5 | 175.9 | 1 | 176 | 8 | 1.1 | 471.06 | 92.44 | 140488.74 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:35:00 | Operating | 1403.3 | 91.8 | 70 | 99 | 69 | 90 | 228.785 | 509.231 | 128.902 | 30.9 | 8 | 29.8 | 3 | 175.5 | 1 | 175.6 | 4 | 1.1 | 485.88 | 92.44 | 140503.56 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:40:00 | Operating | 1396.4 | 40.6 | 72 | 99 | 70 | 90 | 221.405 | 516.612 | 56.686 | 30.8 | 8 | 29.6 | 5 | 174.7 | 1 | 174.7 | 8 | 1.2 | 494.24 | 92.44 | 140512.1 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:45:00 | Operating | 1401.2 | 86.4 | 72 | 99 | 71 | 90 | 214.025 | 523.992 | 121.148 | 30.5 | 8 | 29.4 | 4 | 175.2 | 1 | 175.3 | 8 | 1.1 | 498.22 | 92.44 | 140515.9 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:50:00 | Operating | 1399.8 | 53.3 | 74 | 99 | 72 | 90 | 206.644 | 531.372 | 74.616 | 30.4 | 8 | 29.3 | 5 | 175.1 | 1 | 175.2 | 8 | 1.1 | 508.06 | 92.44 | 140525.74 | 136034.98 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 12:55:00 | Operating | 1384.6 | -36.5 | 74 | 99 | 72 | 90 | 206.644 | 531.372 | -50.54 | 30.2 | 8 | 29.1 | 5 | 173.3 | 3 | 173.3 | 4 | 1.1 | 510.7 | 92.8 | 140528.38 | 136035.48 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:00:00 | Operating | 1388.5 | 1.1 | 74 | 99 | 72 | 90 | 206.644 | 531.372 | 1.58 | 30 | 8 | 28.9 | 5 | 173.7 | 3 | 173.8 | 7 | 1.1 | 511.2 | 93.76 | 140528.88 | 136036.3 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:05:00 | Operating | 1391.2 | 22.3 | 74 | 99 | 72 | 90 | 206.644 | 531.372 | 31.046 | 29.7 | 8 | 28.7 | 5 | 174 | 1 | 174.1 | 7 | 1 | 511.74 | 94.12 | 140529.5 | 136036.66 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:10:00 | Operating | 1412.6 | 135.1 | 75 | 99 | 74 | 90 | 191.884 | 546.132 | 191.081 | 29.6 | 8 | 28.6 | 4 | 176.6 | 1 | 176.7 | 8 | 1 | 520.56 | 94.12 | 140538.84 | 136036.66 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:15:00 | Operating | 1409.9 | 109.9 | 77 | 99 | 76 | 90 | 177.124 | 560.893 | 155.06 | 29.7 | 8 | 28.6 | 4 | 176.3 | 1 | 176.4 | 8 | 1.1 | 535.34 | 94.12 | 140553.52 | 136036.66 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:20:00 | Operating | 1403.9 | 72.9 | 79 | 99 | 77 | 90 | 169.743 | 568.273 | 102.463 | 29.5 | 8 | 28.5 | 5 | 175.6 | 1 | 175.6 | 8 | 1 | 546.74 | 94.12 | 140564.42 | 136036.66 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:25:00 | Operating | 1408.5 | 100.5 | 80 | 99 | 79 | 90 | 154.983 | 583.033 | 141.67 | 29.4 | 8 | 28.4 | 3 | 176.1 | 1 | 176.2 | 8 | 1 | 556.68 | 94.12 | 140574.36 | 136036.66 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:30:00 | Operating | 1406.8 | 90.8 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | 127.8 | 29.4 | 8 | 28.3 | 4 | 175.8 | 1 | 175.9 | 4 | 1.1 | 567.88 | 94.12 | 140585.9 | 136036.66 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:35:00 | Operating | 1400.6 | 43.5 | 83 | 99 | 81 | 90 | 140.223 | 597.793 | 61.005 | 29.3 | 8 | 28.2 | 5 | 175.2 | 1 | 175.2 | 4 | 1 | 576.6 | 94.12 | 140594.48 | 136036.66 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:40:00 | Operating | 1389 | 6.6 | 82 | 99 | 82 | 90 | 132.843 | 605.174 | 9.153 | 29 | 8 | 28 | 4 | 173.8 | 1 | 173.8 | 7 | 1 | 577.68 | 96.02 | 140595.36 | 136038.56 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:45:00 | Operating | 1392 | 15.2 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 21.167 | 28.8 | 8 | 27.8 | 3 | 174.1 | 1 | 174.2 | 7 | 0.9 | 578.9 | 96.02 | 140596.58 | 136038.56 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:50:00 | Operating | 1383.4 | -38.8 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -53.73 | 28.6 | 8 | 27.5 | 5 | 173.1 | 2 | 173.1 | 4 | 1.1 | 580.44 | 96.68 | 140598.12 | 136039.22 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 13:55:00 | Operating | 1383.4 | -17 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -23.485 | 28.4 | 8 | 27.3 | 5 | 173.1 | 5 | 173.1 | 4 | 1.1 | 580.44 | 99.54 | 140598.12 | 136042.18 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:00:00 | Operating | 1401.9 | 80.8 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | 113.119 | 28.2 | 8 | 27.1 | 4 | 175.3 | 1 | 175.4 | 8 | 1.1 | 582.36 | 100.94 | 140600.38 | 136043.48 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:05:00 | Operating | 1407.4 | 72.7 | 84 | 99 | 82 | 90 | 132.843 | 605.174 | 102.45 | 28 | 8 | 27 | 5 | 176 | 1 | 176.1 | 8 | 1.1 | 591.24 | 100.94 | 140609.22 | 136043.48 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:10:00 | Operating | 1403.1 | 40.9 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | 57.507 | 28 | 8 | 26.9 | 4 | 175.5 | 1 | 175.5 | 8 | 1 | 600.04 | 100.94 | 140617.72 | 136043.48 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:15:00 | Operating | 1402.3 | 41.7 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | 58.561 | 27.7 | 8 | 26.7 | 5 | 175.4 | 1 | 175.4 | 8 | 1.1 | 604.38 | 100.94 | 140622.24 | 136043.48 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:20:00 | Operating | 1387.6 | -23 | 86 | 99 | 84 | 90 | 118.082 | 619.934 | -31.931 | 27.5 | 8 | 26.5 | 5 | 173.6 | 1 | 173.7 | 3 | 1 | 606 | 101.22 | 140623.68 | 136043.84 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:25:00 | Operating | 1390.6 | 17 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | 23.636 | 27.3 | 8 | 26.3 | 5 | 173.9 | 1 | 174 | 7 | 1 | 606.14 | 103.14 | 140623.9 | 136045.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:30:00 | Operating | 1393 | 4.6 | 86 | 99 | 84 | 90 | 118.082 | 619.934 | 6.447 | 27.1 | 8 | 26.1 | 5 | 174.3 | 1 | 174.3 | 8 | 0.9 | 608.42 | 103.14 | 140626.1 | 136045.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:35:00 | Operating | 1377.9 | -39.9 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | -55.066 | 26.9 | 8 | 25.9 | 4 | 172.4 | 8 | 172.4 | 1 | 0.9 | 608.58 | 106.34 | 140626.26 | 136049.06 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:40:00 | Operating | 1403.8 | 63.1 | 86 | 99 | 84 | 90 | 118.082 | 619.934 | 88.619 | 26.6 | 8 | 25.7 | 4 | 175.5 | 1 | 175.6 | 8 | 1 | 611.88 | 107 | 140629.56 | 136049.54 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:45:00 | Operating | 1404.6 | 36.7 | 87 | 99 | 85 | 90 | 110.702 | 627.314 | 51.568 | 26.5 | 8 | 25.6 | 4 | 175.7 | 1 | 175.7 | 8 | 0.9 | 618.26 | 107 | 140636.1 | 136049.54 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:50:00 | Operating | 1399.8 | 29 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 40.581 | 26.3 | 8 | 25.3 | 5 | 175.1 | 1 | 175.1 | 8 | 1.1 | 620.92 | 107 | 140638.6 | 136049.54 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 14:55:00 | Operating | 1388.6 | -12.4 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -17.202 | 26.1 | 8 | 25.1 | 5 | 173.7 | 2 | 173.8 | 3 | 0.9 | 622.62 | 107.52 | 140640.3 | 136050.12 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:00:00 | Operating | 1383.3 | -23.9 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -33.103 | 25.9 | 8 | 24.9 | 5 | 173.2 | 2 | 173.1 | 3 | 1 | 622.62 | 109.1 | 140640.3 | 136051.64 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:05:00 | Operating | 1391.6 | 17 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 23.721 | 25.7 | 8 | 24.7 | 5 | 174 | 1 | 174.1 | 8 | 1 | 623.08 | 109.64 | 140640.82 | 136052.18 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:10:00 | Operating | 1397.3 | 18.6 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 26.021 | 25.5 | 8 | 24.6 | 3 | 174.7 | 1 | 174.8 | 8 | 1 | 625.86 | 109.64 | 140643.54 | 136052.18 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:15:00 | Operating | 1393.6 | 4.5 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | 6.248 | 25.5 | 8 | 24.4 | 5 | 174.3 | 1 | 174.3 | 4 | 1 | 627.46 | 109.64 | 140645.16 | 136052.18 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:20:00 | Operating | 1381.9 | -30.8 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -42.643 | 25.3 | 8 | 24.4 | 3 | 172.9 | 2 | 172.9 | 3 | 0.9 | 627.52 | 111.24 | 140645.2 | 136053.9 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:25:00 | Operating | 1376.9 | -38.8 | 87 | 99 | 86 | 90 | 103.322 | 634.694 | -53.533 | 25.3 | 8 | 24.3 | 4 | 172.2 | 2 | 172.3 | 1 | 1 | 627.52 | 115.82 | 140645.2 | 136058.36 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:30:00 | Operating | 1376.6 | -32.2 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -44.361 | 25.2 | 8 | 24.3 | 3 | 172.2 | 2 | 172.2 | 1 | 1 | 627.52 | 120.42 | 140645.2 | 136062.96 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:35:00 | Operating | 1378.4 | -23.1 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | -31.858 | 25.2 | 8 | 24.3 | 4 | 172.4 | 6 | 172.4 | 8 | 0.8 | 627.52 | 123.56 | 140645.2 | 136066.18 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:40:00 | Operating | 1386.3 | 11.9 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | 16.536 | 25.1 | 8 | 24.3 | 4 | 173.4 | 6 | 173.4 | 8 | 0.8 | 628.42 | 123.88 | 140646.1 | 136066.42 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:45:00 | Operating | 1388.7 | 19.8 | 86 | 99 | 84 | 90 | 118.082 | 619.934 | 27.463 | 25.1 | 8 | 24.3 | 4 | 173.7 | 6 | 173.7 | 8 | 0.8 | 629.26 | 123.88 | 140646.94 | 136066.42 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:50:00 | Operating | 1387.9 | 19.7 | 86 | 99 | 84 | 90 | 118.082 | 619.934 | 27.394 | 25.1 | 8 | 24.3 | 3 | 173.6 | 6 | 173.6 | 8 | 0.8 | 629.58 | 124.28 | 140647.3 | 136066.82 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 15:55:00 | Operating | 1381 | -26 | 86 | 99 | 85 | 90 | 110.702 | 627.314 | -35.878 | 25.1 | 8 | 24.2 | 5 | 172.8 | 6 | 172.8 | 4 | 0.9 | 630.06 | 125.16 | 140647.74 | 136067.7 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:00:00 | Operating | 1377.4 | -26 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | -35.928 | 25 | 8 | 24.2 | 5 | 172.3 | 2 | 172.3 | 7 | 0.9 | 630.06 | 129.34 | 140647.74 | 136072.08 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:05:00 | Operating | 1378.8 | -19.4 | 85 | 99 | 84 | 90 | 118.082 | 619.934 | -26.754 | 25 | 8 | 24.2 | 5 | 172.5 | 2 | 172.5 | 1 | 0.7 | 630.06 | 132.22 | 140647.74 | 136074.76 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:10:00 | Operating | 1379.4 | -17.6 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -24.242 | 25.1 | 8 | 24.2 | 5 | 172.6 | 6 | 172.6 | 4 | 0.8 | 630.06 | 134.1 | 140647.74 | 136076.72 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:15:00 | Operating | 1379.6 | -17.3 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -23.95 | 25.1 | 8 | 24.2 | 4 | 172.6 | 2 | 172.6 | 4 | 0.8 | 630.06 | 135.8 | 140647.74 | 136078.34 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:20:00 | Operating | 1380.3 | -17.7 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -24.426 | 25 | 8 | 24.2 | 5 | 172.7 | 3 | 172.7 | 8 | 0.8 | 630.06 | 137.1 | 140647.74 | 136079.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:25:00 | Operating | 1380.1 | -16 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -22.168 | 25 | 8 | 24.2 | 4 | 172.6 | 6 | 172.7 | 8 | 0.7 | 630.06 | 139.02 | 140647.74 | 136081.6 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:30:00 | Operating | 1380.7 | -14.1 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -19.459 | 25.1 | 8 | 24.3 | 4 | 172.7 | 3 | 172.7 | 8 | 0.7 | 630.1 | 140.12 | 140647.78 | 136082.7 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:35:00 | Operating | 1385.3 | 14.5 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | 20.091 | 25 | 8 | 24.2 | 4 | 173.2 | 3 | 173.3 | 8 | 0.7 | 630.3 | 141.14 | 140647.98 | 136083.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:40:00 | Operating | 1390.5 | 20.9 | 84 | 99 | 82 | 90 | 132.843 | 605.174 | 29.055 | 25 | 8 | 24.3 | 4 | 173.9 | 3 | 173.9 | 8 | 0.7 | 632.46 | 141.14 | 140650.24 | 136083.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:45:00 | Operating | 1391.6 | 15.7 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | 21.852 | 25 | 8 | 24.2 | 4 | 174 | 3 | 174.1 | 8 | 0.7 | 634.36 | 141.14 | 140652.04 | 136083.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:50:00 | Operating | 1382.8 | -22.6 | 84 | 99 | 83 | 90 | 125.462 | 612.554 | -31.326 | 25 | 8 | 24.2 | 5 | 173 | 3 | 173 | 4 | 0.8 | 635 | 141.72 | 140652.68 | 136084.36 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 16:55:00 | Operating | 1380.4 | -16.7 | 84 | 99 | 82 | 90 | 132.843 | 605.174 | -23.123 | 25 | 8 | 24.3 | 4 | 172.7 | 6 | 172.7 | 1 | 0.7 | 635.02 | 144.36 | 140652.7 | 136086.92 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:00:00 | Operating | 1372.1 | -58.4 | 83 | 99 | 82 | 90 | 132.843 | 605.174 | -80.266 | 25 | 8 | 24.3 | 4 | 171.6 | 2 | 171.7 | 1 | 0.8 | 635.02 | 148.82 | 140652.7 | 136091.58 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:05:00 | Operating | 1382.3 | 12.2 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | 16.889 | 25.1 | 8 | 24.3 | 4 | 172.9 | 2 | 172.9 | 8 | 0.7 | 635.1 | 152.4 | 140652.82 | 136094.94 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:10:00 | Operating | 1383.6 | 7.7 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | 10.721 | 25.1 | 8 | 24.3 | 4 | 173 | 3 | 173.1 | 8 | 0.7 | 635.42 | 152.7 | 140653.1 | 136095.24 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:15:00 | Operating | 1377.5 | -30.2 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -41.653 | 25.1 | 8 | 24.3 | 5 | 172.3 | 2 | 172.3 | 7 | 0.7 | 635.62 | 154.66 | 140653.3 | 136097.2 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:20:00 | Operating | 1377.8 | -23.5 | 82 | 99 | 81 | 90 | 140.223 | 597.793 | -32.469 | 25 | 8 | 24.3 | 5 | 172.4 | 2 | 172.4 | 4 | 0.8 | 635.62 | 157.46 | 140653.3 | 136100.1 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:25:00 | Operating | 1377.9 | -23.4 | 81 | 99 | 81 | 90 | 140.223 | 597.793 | -32.432 | 25.1 | 8 | 24.3 | 4 | 172.4 | 2 | 172.4 | 7 | 0.8 | 635.62 | 160.2 | 140653.3 | 136102.84 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:30:00 | Operating | 1378.9 | -16.5 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -22.782 | 25 | 8 | 24.3 | 5 | 172.5 | 2 | 172.5 | 8 | 0.8 | 635.62 | 162.92 | 140653.3 | 136105.54 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:35:00 | Operating | 1381.1 | -7.1 | 81 | 99 | 80 | 90 | 147.603 | 590.413 | -9.767 | 25 | 8 | 24.4 | 4 | 172.7 | 3 | 172.8 | 8 | 0.7 | 635.62 | 164.34 | 140653.3 | 136106.9 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:40:00 | Operating | 1380.1 | -16.8 | 81 | 99 | 79 | 90 | 154.983 | 583.033 | -23.263 | 25 | 7 | 24.3 | 5 | 172.7 | 3 | 172.7 | 7 | 0.7 | 635.62 | 165.72 | 140653.3 | 136108.26 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:45:00 | Operating | 1373.2 | -53.6 | 80 | 99 | 79 | 90 | 154.983 | 583.033 | -73.616 | 25 | 7 | 24.4 | 4 | 171.8 | 5 | 171.8 | 4 | 0.7 | 635.62 | 170.18 | 140653.3 | 136112.92 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:50:00 | Operating | 1374.2 | -45.4 | 79 | 99 | 78 | 90 | 162.363 | 575.653 | -62.504 | 25.1 | 8 | 24.4 | 4 | 171.9 | 2 | 172 | 7 | 0.7 | 635.62 | 175.18 | 140653.3 | 136117.72 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 17:55:00 | Operating | 1375 | -36.5 | 79 | 99 | 78 | 90 | 162.363 | 575.653 | -50.245 | 25.1 | 8 | 24.4 | 5 | 172 | 2 | 172 | 7 | 0.7 | 635.62 | 180.82 | 140653.3 | 136123.36 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:00:00 | Operating | 1373.6 | -45.6 | 78 | 99 | 77 | 90 | 169.743 | 568.273 | -62.684 | 25.2 | 8 | 24.5 | 5 | 171.8 | 2 | 171.8 | 7 | 0.7 | 635.62 | 186.9 | 140653.3 | 136129.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:05:00 | Operating | 1375 | -39.9 | 77 | 99 | 76 | 90 | 177.124 | 560.893 | -54.948 | 25.2 | 7 | 24.5 | 5 | 172 | 2 | 172 | 7 | 0.7 | 635.62 | 191.4 | 140653.3 | 136133.94 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:10:00 | Operating | 1374.8 | -41.3 | 77 | 99 | 76 | 90 | 177.124 | 560.893 | -56.793 | 25.2 | 7 | 24.5 | 5 | 172 | 2 | 172 | 7 | 0.6 | 635.62 | 195.78 | 140653.3 | 136138.32 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:15:00 | Operating | 1372.6 | -56 | 76 | 99 | 75 | 90 | 184.504 | 553.512 | -76.918 | 25.2 | 7 | 24.6 | 4 | 171.7 | 2 | 171.7 | 7 | 0.7 | 635.62 | 201.2 | 140653.3 | 136143.96 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:20:00 | Operating | 1369.6 | -79.7 | 75 | 99 | 74 | 90 | 191.884 | 546.132 | -109.289 | 25.3 | 7 | 24.6 | 5 | 171.4 | 3 | 171.4 | 7 | 0.6 | 635.62 | 207.76 | 140653.3 | 136150.3 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:25:00 | Operating | 1366 | -93.6 | 73 | 99 | 72 | 90 | 206.644 | 531.372 | -127.953 | 25.4 | 7 | 24.8 | 4 | 170.9 | 3 | 171 | 7 | 0.6 | 635.62 | 217.98 | 140653.3 | 136160.52 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:30:00 | Operating | 1364.8 | -92.4 | 72 | 99 | 70 | 90 | 221.405 | 516.612 | -126.229 | 25.6 | 7 | 24.9 | 5 | 170.7 | 3 | 170.8 | 8 | 0.7 | 635.62 | 229.44 | 140653.3 | 136172.36 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:35:00 | Operating | 1363.1 | -96.3 | 70 | 99 | 69 | 90 | 228.785 | 509.231 | -131.394 | 25.7 | 7 | 25 | 5 | 170.5 | 3 | 170.7 | 8 | 0.7 | 635.62 | 239.78 | 140653.3 | 136182.32 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:40:00 | Operating | 1359.3 | -111.9 | 69 | 99 | 67 | 90 | 243.545 | 494.471 | -152.165 | 25.8 | 3 | 25.2 | 4 | 170 | 3 | 170.2 | 8 | 0.6 | 635.62 | 251.28 | 140653.3 | 136194.26 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:45:00 | Operating | 1356.5 | -105.1 | 67 | 99 | 66 | 90 | 250.925 | 487.091 | -142.645 | 26 | 7 | 25.3 | 5 | 169.7 | 3 | 169.8 | 8 | 0.7 | 635.62 | 263.16 | 140653.3 | 136205.7 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:50:00 | Operating | 1354.5 | -104.9 | 65 | 99 | 64 | 90 | 265.686 | 472.331 | -142.182 | 26 | 7 | 25.4 | 5 | 169.4 | 3 | 169.6 | 8 | 0.6 | 635.62 | 275 | 140653.3 | 136217.54 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 18:55:00 | Operating | 1351 | -128.4 | 64 | 99 | 62 | 90 | 280.446 | 457.57 | -173.625 | 26.1 | 7 | 25.4 | 5 | 169.1 | 5 | 169.1 | 7 | 0.7 | 635.62 | 286.5 | 140653.3 | 136229.54 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:00:00 | Operating | 1348.1 | -142.5 | 62 | 99 | 59 | 90 | 302.587 | 435.43 | -192.321 | 26.1 | 7 | 25.6 | 5 | 168.7 | 3 | 168.8 | 7 | 0.6 | 635.62 | 302.06 | 140653.3 | 136244.6 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:05:00 | Operating | 1346.8 | -149.4 | 59 | 99 | 57 | 90 | 317.347 | 420.669 | -201.432 | 26.2 | 7 | 25.7 | 2 | 168.6 | 5 | 168.6 | 7 | 0.5 | 635.62 | 317.62 | 140653.3 | 136260.78 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:10:00 | Operating | 1346.8 | -146.3 | 57 | 99 | 55 | 90 | 332.107 | 405.909 | -197.279 | 26.4 | 7 | 25.8 | 5 | 168.6 | 5 | 168.6 | 7 | 0.6 | 635.62 | 335.72 | 140653.3 | 136278.88 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:15:00 | Operating | 1344.8 | -162 | 54 | 99 | 52 | 90 | 354.248 | 383.768 | -218.124 | 26.4 | 7 | 25.9 | 4 | 168.3 | 5 | 168.4 | 7 | 0.6 | 635.62 | 353.26 | 140653.3 | 136295.8 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:20:00 | Operating | 1343.5 | -169.6 | 52 | 99 | 49 | 90 | 376.388 | 361.628 | -228.09 | 26.5 | 3 | 26 | 2 | 168.2 | 5 | 168.2 | 7 | 0.7 | 635.62 | 371.44 | 140653.3 | 136314.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:25:00 | Operating | 1340.9 | -186.9 | 49 | 99 | 46 | 90 | 398.529 | 339.487 | -250.859 | 26.7 | 7 | 26.1 | 2 | 167.9 | 5 | 167.9 | 7 | 0.6 | 635.62 | 390.98 | 140653.3 | 136334.26 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:30:00 | Operating | 1336.9 | -209.8 | 46 | 99 | 43 | 90 | 420.669 | 317.347 | -280.78 | 26.9 | 7 | 26.3 | 2 | 167.4 | 3 | 167.5 | 7 | 0.6 | 635.62 | 414.08 | 140653.3 | 136357.48 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:35:00 | Operating | 1335.2 | -214.8 | 42 | 99 | 40 | 90 | 442.81 | 295.206 | -287.011 | 27.2 | 7 | 26.6 | 2 | 167.2 | 3 | 167.3 | 7 | 0.6 | 635.62 | 437.82 | 140653.3 | 136381.22 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:40:00 | Operating | 1333.8 | -210.1 | 39 | 99 | 37 | 90 | 472.331 | 265.686 | -281.599 | 27.5 | 7 | 26.8 | 2 | 167 | 3 | 167.1 | 7 | 0.7 | 635.62 | 461.56 | 140653.3 | 136404.1 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:45:00 | Operating | 1332 | -206.2 | 35 | 99 | 33 | 90 | 494.471 | 243.545 | -274.989 | 27.8 | 3 | 27.1 | 2 | 166.8 | 3 | 166.9 | 7 | 0.7 | 635.62 | 485.1 | 140653.3 | 136427.64 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:50:00 | Operating | 1325.1 | -239 | 32 | 99 | 29 | 90 | 523.992 | 214.025 | -317.114 | 28.3 | 3 | 27.7 | 2 | 166 | 5 | 166.1 | 7 | 0.6 | 635.62 | 511.04 | 140653.3 | 136453.58 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 19:55:00 | Operating | 1332.4 | -153.6 | 28 | 99 | 27 | 90 | 538.752 | 199.264 | -204.833 | 28.8 | 7 | 28.2 | 2 | 166.8 | 3 | 166.9 | 7 | 0.6 | 635.62 | 534.62 | 140653.3 | 136477.8 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:00:00 | Operating | 1340 | -90.7 | 26 | 99 | 25 | 90 | 553.512 | 184.504 | -121.673 | 28.8 | 7 | 28.2 | 2 | 167.7 | 3 | 167.8 | 8 | 0.6 | 635.62 | 548.08 | 140653.3 | 136491 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:05:00 | Operating | 1344.8 | -47.5 | 25 | 99 | 24 | 90 | 560.893 | 177.124 | -63.966 | 28.6 | 3 | 28.1 | 4 | 168.3 | 1 | 168.4 | 8 | 0.5 | 635.62 | 557.74 | 140653.3 | 136500.28 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:10:00 | Operating | 1354.6 | 2.3 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | 3.164 | 28.5 | 3 | 27.8 | 4 | 169.4 | 1 | 169.6 | 8 | 0.7 | 635.88 | 559.22 | 140653.56 | 136501.8 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:15:00 | Operating | 1350.3 | -33.5 | 25 | 99 | 23 | 90 | 568.273 | 169.743 | -45.277 | 28.4 | 1 | 27.7 | 5 | 168.9 | 1 | 169 | 8 | 0.7 | 635.92 | 560.78 | 140653.6 | 136503.5 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:20:00 | Operating | 1345.4 | -50.6 | 24 | 99 | 23 | 90 | 568.273 | 169.743 | -68.147 | 28.2 | 1 | 27.5 | 5 | 168.3 | 1 | 168.4 | 8 | 0.7 | 635.92 | 566.18 | 140653.6 | 136508.72 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:25:00 | Operating | 1344.2 | -47.3 | 23 | 99 | 22 | 90 | 575.653 | 162.363 | -63.702 | 28.1 | 1 | 27.5 | 4 | 168.1 | 1 | 168.3 | 8 | 0.6 | 635.92 | 571.58 | 140653.6 | 136514.32 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:30:00 | Operating | 1344.1 | -39.1 | 22 | 99 | 21 | 90 | 583.033 | 154.983 | -52.633 | 28 | 1 | 27.4 | 4 | 168.1 | 1 | 168.3 | 8 | 0.6 | 635.92 | 577.14 | 140653.6 | 136519.68 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:35:00 | Operating | 1344 | -38 | 22 | 99 | 21 | 90 | 583.033 | 154.983 | -51.139 | 27.8 | 1 | 27.2 | 4 | 168.1 | 1 | 168.2 | 8 | 0.7 | 635.92 | 581.26 | 140653.6 | 136523.8 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:40:00 | Operating | 1343.3 | -36 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | -48.477 | 27.7 | 1 | 27.1 | 4 | 168 | 1 | 168.1 | 8 | 0.7 | 635.92 | 585.6 | 140653.6 | 136528.14 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:45:00 | Operating | 1343.2 | -33.7 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | -45.295 | 27.5 | 1 | 26.9 | 4 | 168 | 1 | 168.1 | 8 | 0.6 | 635.92 | 589.46 | 140653.6 | 136532.14 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:50:00 | Operating | 1344 | -23 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | -31.003 | 27.4 | 1 | 26.7 | 4 | 168.1 | 1 | 168.2 | 8 | 0.7 | 635.92 | 593 | 140653.6 | 136535.64 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 20:55:00 | Operating | 1341.3 | -33 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -44.323 | 27.1 | 1 | 26.6 | 4 | 167.8 | 1 | 167.9 | 8 | 0.6 | 635.92 | 597.38 | 140653.6 | 136539.92 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:00:00 | Operating | 1341.7 | -28.5 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -38.282 | 26.9 | 1 | 26.4 | 4 | 167.8 | 1 | 168 | 8 | 0.5 | 635.92 | 600.04 | 140653.6 | 136542.8 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:05:00 | Operating | 1345.1 | -11.9 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | -16.007 | 26.8 | 1 | 26.3 | 4 | 168.2 | 1 | 168.4 | 8 | 0.6 | 635.92 | 601.9 | 140653.6 | 136544.44 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:10:00 | Operating | 1348.7 | 7.5 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 10.124 | 26.6 | 8 | 26.1 | 4 | 168.6 | 1 | 168.8 | 8 | 0.5 | 635.94 | 602.62 | 140653.64 | 136545.16 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:15:00 | Operating | 1347.1 | -4 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | -5.402 | 26.4 | 1 | 25.8 | 5 | 168.4 | 1 | 168.7 | 8 | 0.5 | 636.08 | 603.1 | 140653.76 | 136545.64 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:20:00 | Operating | 1345.3 | -14.3 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | -19.311 | 26.2 | 8 | 25.6 | 4 | 168.2 | 1 | 168.4 | 8 | 0.5 | 636.24 | 603.76 | 140653.92 | 136546.3 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:25:00 | Operating | 1348.3 | 3.6 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 4.8 | 25.9 | 1 | 25.4 | 4 | 168.6 | 1 | 168.8 | 8 | 0.6 | 636.32 | 604.7 | 140654 | 136547.24 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:30:00 | Operating | 1349.9 | 5.6 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 7.599 | 25.8 | 8 | 25.2 | 4 | 168.8 | 1 | 169 | 8 | 0.6 | 636.78 | 604.72 | 140654.46 | 136547.26 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:35:00 | Operating | 1347 | -5.4 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -7.325 | 25.6 | 8 | 25 | 5 | 168.4 | 1 | 168.6 | 8 | 0.6 | 636.82 | 605.58 | 140654.5 | 136548.12 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:40:00 | Operating | 1346.5 | -5.1 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -6.865 | 25.5 | 8 | 24.9 | 4 | 168.3 | 1 | 168.6 | 8 | 0.6 | 636.82 | 606.46 | 140654.5 | 136549.02 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:45:00 | Operating | 1346.1 | -7.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -10.065 | 25.3 | 8 | 24.7 | 4 | 168.3 | 1 | 168.5 | 8 | 0.6 | 636.84 | 607.02 | 140654.52 | 136549.6 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:50:00 | Operating | 1348 | 2.6 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 3.466 | 25.2 | 8 | 24.6 | 4 | 168.5 | 1 | 168.8 | 8 | 0.6 | 636.86 | 607.38 | 140654.54 | 136549.92 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 21:55:00 | Operating | 1345.8 | -5.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -7.426 | 25.2 | 8 | 24.5 | 5 | 168.2 | 1 | 168.5 | 8 | 0.5 | 637.16 | 608.24 | 140654.84 | 136550.78 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:00:00 | Operating | 1343.6 | -17.7 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -23.759 | 25.1 | 8 | 24.4 | 4 | 168 | 1 | 168.2 | 8 | 0.6 | 637.28 | 608.96 | 140654.96 | 136551.58 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:05:00 | Operating | 1346 | -1.1 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | -1.529 | 24.9 | 8 | 24.3 | 7 | 168.3 | 1 | 168.5 | 8 | 0.6 | 637.28 | 609.96 | 140654.96 | 136552.5 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:10:00 | Operating | 1347.9 | 6.9 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 9.333 | 24.9 | 8 | 24.2 | 5 | 168.5 | 1 | 168.7 | 8 | 0.7 | 637.36 | 610.24 | 140655.06 | 136552.78 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:15:00 | Operating | 1348.2 | 0.9 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 1.151 | 24.8 | 8 | 24.2 | 4 | 168.5 | 1 | 168.8 | 8 | 0.6 | 637.72 | 610.26 | 140655.4 | 136552.8 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:20:00 | Operating | 1350.4 | 8.6 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 11.638 | 24.7 | 8 | 24.2 | 4 | 168.8 | 1 | 169.1 | 8 | 0.5 | 638.24 | 610.3 | 140655.94 | 136552.84 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:25:00 | Operating | 1355.3 | 23.5 | 18 | 99 | 17 | 90 | 612.554 | 125.462 | 31.94 | 24.7 | 8 | 24.1 | 4 | 169.4 | 1 | 169.7 | 8 | 0.5 | 639.88 | 610.3 | 140657.56 | 136552.84 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:30:00 | Operating | 1362.5 | 49.2 | 19 | 99 | 17 | 90 | 612.554 | 125.462 | 67.097 | 24.7 | 8 | 24.1 | 4 | 170.2 | 1 | 170.5 | 8 | 0.6 | 643 | 610.3 | 140660.86 | 136552.84 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:35:00 | Operating | 1357.1 | 11 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 14.924 | 24.7 | 8 | 24.1 | 4 | 169.6 | 1 | 169.9 | 8 | 0.7 | 645.08 | 610.3 | 140662.76 | 136552.84 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:40:00 | Operating | 1356.5 | 10.3 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 14.043 | 24.7 | 8 | 24.1 | 4 | 169.5 | 1 | 169.8 | 8 | 0.5 | 645.42 | 610.7 | 140663.16 | 136553.24 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:45:00 | Operating | 1360.8 | 27.7 | 19 | 99 | 18 | 90 | 605.174 | 132.843 | 37.681 | 24.6 | 1 | 24 | 5 | 170.1 | 1 | 170.3 | 8 | 0.5 | 647.46 | 610.7 | 140665.14 | 136553.24 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:50:00 | Operating | 1362.8 | 19.1 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 26.138 | 24.6 | 1 | 24.1 | 5 | 170.3 | 1 | 170.6 | 8 | 0.6 | 650.98 | 610.7 | 140668.66 | 136553.24 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 22:55:00 | Operating | 1357 | -4.1 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -5.612 | 24.6 | 8 | 24.1 | 4 | 169.6 | 1 | 169.9 | 8 | 0.5 | 651.6 | 610.76 | 140669.28 | 136553.3 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:00:00 | Operating | 1352.9 | -8 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -10.824 | 24.6 | 1 | 24.1 | 4 | 169.1 | 1 | 169.3 | 8 | 0.6 | 651.6 | 611.88 | 140669.28 | 136554.52 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:05:00 | Operating | 1357.3 | 6.6 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 8.901 | 24.6 | 1 | 24.1 | 5 | 169.7 | 1 | 169.9 | 8 | 0.5 | 652.14 | 612.1 | 140669.82 | 136554.64 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:10:00 | Operating | 1356.9 | -0.1 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | -0.148 | 24.6 | 1 | 24.1 | 4 | 169.6 | 1 | 169.8 | 8 | 0.5 | 653 | 612.24 | 140670.7 | 136554.78 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:15:00 | Operating | 1356.7 | 0.8 | 20 | 99 | 18 | 90 | 605.174 | 132.843 | 1.087 | 24.6 | 8 | 24 | 5 | 169.6 | 1 | 169.8 | 8 | 0.5 | 653.6 | 612.32 | 140671.28 | 136554.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:20:00 | Operating | 1359.4 | 10.5 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 14.248 | 24.6 | 1 | 24.1 | 4 | 169.9 | 1 | 170.1 | 8 | 0.6 | 654.36 | 612.32 | 140672.08 | 136554.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:25:00 | Operating | 1362.7 | 21.5 | 20 | 99 | 19 | 90 | 597.793 | 140.223 | 29.337 | 24.5 | 1 | 24 | 5 | 170.3 | 1 | 170.6 | 8 | 0.5 | 655.96 | 612.32 | 140673.74 | 136554.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:30:00 | Operating | 1364.6 | 23.1 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | 31.597 | 24.6 | 1 | 24.1 | 4 | 170.5 | 1 | 170.8 | 8 | 0.6 | 658.14 | 612.32 | 140675.82 | 136554.86 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:35:00 | Operating | 1359.9 | -1.4 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | -1.899 | 24.6 | 1 | 24.1 | 4 | 170 | 1 | 170.2 | 8 | 0.6 | 659.42 | 612.4 | 140677.1 | 136554.94 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:40:00 | Operating | 1360.1 | 2.4 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | 3.245 | 24.6 | 1 | 24 | 5 | 170 | 1 | 170.2 | 8 | 0.6 | 659.78 | 612.7 | 140677.48 | 136555.24 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:45:00 | Operating | 1358.1 | -3.1 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | -4.17 | 24.6 | 3 | 24 | 5 | 169.8 | 1 | 170 | 8 | 0.6 | 660.16 | 612.94 | 140677.84 | 136555.48 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:50:00 | Operating | 1362.2 | 11.6 | 21 | 99 | 19 | 90 | 597.793 | 140.223 | 15.78 | 24.6 | 1 | 24 | 5 | 170.3 | 1 | 170.5 | 8 | 0.6 | 660.8 | 613.24 | 140678.56 | 136555.78 | 1.064
Amleang 136MW-01 | / | SACU-05/B05-ESS04/ESR-HV2530045932 | 2026-06-03 23:55:00 | Operating | 1364.7 | 15.5 | 21 | 99 | 20 | 90 | 590.413 | 147.603 | 21.199 | 24.6 | 1 | 24 | 5 | 170.6 | 1 | 170.8 | 8 | 0.6 | 663.14 | 613.24 | 140680.88 | 136555.78 | 1.064